## README
This excel-tool is a translation based on a German document which was developed by the Austrian "klimaaktiv QM Heizwerke" program.
The translation was carried out within the European project ENhancing renewable heaT planning for improving the aiR quAlity of commuNities (ENTRAIN).
Please contact Sabrina Metz at s.metz@aee.at for any suggestion or bug-report of this tool.
"klimaaktiv QM Heizwerke" is a quality management program throughout Austria in order to improve the technical quality and efficiency of biomass heating plants and district heating grids. This is achieved by accompanying quality control during the planning, construction and operation phase. For consulting and further information see www.klimaaktiv.at/qmheizwerke
"klimaaktiv QM Heizwerke" is supported by the Austrian Federal Ministry for Climate Protection, Environment, Energy, Mobility, Innovation and Technology (BMK).

## Tool notes
The Pipe Design.xlsx is meant to be used as support tool for simple calculations while working on pre-feasibility studies of district heating networks or checking monitoring data. This tool does not replace a detailed and comprehensive design and engineering process for district heating systems. Therefore, it is stringly recommenden to contact experience experts. It includes e.g. simplified calculations to estimate fluid velocity, pressure loss, pumping power demand and based on that choosing suitable pipe diameters. Additionaly, there is a sheet dedicated to storage sizing with simplified calculations (e.g. no heat losses) to estimate the heat capacity of a heat storage tank and discharge capacities. The tool is divided in three sheets, see below for more information.
The Main design and input sheet focuses on the dimensioning of district heating pipes. Water properties are calculated based on district heating network temperatures (average supply and return temperature) and an average pressure. Because of this approach the validity of the defined operating conditions (e.g. are the operating conditions within the liquid phase?) can be only partially checked. I.e. only remarkable deviations can be detected. The user can select a heat capacity (kW) and pipe diameter (DN) (predefined pipes from DN20 till DN400 are included and can be choosen via a drop-down menu). Notice that to facilitate the pipe diameter selection, a range of pipe diameters (smaller and larger diameters than the one choosen) are also included in the calculation. The tool then calculates the expected fluid velocity (m/s) and specific pressure loss (Pa/m). Once a pump efficiency is assumed, then the specific electrical consumption in (kWhel/m) is obtained. Furthermore, the expected pressure loss and pumping power consumption of the choosen pipe diameter and heat transport capacity at the defined operating conditions is calculated for different pipe lengths.
The Heat transport capacity sheet focuses on showing the influence of the temperature difference on the heat transport capacity given for 1) a specific annual volume flow rate (m3/a) or 2) for a specific heat quantity (kWh/a)
The Heat storage sheet gives, for a choosen heat storage volume in m3, information of the influence of the temperature difference on the heat storage capacity (temperatures are taken from the "Main design" sheet) as well as the possible discharge capacity in kW for different discharging times.

## Main design
Operating conditions: temperatures and average pressure
Supply temperature [°C] | 100
Return temperature [°C] | 70
Average pressure [bar] | 3
Average temperature [°C] | 85
Temperature difference [°C] | 30
Water properties at averaged conditions
Specific heat capacity [kJ/(kg.K)] | 4.1996
Density [kg/m³] | 968.7138
Dynamic viscosity [Pa.s] | 0.0003334
Pipe diameter selection
Heat transport capacity [kW] | 3000 | [5 empty] | Flow velocities according to data sheet no. 67 of the austrian board of trustees for agricultural technology and land development (ÖKL)
Volume flow rate [m³/h] | 88.4919 | [5 empty] | [ÖKL-Merkblatt Nr. 67: Technisch-wirtschaftliche Standards für Biomasse-Fernheizwerke. Wien: ÖKL, 3. Auflage 2016]
Specific volume flow rate [m³/MWh] | 29.4973 | [5 empty] | Main and dual pipelines
Nominal pipe diameter DN | 100 | 125 | 150 | 200 | 250 |  | DN | Inner pipe diameter | Flow velocity | Volume flow rate | Heat transport capacity
Inner pipe diameter [mm] | 107.1 | 132.5 | 160.3 | 210.1 | 263 | [5 empty] | ∆T=30K
Fluid velocity [m/s] | 2.7286 | 1.7827 | 1.218 | 0.70902 | 0.45248 |  |  | Di | v | Vs | P
Specific pressure loss [Pa/m] | 634.8155 | 211.0753 | 79.1772 | 19.8583 | 6.3635 |  |  | [mm] | [m/s] | [m3/h] | [kW]
Average pump efficiency | 70% | [5 empty] | 20 | 22.3 | 0.6 | 0.8 | 29
Electricity consumption [Wel/m] | 22.2921 | 7.4121 | 2.7804 | 0.69734 | 0.22346 |  | 25 | 28.5 | 1 | 2.3 | 80
[7 empty] | 32 | 37.2 | 1.1 | 4.3 | 150
Pressure loss and power consumption | [6 empty] | 40 | 43.1 | 1.2 | 6.3 | 220
Nominal pipe diameter DN | 150 | [5 empty] | 50 | 54.5 | 1.4 | 11.8 | 410
Fluid velocity [m/s] | 1.218 | [5 empty] | 65 | 70.3 | 1.6 | 22.4 | 780
Average pump efficiency | 70% | [5 empty] | 80 | 82.5 | 1.8 | 34.6 | 1200
Pipe length (1 pipe) [m] | 10 | 25 | 50 | 200 | 500 | 1000 | 100 | 107.1 | 1.9 | 61.6 | 2150
Time delay (time out - time in) [min] | 0.13684 | 0.34209 | 0.68419 | 2.7367 | 6.8419 | 13.6837 | 125 | 132.5 | 2 | 99.3 | 3400
Pressure loss (1 pipe) [bar] | 0.0079177 | 0.019794 | 0.039589 | 0.15835 | 0.39589 | 0.79177 | 150 | 160.3 | 2.5 | 181.6 | 6300
Electricity consumption of pump [Wel] | 27.8037 | 69.5093 | 139.0186 | 556.0746 | 1390.1864 | 2780.3728 | 200 | 210.1 | 3.3 | 411.9 | 14000
[7 empty] | 250 | 263 | 3.9 | 762.7 | 26000
[7 empty] | 300 | 312.7 | 4.3 | 1188.8 | 40000
[7 empty] | 350 | 344.4 | 4.6 | 1542.7 | 50000
[7 empty] | 400 | 393.8 | 5 | 2192.4 | 76000
House connection pipelines
[7 empty] | DN | Internal pipe diameter | Flow velocity | Volume flow rate | Heat transport capacity
∆T=30K
[8 empty] | Di | v | Vs | P
[8 empty] | [mm] | [m/s] | [m3/h] | [kW]
[7 empty] | 20 | 22.3 | 0.5 | 0.7 | 24
[7 empty] | 25 | 28.5 | 0.6 | 1.4 | 48
[7 empty] | 32 | 37.2 | 0.8 | 3.1 | 110
[7 empty] | 40 | 43.1 | 1 | 5.3 | 180
[7 empty] | 50 | 54.5 | 1.4 | 11.8 | 410
[7 empty] | 65 | 70.3 | 1.6 | 22.4 | 780
[7 empty] | 80 | 82.5 | 1.8 | 34.6 | 1200
[7 empty] | 100 | 107.1 | 1.9 | 61.6 | 2150
Note on B25: e.g. according to manufacturers data sheets

## Heat transport capacity
Water properties
Specific heat capacity [kJ/(kg.K)] | 4.1993
Density [kg/m³] | 968.7571
Main design data
Annual heat quantity [kWh/a] | 2000000
Yearly volume flow rate [m³/a] | 40000
Specific volume flow rate [m³/MWh] | 20
Annual averaged temperature spread [°C] | 44.2462
Dependece of transport capacity for specific heat quantity as a function of the temperature difference | [7 empty] | Dependece of transport capacity for specific anual volume flow rate as a function of the temperature difference
Heat quantity [kWh/a] | 2000000 | [6 empty] | Annual volume flow rate [m³/a] | 40000
Temperature difference [°C] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | Temperature difference [°C] | 10 | 20 | 30 | 40 | 50 | 60 | 70
Annual volume flow rate [m³/a] | 176984.7312 | 88492.3656 | 58994.9104 | 44246.1828 | 35396.9462 | 29497.4552 | 25283.533 | Heat quantity [kWh/a] | 452016.394 | 904032.788 | 1356049.182 | 1808065.576 | 2260081.97 | 2712098.364 | 3164114.758
Specific volume flow rate [m³/MWh] | 88.4924 | 44.2462 | 29.4975 | 22.1231 | 17.6985 | 14.7487 | 12.6418 | Specific volume flow rate [m³/MWh] | 88.4924 | 44.2462 | 29.4975 | 22.1231 | 17.6985 | 14.7487 | 12.6418
Dependece of flow capacity (heat quantity equal to 2000000 kWh/a) | [7 empty] | Dependece of heat transport capacity (annual volume flow rate equal to 40000 m³/a)

## Heat storage
Water properties
Specific heat capacity [kJ/(kg.K)] | 4.1993
Density [kg/m³] | 968.7571
Main design data
Yearly averaged temperature spread [°C] | 30
Heat storage capacity
Heat storage volume [m³] | 23
Temperature difference in storage [°C] | 7.5 | 15 | 22.5 | 30 | 37.5 | 45 | 52.5 | 60
Specific storage capacity [kWh/m³] | 8.4753 | 16.9506 | 25.4259 | 33.9012 | 42.3765 | 50.8518 | 59.3272 | 67.8025
Storage capacity [kWh] | 194.9321 | 389.8641 | 584.7962 | 779.7283 | 974.6603 | 1169.5924 | 1364.5245 | 1559.4566
Storage capacity[%] | 25% | 50% | 75% | 100% | 125% | 150% | 175% | 200%
Heat storage capacity in kW (constant discharge rate)
Temperature difference in heat storage [°C] | Discharge time [h]
| 1 | 2 | 3 | 4 | 6 | 8 | 12
7.5 | 194.9321 | 97.466 | 64.9774 | 48.733 | 32.4887 | 24.3665 | 16.2443
15 | 389.8641 | 194.9321 | 129.9547 | 97.466 | 64.9774 | 48.733 | 32.4887
22.5 | 584.7962 | 292.3981 | 194.9321 | 146.1991 | 97.466 | 73.0995 | 48.733
30 | 779.7283 | 389.8641 | 259.9094 | 194.9321 | 129.9547 | 97.466 | 64.9774
37.5 | 974.6603 | 487.3302 | 324.8868 | 243.6651 | 162.4434 | 121.8325 | 81.2217
45 | 1169.5924 | 584.7962 | 389.8641 | 292.3981 | 194.9321 | 146.1991 | 97.466
52.5 | 1364.5245 | 682.2622 | 454.8415 | 341.1311 | 227.4207 | 170.5656 | 113.7104
60 | 1559.4566 | 779.7283 | 519.8189 | 389.8641 | 259.9094 | 194.9321 | 129.9547

## PipeCalc (hidden)
|  | Density [kg/m³] | 968.7138 | [5 empty] | Re | flaminar
|  | Dynamic viscosity [Pa.s] | 0.0003334 |  | 0.0003334 |  |  |  | 500 | 0.128
[5 empty] | 0.004 |  |  |  | 1000 | 0.064
|  | Internal roughness [mm] | 0.08 | [5 empty] | 1500 | 0.042667
[9 empty] | 2500 | 0.0256
Swamee-Jain
DN | Inner diameter (DI) [mm] | Relative roughness | Fluid velocity [m/s] | Reynolds [-] | Flow assumption | T1 | T2 | T3 | fturbulent | interpolation factor | fused | Specific pressure loss [Pa/m]
400 | 393.8 | 0.00020315 | 0.20182 | 230920.7146 | Turbulence | 5.4905e-05 | 8.5466e-05 | -3.8527 | 0.016842 | 1 | 0.016842 | 0.84375
350 | 344.4 | 0.00023229 | 0.26387 | 264043.4884 | Turbulence | 6.2781e-05 | 7.5754e-05 | -3.8584 | 0.016793 | 1 | 0.016793 | 1.6443
300 | 312.7 | 0.00025584 | 0.32008 | 290810.9287 | Turbulence | 6.9145e-05 | 6.9448e-05 | -3.8583 | 0.016794 | 1 | 0.016794 | 2.6651
250 | 263 | 0.00030418 | 0.45248 | 345766.454 | Turbulence | 8.2211e-05 | 5.943e-05 | -3.8488 | 0.016877 | 1 | 0.016877 | 6.3635
200 | 210.1 | 0.00038077 | 0.70902 | 432825.2138 | Turbulence | 0.00010291 | 4.8555e-05 | -3.8197 | 0.017135 | 1 | 0.017135 | 19.8583
150 | 160.3 | 0.00049906 | 1.218 | 567289.9402 | Turbulence | 0.00013488 | 3.8062e-05 | -3.7621 | 0.017664 | 1 | 0.017664 | 79.1772
125 | 132.5 | 0.00060377 | 1.7827 | 686313.7918 | Turbulence | 0.00016318 | 3.2066e-05 | -3.7094 | 0.018169 | 1 | 0.018169 | 211.0753
100 | 107.1 | 0.00074697 | 2.7286 | 849081.0216 | Turbulence | 0.00020188 | 2.6476e-05 | -3.6414 | 0.018854 | 1 | 0.018854 | 634.8155
80 | 82.5 | 0.0009697 | 4.5984 | 1102261.5444 | Turbulence | 0.00026208 | 2.0934e-05 | -3.5482 | 0.019858 | 1 | 0.019858 | 2465.151
65 | 70.3 | 0.001138 | 6.3329 | 1293550.1765 | Turbulence | 0.00030756 | 1.8126e-05 | -3.4872 | 0.020558 | 1 | 0.020558 | 5680.6442
50 | 54.5 | 0.0014679 | 10.537 | 1668561.0534 | Turbulence | 0.00039673 | 1.4415e-05 | -3.386 | 0.021805 | 1 | 0.021805 | 21516.3575
40 | 43.1 | 0.0018561 | 16.8483 | 2109897.3877 | Turbulence | 0.00050166 | 1.167e-05 | -3.2896 | 0.023102 | 1 | 0.023102 | 73697.7725
32 | 37.2 | 0.0021505 | 22.6165 | 2444531.6508 | Turbulence | 0.00058123 | 1.0222e-05 | -3.2281 | 0.023991 | 1 | 0.023991 | 159780.2999
25 | 28.5 | 0.002807 | 38.532 | 3190757.1021 | Turbulence | 0.00075865 | 8.0428e-06 | -3.1154 | 0.025758 | 1 | 0.025758 | 649952.9574
20 | 22.3 | 0.0035874 | 62.9363 | 4077873.4265 | Turbulence | 0.00096958 | 6.4494e-06 | -3.0105 | 0.027584 | 1 | 0.027584 | 2373094.362

## Data Selection (hidden)
Operating point
| [atm] | [bar] | [Pa]
pressure [atm]: | 37.4903 | 3 | 300000
| [°C] | [K]
Temperature [°C]: | 85 | 358.15 |  | Temperature as search variable |  |  | Pressure as search variable
|  |  |  | Row n° | Row n° - corrected |  | Row n° | Row n° - corrected
|  |  |  | #N/A | #N/A | TRUE | #N/A | #N/A | TRUE
Data start at row: | 8 |  |  | 115 | 122 |  | 5025 | 5032 |  | If "False" the corrected row value (Cell I9) corresponds to the first item at the operating pressure.
Data per pressure: | 200 | [8 empty] | If "True" the corrected row value (Cell I9) corresponds to the last item of the first data block with a pressure slightly higher
Temperature [°C] Column: | 8
Pressure [bar] Column: | 9
Density [kg/m³] Column: | 6 |  |  |  | Row n° |  | T [°C] | P [bar] |  | Density [kg/m³] | Specific heat capcity, Cp [kJ/(kg.K)] | Specific heat capcity, Cv [kJ/(kg.K)] | Dynamic viscosity, eta [Pa.s]
Specific heat capcity, Cp [kJ/(kg.K)] Column: | 10 |  | Low T, high P | Point a) | 4947 |  | 85 | 3.9477 |  | 968.7571 | 4.1993 | 3.844 | 0.00033343
Specific heat capcity, Cv [kJ/(kg.K)] Column: | 11
Dynamic viscosity, eta [Pa.s] Column: | 7 |  | High T, high P | Point b) | 4946 |  | 86 | 3.9477 |  | 968.1064 | 4.2003 | 3.8388 | 0.00032948
|  |  | Low T, low P | Point c) | 5148 |  | 85 | 2.9608 |  | 968.712 | 4.1996 | 3.8441 | 0.0003334
|  |  | High T, low P | Point d) | 5147 |  | 86 | 2.9608 |  | 968.0612 | 4.2005 | 3.839 | 0.00032946
|  | Average on T |  | (slope) | (initial value) | (result)
Low p | Low p | c) & d) | Density [kg/m³] | -0.65082 | 968.712 | 968.712
|  |  | Specific heat capcity, Cp [kJ/(kg.K)] | 0.00096045 | 4.1996 | 4.1996
|  |  | Specific heat capcity, Cv [kJ/(kg.K)] | -0.0051543 | 3.8441 | 3.8441
High p |  |  | Dynamic viscosity, eta [Pa.s] | -3.9436e-06 | 0.0003334 | 0.0003334
|  |  |  | (slope) | (initial value) | (result)
| High p | a) & b) | Density [kg/m³] | -0.6507 | 968.7571 | 968.7571
|  |  | Specific heat capcity, Cp [kJ/(kg.K)] | 0.00095996 | 4.1993 | 4.1993
|  |  | Specific heat capcity, Cv [kJ/(kg.K)] | -0.0051526 | 3.844 | 3.844
|  |  | Dynamic viscosity, eta [Pa.s] | -3.9435e-06 | 0.00033343 | 0.00033343
|  |  |  | (slope) | (initial value) | (result)
|  | final results: | Density [kg/m³] | 0.045703 | 968.712 | 968.7138
|  |  | Specific heat capcity, Cp [kJ/(kg.K)] | -0.00022363 | 4.1996 | 4.1996
|  |  | Specific heat capcity, Cv [kJ/(kg.K)] | -0.00017465 | 3.8441 | 3.8441
|  |  | Dynamic viscosity, eta [Pa.s] | 2.6835e-08 | 0.0003334 | 0.0003334

## Water Data (hidden)
Water properties using the IAPWS-IF97 standard
Data is generated using Modelica.Media.Water.WaterIF97_pT within a simple modelica model.
https://build.openmodelica.org/Documentation/Modelica.Media.Water.IF97_Utilities.BaseIF97.html
| Temperature [K] | Pressure [Pa] | cp [J/(kg.K)] | cv [J/(kg.K)] | Density [kg/m³] | eta [kg/(m.s)] | Temperature [°C] | Pressure [bar] | cp [kJ/(kg.K)] | cv [kJ/(kg.K)] | boundary.medium.d [g/cm³] | Dynamic viscosity [Pa.s]
| 473.15 | 4000000 | 4479.8882 | 3315.1487 | 866.5211 | 0.00013493 | 200 | 39.4768 | 4.4799 | 3.3151 | 0.86652 | 0.00013493
| 472.15 | 4000000 | 4474.8833 | 3318.9292 | 867.6971 | 0.00013565 | 199 | 39.4768 | 4.4749 | 3.3189 | 0.8677 | 0.00013565
| 471.15 | 4000000 | 4469.9507 | 3322.7268 | 868.8673 | 0.00013638 | 198 | 39.4768 | 4.47 | 3.3227 | 0.86887 | 0.00013638
| 470.15 | 4000000 | 4465.0898 | 3326.542 | 870.0318 | 0.00013711 | 197 | 39.4768 | 4.4651 | 3.3265 | 0.87003 | 0.00013711
| 469.15 | 4000000 | 4460.2988 | 3330.3743 | 871.1907 | 0.00013785 | 196 | 39.4768 | 4.4603 | 3.3304 | 0.87119 | 0.00013785
| 468.15 | 4000000 | 4455.5771 | 3334.2236 | 872.3439 | 0.0001386 | 195 | 39.4768 | 4.4556 | 3.3342 | 0.87234 | 0.0001386
| 467.15 | 4000000 | 4450.9224 | 3338.0898 | 873.4916 | 0.00013936 | 194 | 39.4768 | 4.4509 | 3.3381 | 0.87349 | 0.00013936
| 466.15 | 4000000 | 4446.335 | 3341.9727 | 874.6339 | 0.00014012 | 193 | 39.4768 | 4.4463 | 3.342 | 0.87463 | 0.00014012
| 465.15 | 4000000 | 4441.8125 | 3345.8726 | 875.7705 | 0.00014089 | 192 | 39.4768 | 4.4418 | 3.3459 | 0.87577 | 0.00014089
| 464.15 | 4000000 | 4437.3545 | 3349.7888 | 876.9018 | 0.00014168 | 191 | 39.4768 | 4.4374 | 3.3498 | 0.8769 | 0.00014168
| 463.15 | 4000000 | 4432.9595 | 3353.7214 | 878.0276 | 0.00014247 | 190 | 39.4768 | 4.433 | 3.3537 | 0.87803 | 0.00014247
| 462.15 | 4000000 | 4428.627 | 3357.6704 | 879.1481 | 0.00014327 | 189 | 39.4768 | 4.4286 | 3.3577 | 0.87915 | 0.00014327
| 461.15 | 4000000 | 4424.3555 | 3361.6355 | 880.2633 | 0.00014407 | 188 | 39.4768 | 4.4244 | 3.3616 | 0.88026 | 0.00014407
| 460.15 | 4000000 | 4420.144 | 3365.6167 | 881.3732 | 0.00014489 | 187 | 39.4768 | 4.4201 | 3.3656 | 0.88137 | 0.00014489
| 459.15 | 4000000 | 4415.9917 | 3369.614 | 882.4778 | 0.00014572 | 186 | 39.4768 | 4.416 | 3.3696 | 0.88248 | 0.00014572
| 458.15 | 4000000 | 4411.8975 | 3373.627 | 883.5773 | 0.00014655 | 185 | 39.4768 | 4.4119 | 3.3736 | 0.88358 | 0.00014655
| 457.15 | 4000000 | 4407.8608 | 3377.6558 | 884.6715 | 0.0001474 | 184 | 39.4768 | 4.4079 | 3.3777 | 0.88467 | 0.0001474
| 456.15 | 4000000 | 4403.8799 | 3381.7002 | 885.7606 | 0.00014826 | 183 | 39.4768 | 4.4039 | 3.3817 | 0.88576 | 0.00014826
| 455.15 | 4000000 | 4399.9546 | 3385.76 | 886.8447 | 0.00014912 | 182 | 39.4768 | 4.4 | 3.3858 | 0.88684 | 0.00014912
| 454.15 | 4000000 | 4396.0835 | 3389.8352 | 887.9236 | 0.00015 | 181 | 39.4768 | 4.3961 | 3.3898 | 0.88792 | 0.00015
| 453.15 | 4000000 | 4392.2666 | 3393.9258 | 888.9974 | 0.00015088 | 180 | 39.4768 | 4.3923 | 3.3939 | 0.889 | 0.00015088
| 452.15 | 4000000 | 4388.502 | 3398.0315 | 890.0663 | 0.00015178 | 179 | 39.4768 | 4.3885 | 3.398 | 0.89007 | 0.00015178
| 451.15 | 4000000 | 4384.7891 | 3402.1521 | 891.1302 | 0.00015269 | 178 | 39.4768 | 4.3848 | 3.4022 | 0.89113 | 0.00015269
| 450.15 | 4000000 | 4381.1274 | 3406.2876 | 892.1891 | 0.0001536 | 177 | 39.4768 | 4.3811 | 3.4063 | 0.89219 | 0.0001536
| 449.15 | 4000000 | 4377.5161 | 3410.438 | 893.2432 | 0.00015453 | 176 | 39.4768 | 4.3775 | 3.4104 | 0.89324 | 0.00015453
| 448.15 | 4000000 | 4373.9546 | 3414.603 | 894.2923 | 0.00015547 | 175 | 39.4768 | 4.374 | 3.4146 | 0.89429 | 0.00015547
| 447.15 | 4000000 | 4370.4414 | 3418.7827 | 895.3365 | 0.00015642 | 174 | 39.4768 | 4.3704 | 3.4188 | 0.89534 | 0.00015642
| 446.15 | 4000000 | 4366.9761 | 3422.9771 | 896.3759 | 0.00015739 | 173 | 39.4768 | 4.367 | 3.423 | 0.89638 | 0.00015739
| 445.15 | 4000000 | 4363.5581 | 3427.1855 | 897.4105 | 0.00015836 | 172 | 39.4768 | 4.3636 | 3.4272 | 0.89741 | 0.00015836
| 444.15 | 4000000 | 4360.187 | 3431.4082 | 898.4403 | 0.00015935 | 171 | 39.4768 | 4.3602 | 3.4314 | 0.89844 | 0.00015935
| 443.15 | 4000000 | 4356.8613 | 3435.6453 | 899.4653 | 0.00016035 | 170 | 39.4768 | 4.3569 | 3.4356 | 0.89947 | 0.00016035
| 442.15 | 4000000 | 4353.5806 | 3439.8962 | 900.4856 | 0.00016136 | 169 | 39.4768 | 4.3536 | 3.4399 | 0.90049 | 0.00016136
| 441.15 | 4000000 | 4350.3447 | 3444.1614 | 901.5012 | 0.00016239 | 168 | 39.4768 | 4.3503 | 3.4442 | 0.9015 | 0.00016239
| 440.15 | 4000000 | 4347.1523 | 3448.4402 | 902.512 | 0.00016343 | 167 | 39.4768 | 4.3472 | 3.4484 | 0.90251 | 0.00016343
| 439.15 | 4000000 | 4344.0029 | 3452.7327 | 903.5182 | 0.00016448 | 166 | 39.4768 | 4.344 | 3.4527 | 0.90352 | 0.00016448
| 438.15 | 4000000 | 4340.896 | 3457.0391 | 904.5197 | 0.00016555 | 165 | 39.4768 | 4.3409 | 3.457 | 0.90452 | 0.00016555
| 437.15 | 4000000 | 4337.8311 | 3461.3589 | 905.5165 | 0.00016663 | 164 | 39.4768 | 4.3378 | 3.4614 | 0.90552 | 0.00016663
| 436.15 | 4000000 | 4334.8076 | 3465.6921 | 906.5089 | 0.00016772 | 163 | 39.4768 | 4.3348 | 3.4657 | 0.90651 | 0.00016772
| 435.15 | 4000000 | 4331.8242 | 3470.0386 | 907.4965 | 0.00016883 | 162 | 39.4768 | 4.3318 | 3.47 | 0.9075 | 0.00016883
| 434.15 | 4000000 | 4328.8813 | 3474.3984 | 908.4796 | 0.00016995 | 161 | 39.4768 | 4.3289 | 3.4744 | 0.90848 | 0.00016995
| 433.15 | 4000000 | 4325.9775 | 3478.7715 | 909.4581 | 0.00017109 | 160 | 39.4768 | 4.326 | 3.4788 | 0.90946 | 0.00017109
| 432.15 | 4000000 | 4323.1128 | 3483.1577 | 910.4321 | 0.00017224 | 159 | 39.4768 | 4.3231 | 3.4832 | 0.91043 | 0.00017224
| 431.15 | 4000000 | 4320.2866 | 3487.5569 | 911.4016 | 0.00017341 | 158 | 39.4768 | 4.3203 | 3.4876 | 0.9114 | 0.00017341
| 430.15 | 4000000 | 4317.4976 | 3491.9688 | 912.3665 | 0.00017459 | 157 | 39.4768 | 4.3175 | 3.492 | 0.91237 | 0.00017459
| 429.15 | 4000000 | 4314.7461 | 3496.3936 | 913.327 | 0.00017579 | 156 | 39.4768 | 4.3147 | 3.4964 | 0.91333 | 0.00017579
| 428.15 | 4000000 | 4312.0312 | 3500.8311 | 914.283 | 0.00017701 | 155 | 39.4768 | 4.312 | 3.5008 | 0.91428 | 0.00017701
| 427.15 | 4000000 | 4309.353 | 3505.2812 | 915.2344 | 0.00017824 | 154 | 39.4768 | 4.3094 | 3.5053 | 0.91523 | 0.00017824
| 426.15 | 4000000 | 4306.71 | 3509.7439 | 916.1815 | 0.00017949 | 153 | 39.4768 | 4.3067 | 3.5097 | 0.91618 | 0.00017949
| 425.15 | 4000000 | 4304.1025 | 3514.219 | 917.1241 | 0.00018076 | 152 | 39.4768 | 4.3041 | 3.5142 | 0.91712 | 0.00018076
| 424.15 | 4000000 | 4301.5293 | 3518.7065 | 918.0623 | 0.00018205 | 151 | 39.4768 | 4.3015 | 3.5187 | 0.91806 | 0.00018205
| 423.15 | 4000000 | 4298.9907 | 3523.2061 | 918.9961 | 0.00018335 | 150 | 39.4768 | 4.299 | 3.5232 | 0.919 | 0.00018335
| 422.15 | 4000000 | 4296.4858 | 3527.718 | 919.9255 | 0.00018467 | 149 | 39.4768 | 4.2965 | 3.5277 | 0.91993 | 0.00018467
| 421.15 | 4000000 | 4294.0142 | 3532.2422 | 920.8505 | 0.00018601 | 148 | 39.4768 | 4.294 | 3.5322 | 0.92085 | 0.00018601
| 420.15 | 4000000 | 4291.5752 | 3536.7781 | 921.7711 | 0.00018738 | 147 | 39.4768 | 4.2916 | 3.5368 | 0.92177 | 0.00018738
| 419.15 | 4000000 | 4289.1689 | 3541.3262 | 922.6874 | 0.00018876 | 146 | 39.4768 | 4.2892 | 3.5413 | 0.92269 | 0.00018876
| 418.15 | 4000000 | 4286.7949 | 3545.886 | 923.5992 | 0.00019016 | 145 | 39.4768 | 4.2868 | 3.5459 | 0.9236 | 0.00019016
| 417.15 | 4000000 | 4284.4521 | 3550.4578 | 924.5068 | 0.00019158 | 144 | 39.4768 | 4.2845 | 3.5505 | 0.92451 | 0.00019158
| 416.15 | 4000000 | 4282.1406 | 3555.041 | 925.41 | 0.00019302 | 143 | 39.4768 | 4.2821 | 3.555 | 0.92541 | 0.00019302
| 415.15 | 4000000 | 4279.8604 | 3559.636 | 926.3088 | 0.00019448 | 142 | 39.4768 | 4.2799 | 3.5596 | 0.92631 | 0.00019448
| 414.15 | 4000000 | 4277.6099 | 3564.2424 | 927.2034 | 0.00019596 | 141 | 39.4768 | 4.2776 | 3.5642 | 0.9272 | 0.00019596
| 413.15 | 4000000 | 4275.3896 | 3568.8604 | 928.0936 | 0.00019747 | 140 | 39.4768 | 4.2754 | 3.5689 | 0.92809 | 0.00019747
| 412.15 | 4000000 | 4273.1992 | 3573.4897 | 928.9794 | 0.000199 | 139 | 39.4768 | 4.2732 | 3.5735 | 0.92898 | 0.000199
| 411.15 | 4000000 | 4271.0376 | 3578.1304 | 929.861 | 0.00020055 | 138 | 39.4768 | 4.271 | 3.5781 | 0.92986 | 0.00020055
| 410.15 | 4000000 | 4268.9053 | 3582.7822 | 930.7383 | 0.00020213 | 137 | 39.4768 | 4.2689 | 3.5828 | 0.93074 | 0.00020213
| 409.15 | 4000000 | 4266.8018 | 3587.4453 | 931.6113 | 0.00020373 | 136 | 39.4768 | 4.2668 | 3.5874 | 0.93161 | 0.00020373
| 408.15 | 4000000 | 4264.7261 | 3592.1194 | 932.48 | 0.00020535 | 135 | 39.4768 | 4.2647 | 3.5921 | 0.93248 | 0.00020535
| 407.15 | 4000000 | 4262.6782 | 3596.8044 | 933.3444 | 0.000207 | 134 | 39.4768 | 4.2627 | 3.5968 | 0.93334 | 0.000207
| 406.15 | 4000000 | 4260.6582 | 3601.5005 | 934.2045 | 0.00020868 | 133 | 39.4768 | 4.2607 | 3.6015 | 0.9342 | 0.00020868
| 405.15 | 4000000 | 4258.6655 | 3606.2073 | 935.0603 | 0.00021038 | 132 | 39.4768 | 4.2587 | 3.6062 | 0.93506 | 0.00021038
| 404.15 | 4000000 | 4256.6992 | 3610.9248 | 935.9119 | 0.00021211 | 131 | 39.4768 | 4.2567 | 3.6109 | 0.93591 | 0.00021211
| 403.15 | 4000000 | 4254.7603 | 3615.6531 | 936.7591 | 0.00021386 | 130 | 39.4768 | 4.2548 | 3.6157 | 0.93676 | 0.00021386
| 402.15 | 4000000 | 4252.8472 | 3620.3921 | 937.6021 | 0.00021564 | 129 | 39.4768 | 4.2528 | 3.6204 | 0.9376 | 0.00021564
| 401.15 | 4000000 | 4250.9604 | 3625.1414 | 938.4408 | 0.00021745 | 128 | 39.4768 | 4.251 | 3.6251 | 0.93844 | 0.00021745
| 400.15 | 4000000 | 4249.0991 | 3629.9011 | 939.2752 | 0.0002193 | 127 | 39.4768 | 4.2491 | 3.6299 | 0.93928 | 0.0002193
| 399.15 | 4000000 | 4247.2637 | 3634.6711 | 940.1053 | 0.00022117 | 126 | 39.4768 | 4.2473 | 3.6347 | 0.94011 | 0.00022117
| 398.15 | 4000000 | 4245.4531 | 3639.4517 | 940.9312 | 0.00022307 | 125 | 39.4768 | 4.2455 | 3.6395 | 0.94093 | 0.00022307
| 397.15 | 4000000 | 4243.668 | 3644.2422 | 941.7528 | 0.000225 | 124 | 39.4768 | 4.2437 | 3.6442 | 0.94175 | 0.000225
| 396.15 | 4000000 | 4241.9072 | 3649.0427 | 942.5701 | 0.00022696 | 123 | 39.4768 | 4.2419 | 3.649 | 0.94257 | 0.00022696
| 395.15 | 4000000 | 4240.1709 | 3653.8535 | 943.3831 | 0.00022896 | 122 | 39.4768 | 4.2402 | 3.6539 | 0.94338 | 0.00022896
| 394.15 | 4000000 | 4238.459 | 3658.6741 | 944.1918 | 0.00023099 | 121 | 39.4768 | 4.2385 | 3.6587 | 0.94419 | 0.00023099
| 393.15 | 4000000 | 4236.771 | 3663.5044 | 944.9962 | 0.00023305 | 120 | 39.4768 | 4.2368 | 3.6635 | 0.945 | 0.00023305
| 392.15 | 4000000 | 4235.1069 | 3668.3445 | 945.7963 | 0.00023515 | 119 | 39.4768 | 4.2351 | 3.6683 | 0.9458 | 0.00023515
| 391.15 | 4000000 | 4233.4663 | 3673.1943 | 946.5921 | 0.00023728 | 118 | 39.4768 | 4.2335 | 3.6732 | 0.94659 | 0.00023728
| 390.15 | 4000000 | 4231.8491 | 3678.0535 | 947.3836 | 0.00023945 | 117 | 39.4768 | 4.2318 | 3.6781 | 0.94738 | 0.00023945
| 389.15 | 4000000 | 4230.2549 | 3682.9224 | 948.1708 | 0.00024166 | 116 | 39.4768 | 4.2303 | 3.6829 | 0.94817 | 0.00024166
| 388.15 | 4000000 | 4228.6841 | 3687.8003 | 948.9537 | 0.0002439 | 115 | 39.4768 | 4.2287 | 3.6878 | 0.94895 | 0.0002439
| 387.15 | 4000000 | 4227.1357 | 3692.6875 | 949.7322 | 0.00024618 | 114 | 39.4768 | 4.2271 | 3.6927 | 0.94973 | 0.00024618
| 386.15 | 4000000 | 4225.6099 | 3697.584 | 950.5064 | 0.00024851 | 113 | 39.4768 | 4.2256 | 3.6976 | 0.95051 | 0.00024851
| 385.15 | 4000000 | 4224.1064 | 3702.4893 | 951.2763 | 0.00025087 | 112 | 39.4768 | 4.2241 | 3.7025 | 0.95128 | 0.00025087
| 384.15 | 4000000 | 4222.625 | 3707.4036 | 952.0418 | 0.00025328 | 111 | 39.4768 | 4.2226 | 3.7074 | 0.95204 | 0.00025328
| 383.15 | 4000000 | 4221.166 | 3712.3264 | 952.8029 | 0.00025572 | 110 | 39.4768 | 4.2212 | 3.7123 | 0.9528 | 0.00025572
| 382.15 | 4000000 | 4219.729 | 3717.2581 | 953.5597 | 0.00025821 | 109 | 39.4768 | 4.2197 | 3.7173 | 0.95356 | 0.00025821
| 381.15 | 4000000 | 4218.3135 | 3722.1982 | 954.3121 | 0.00026075 | 108 | 39.4768 | 4.2183 | 3.7222 | 0.95431 | 0.00026075
| 380.15 | 4000000 | 4216.9194 | 3727.1467 | 955.0601 | 0.00026333 | 107 | 39.4768 | 4.2169 | 3.7271 | 0.95506 | 0.00026333
| 379.15 | 4000000 | 4215.5469 | 3732.1033 | 955.8036 | 0.00026596 | 106 | 39.4768 | 4.2155 | 3.7321 | 0.9558 | 0.00026596
| 378.15 | 4000000 | 4214.1958 | 3737.0681 | 956.5428 | 0.00026864 | 105 | 39.4768 | 4.2142 | 3.7371 | 0.95654 | 0.00026864
| 377.15 | 4000000 | 4212.8657 | 3742.041 | 957.2776 | 0.00027137 | 104 | 39.4768 | 4.2129 | 3.742 | 0.95728 | 0.00027137
| 376.15 | 4000000 | 4211.5571 | 3747.0215 | 958.0079 | 0.00027414 | 103 | 39.4768 | 4.2116 | 3.747 | 0.95801 | 0.00027414
| 375.15 | 4000000 | 4210.269 | 3752.0095 | 958.7338 | 0.00027697 | 102 | 39.4768 | 4.2103 | 3.752 | 0.95873 | 0.00027697
| 374.15 | 4000000 | 4209.002 | 3757.0051 | 959.4551 | 0.00027985 | 101 | 39.4768 | 4.209 | 3.757 | 0.95946 | 0.00027985
| 373.15 | 4000000 | 4207.7554 | 3762.0081 | 960.172 | 0.00028279 | 100 | 39.4768 | 4.2078 | 3.762 | 0.96017 | 0.00028279
| 372.15 | 4000000 | 4206.5298 | 3767.0178 | 960.8844 | 0.00028578 | 99 | 39.4768 | 4.2065 | 3.767 | 0.96088 | 0.00028578
| 371.15 | 4000000 | 4205.3242 | 3772.0347 | 961.5922 | 0.00028883 | 98 | 39.4768 | 4.2053 | 3.772 | 0.96159 | 0.00028883
| 370.15 | 4000000 | 4204.1396 | 3777.0583 | 962.2955 | 0.00029193 | 97 | 39.4768 | 4.2041 | 3.7771 | 0.9623 | 0.00029193
| 369.15 | 4000000 | 4202.9746 | 3782.0884 | 962.9943 | 0.0002951 | 96 | 39.4768 | 4.203 | 3.7821 | 0.96299 | 0.0002951
| 368.15 | 4000000 | 4201.8306 | 3787.1248 | 963.6885 | 0.00029833 | 95 | 39.4768 | 4.2018 | 3.7871 | 0.96369 | 0.00029833
| 367.15 | 4000000 | 4200.7065 | 3792.1672 | 964.3781 | 0.00030162 | 94 | 39.4768 | 4.2007 | 3.7922 | 0.96438 | 0.00030162
| 366.15 | 4000000 | 4199.6025 | 3797.2156 | 965.0631 | 0.00030498 | 93 | 39.4768 | 4.1996 | 3.7972 | 0.96506 | 0.00030498
| 365.15 | 4000000 | 4198.5181 | 3802.2693 | 965.7435 | 0.0003084 | 92 | 39.4768 | 4.1985 | 3.8023 | 0.96574 | 0.0003084
| 364.15 | 4000000 | 4197.4541 | 3807.3286 | 966.4192 | 0.00031189 | 91 | 39.4768 | 4.1975 | 3.8073 | 0.96642 | 0.00031189
| 363.15 | 4000000 | 4196.4102 | 3812.3928 | 967.0902 | 0.00031545 | 90 | 39.4768 | 4.1964 | 3.8124 | 0.96709 | 0.00031545
| 362.15 | 4000000 | 4195.3857 | 3817.4619 | 967.7565 | 0.00031909 | 89 | 39.4768 | 4.1954 | 3.8175 | 0.96776 | 0.00031909
| 361.15 | 4000000 | 4194.3809 | 3822.5356 | 968.4181 | 0.00032279 | 88 | 39.4768 | 4.1944 | 3.8225 | 0.96842 | 0.00032279
| 360.15 | 4000000 | 4193.396 | 3827.6135 | 969.075 | 0.00032658 | 87 | 39.4768 | 4.1934 | 3.8276 | 0.96907 | 0.00032658
| 359.15 | 4000000 | 4192.4312 | 3832.6951 | 969.7271 | 0.00033044 | 86 | 39.4768 | 4.1924 | 3.8327 | 0.96973 | 0.00033044
| 358.15 | 4000000 | 4191.4858 | 3837.7805 | 970.3743 | 0.00033438 | 85 | 39.4768 | 4.1915 | 3.8378 | 0.97037 | 0.00033438
| 357.15 | 4000000 | 4190.5596 | 3842.8691 | 971.0168 | 0.00033841 | 84 | 39.4768 | 4.1906 | 3.8429 | 0.97102 | 0.00033841
| 356.15 | 4000000 | 4189.6533 | 3847.9607 | 971.6544 | 0.00034252 | 83 | 39.4768 | 4.1897 | 3.848 | 0.97165 | 0.00034252
| 355.15 | 4000000 | 4188.7666 | 3853.0549 | 972.2871 | 0.00034671 | 82 | 39.4768 | 4.1888 | 3.8531 | 0.97229 | 0.00034671
| 354.15 | 4000000 | 4187.8994 | 3858.1511 | 972.915 | 0.000351 | 81 | 39.4768 | 4.1879 | 3.8582 | 0.97291 | 0.000351
| 353.15 | 4000000 | 4187.0518 | 3863.2493 | 973.5378 | 0.00035538 | 80 | 39.4768 | 4.1871 | 3.8632 | 0.97354 | 0.00035538
| 352.15 | 4000000 | 4186.2236 | 3868.3486 | 974.1558 | 0.00035985 | 79 | 39.4768 | 4.1862 | 3.8683 | 0.97416 | 0.00035985
| 351.15 | 4000000 | 4185.4146 | 3873.449 | 974.7686 | 0.00036442 | 78 | 39.4768 | 4.1854 | 3.8734 | 0.97477 | 0.00036442
| 350.15 | 4000000 | 4184.6255 | 3878.55 | 975.3765 | 0.00036909 | 77 | 39.4768 | 4.1846 | 3.8786 | 0.97538 | 0.00036909
| 349.15 | 4000000 | 4183.8555 | 3883.6509 | 975.9793 | 0.00037387 | 76 | 39.4768 | 4.1839 | 3.8837 | 0.97598 | 0.00037387
| 348.15 | 4000000 | 4183.105 | 3888.7512 | 976.577 | 0.00037875 | 75 | 39.4768 | 4.1831 | 3.8888 | 0.97658 | 0.00037875
| 347.15 | 4000000 | 4182.3735 | 3893.8508 | 977.1696 | 0.00038374 | 74 | 39.4768 | 4.1824 | 3.8939 | 0.97717 | 0.00038374
| 346.15 | 4000000 | 4181.6616 | 3898.949 | 977.757 | 0.00038885 | 73 | 39.4768 | 4.1817 | 3.8989 | 0.97776 | 0.00038885
| 345.15 | 4000000 | 4180.9692 | 3904.0449 | 978.3391 | 0.00039407 | 72 | 39.4768 | 4.181 | 3.904 | 0.97834 | 0.00039407
| 344.15 | 4000000 | 4180.2964 | 3909.1384 | 978.916 | 0.00039941 | 71 | 39.4768 | 4.1803 | 3.9091 | 0.97892 | 0.00039941
| 343.15 | 4000000 | 4179.6426 | 3914.2288 | 979.4876 | 0.00040487 | 70 | 39.4768 | 4.1796 | 3.9142 | 0.97949 | 0.00040487
| 342.15 | 4000000 | 4179.0083 | 3919.3154 | 980.0539 | 0.00041047 | 69 | 39.4768 | 4.179 | 3.9193 | 0.98005 | 0.00041047
| 341.15 | 4000000 | 4178.3931 | 3924.3977 | 980.6148 | 0.00041619 | 68 | 39.4768 | 4.1784 | 3.9244 | 0.98061 | 0.00041619
| 340.15 | 4000000 | 4177.7974 | 3929.4749 | 981.1703 | 0.00042205 | 67 | 39.4768 | 4.1778 | 3.9295 | 0.98117 | 0.00042205
| 339.15 | 4000000 | 4177.2212 | 3934.5464 | 981.7203 | 0.00042805 | 66 | 39.4768 | 4.1772 | 3.9345 | 0.98172 | 0.00042805
| 338.15 | 4000000 | 4176.6641 | 3939.6113 | 982.2649 | 0.0004342 | 65 | 39.4768 | 4.1767 | 3.9396 | 0.98226 | 0.0004342
| 337.15 | 4000000 | 4176.1265 | 3944.6694 | 982.8038 | 0.0004405 | 64 | 39.4768 | 4.1761 | 3.9447 | 0.9828 | 0.0004405
| 336.15 | 4000000 | 4175.6084 | 3949.7195 | 983.3372 | 0.00044695 | 63 | 39.4768 | 4.1756 | 3.9497 | 0.98334 | 0.00044695
| 335.15 | 4000000 | 4175.1094 | 3954.7607 | 983.8649 | 0.00045356 | 62 | 39.4768 | 4.1751 | 3.9548 | 0.98386 | 0.00045356
| 334.15 | 4000000 | 4174.6299 | 3959.7927 | 984.3869 | 0.00046033 | 61 | 39.4768 | 4.1746 | 3.9598 | 0.98439 | 0.00046033
| 333.15 | 4000000 | 4174.1694 | 3964.8142 | 984.9031 | 0.00046728 | 60 | 39.4768 | 4.1742 | 3.9648 | 0.9849 | 0.00046728
| 332.15 | 4000000 | 4173.7285 | 3969.8245 | 985.4136 | 0.0004744 | 59 | 39.4768 | 4.1737 | 3.9698 | 0.98541 | 0.0004744
| 331.15 | 4000000 | 4173.3071 | 3974.8228 | 985.9182 | 0.0004817 | 58 | 39.4768 | 4.1733 | 3.9748 | 0.98592 | 0.0004817
| 330.15 | 4000000 | 4172.9048 | 3979.8081 | 986.4168 | 0.0004892 | 57 | 39.4768 | 4.1729 | 3.9798 | 0.98642 | 0.0004892
| 329.15 | 4000000 | 4172.522 | 3984.7793 | 986.9095 | 0.00049688 | 56 | 39.4768 | 4.1725 | 3.9848 | 0.98691 | 0.00049688
| 328.15 | 4000000 | 4172.1587 | 3989.7356 | 987.3961 | 0.00050478 | 55 | 39.4768 | 4.1722 | 3.9897 | 0.9874 | 0.00050478
| 327.15 | 4000000 | 4171.8145 | 3994.676 | 987.8766 | 0.00051288 | 54 | 39.4768 | 4.1718 | 3.9947 | 0.98788 | 0.00051288
| 326.15 | 4000000 | 4171.4897 | 3999.5994 | 988.351 | 0.00052119 | 53 | 39.4768 | 4.1715 | 3.9996 | 0.98835 | 0.00052119
| 325.15 | 4000000 | 4171.1846 | 4004.5046 | 988.8191 | 0.00052974 | 52 | 39.4768 | 4.1712 | 4.0045 | 0.98882 | 0.00052974
| 324.15 | 4000000 | 4170.8989 | 4009.3904 | 989.2809 | 0.00053851 | 51 | 39.4768 | 4.1709 | 4.0094 | 0.98928 | 0.00053851
| 323.15 | 4000000 | 4170.6323 | 4014.2561 | 989.7363 | 0.00054753 | 50 | 39.4768 | 4.1706 | 4.0143 | 0.98974 | 0.00054753
| 322.15 | 4000000 | 4170.3857 | 4019.1001 | 990.1853 | 0.0005568 | 49 | 39.4768 | 4.1704 | 4.0191 | 0.99019 | 0.0005568
| 321.15 | 4000000 | 4170.1587 | 4023.9211 | 990.6278 | 0.00056634 | 48 | 39.4768 | 4.1702 | 4.0239 | 0.99063 | 0.00056634
| 320.15 | 4000000 | 4169.9512 | 4028.7183 | 991.0637 | 0.00057614 | 47 | 39.4768 | 4.17 | 4.0287 | 0.99106 | 0.00057614
| 319.15 | 4000000 | 4169.7632 | 4033.49 | 991.4929 | 0.00058622 | 46 | 39.4768 | 4.1698 | 4.0335 | 0.99149 | 0.00058622
| 318.15 | 4000000 | 4169.5952 | 4038.2349 | 991.9154 | 0.0005966 | 45 | 39.4768 | 4.1696 | 4.0382 | 0.99192 | 0.0005966
| 317.15 | 4000000 | 4169.4473 | 4042.9519 | 992.3311 | 0.00060728 | 44 | 39.4768 | 4.1694 | 4.043 | 0.99233 | 0.00060728
| 316.15 | 4000000 | 4169.3193 | 4047.6394 | 992.7398 | 0.00061828 | 43 | 39.4768 | 4.1693 | 4.0476 | 0.99274 | 0.00061828
| 315.15 | 4000000 | 4169.2114 | 4052.2959 | 993.1415 | 0.0006296 | 42 | 39.4768 | 4.1692 | 4.0523 | 0.99314 | 0.0006296
| 314.15 | 4000000 | 4169.1235 | 4056.9202 | 993.5361 | 0.00064127 | 41 | 39.4768 | 4.1691 | 4.0569 | 0.99354 | 0.00064127
| 313.15 | 4000000 | 4169.0566 | 4061.5107 | 993.9235 | 0.0006533 | 40 | 39.4768 | 4.1691 | 4.0615 | 0.99392 | 0.0006533
| 312.15 | 4000000 | 4169.0103 | 4066.0657 | 994.3036 | 0.0006657 | 39 | 39.4768 | 4.169 | 4.0661 | 0.9943 | 0.0006657
| 311.15 | 4000000 | 4168.9849 | 4070.5837 | 994.6764 | 0.00067849 | 38 | 39.4768 | 4.169 | 4.0706 | 0.99468 | 0.00067849
| 310.15 | 4000000 | 4168.981 | 4075.0635 | 995.0417 | 0.00069168 | 37 | 39.4768 | 4.169 | 4.0751 | 0.99504 | 0.00069168
| 309.15 | 4000000 | 4168.9985 | 4079.5029 | 995.3993 | 0.0007053 | 36 | 39.4768 | 4.169 | 4.0795 | 0.9954 | 0.0007053
| 308.15 | 4000000 | 4169.0381 | 4083.9004 | 995.7492 | 0.00071936 | 35 | 39.4768 | 4.169 | 4.0839 | 0.99575 | 0.00071936
| 307.15 | 4000000 | 4169.1006 | 4088.2546 | 996.0913 | 0.00073387 | 34 | 39.4768 | 4.1691 | 4.0883 | 0.99609 | 0.00073387
| 306.15 | 4000000 | 4169.1855 | 4092.5635 | 996.4255 | 0.00074888 | 33 | 39.4768 | 4.1692 | 4.0926 | 0.99643 | 0.00074888
| 305.15 | 4000000 | 4169.2949 | 4096.8257 | 996.7515 | 0.00076438 | 32 | 39.4768 | 4.1693 | 4.0968 | 0.99675 | 0.00076438
| 304.15 | 4000000 | 4169.4282 | 4101.0391 | 997.0694 | 0.00078041 | 31 | 39.4768 | 4.1694 | 4.101 | 0.99707 | 0.00078041
| 303.15 | 4000000 | 4169.5869 | 4105.2021 | 997.379 | 0.000797 | 30 | 39.4768 | 4.1696 | 4.1052 | 0.99738 | 0.000797
| 302.15 | 4000000 | 4169.7715 | 4109.313 | 997.68 | 0.00081416 | 29 | 39.4768 | 4.1698 | 4.1093 | 0.99768 | 0.00081416
| 301.15 | 4000000 | 4169.9834 | 4113.3696 | 997.9725 | 0.00083194 | 28 | 39.4768 | 4.17 | 4.1134 | 0.99797 | 0.00083194
| 300.15 | 4000000 | 4170.2241 | 4117.3711 | 998.2562 | 0.00085035 | 27 | 39.4768 | 4.1702 | 4.1174 | 0.99826 | 0.00085035
| 299.15 | 4000000 | 4170.4937 | 4121.3145 | 998.5309 | 0.00086942 | 26 | 39.4768 | 4.1705 | 4.1213 | 0.99853 | 0.00086942
| 298.15 | 4000000 | 4170.7949 | 4125.1992 | 998.7966 | 0.0008892 | 25 | 39.4768 | 4.1708 | 4.1252 | 0.9988 | 0.0008892
| 297.15 | 4000000 | 4171.1289 | 4129.0225 | 999.053 | 0.00090972 | 24 | 39.4768 | 4.1711 | 4.129 | 0.99905 | 0.00090972
| 296.15 | 4000000 | 4171.498 | 4132.7827 | 999.2999 | 0.00093102 | 23 | 39.4768 | 4.1715 | 4.1328 | 0.9993 | 0.00093102
| 295.15 | 4000000 | 4171.9038 | 4136.4785 | 999.5374 | 0.00095313 | 22 | 39.4768 | 4.1719 | 4.1365 | 0.99954 | 0.00095313
| 294.15 | 4000000 | 4172.3491 | 4140.1084 | 999.7649 | 0.0009761 | 21 | 39.4768 | 4.1723 | 4.1401 | 0.99976 | 0.0009761
| 293.15 | 4000000 | 4172.8364 | 4143.6699 | 999.9825 | 0.00099998 | 20 | 39.4768 | 4.1728 | 4.1437 | 0.99998 | 0.00099998
| 292.15 | 4000000 | 4173.3687 | 4147.1621 | 1000.1898 | 0.0010248 | 19 | 39.4768 | 4.1734 | 4.1472 | 1.0002 | 0.0010248
| 291.15 | 4000000 | 4173.9497 | 4150.583 | 1000.3867 | 0.0010507 | 18 | 39.4768 | 4.1739 | 4.1506 | 1.0004 | 0.0010507
| 290.15 | 4000000 | 4174.5835 | 4153.9312 | 1000.573 | 0.0010776 | 17 | 39.4768 | 4.1746 | 4.1539 | 1.0006 | 0.0010776
| 289.15 | 4000000 | 4175.2739 | 4157.2056 | 1000.7484 | 0.0011056 | 16 | 39.4768 | 4.1753 | 4.1572 | 1.0007 | 0.0011056
| 288.15 | 4000000 | 4176.0259 | 4160.4043 | 1000.9125 | 0.0011349 | 15 | 39.4768 | 4.176 | 4.1604 | 1.0009 | 0.0011349
| 287.15 | 4000000 | 4176.8447 | 4163.5259 | 1001.0653 | 0.0011654 | 14 | 39.4768 | 4.1768 | 4.1635 | 1.0011 | 0.0011654
| 286.15 | 4000000 | 4177.7363 | 4166.5703 | 1001.2064 | 0.0011972 | 13 | 39.4768 | 4.1777 | 4.1666 | 1.0012 | 0.0011972
| 285.15 | 4000000 | 4178.7075 | 4169.5352 | 1001.3355 | 0.0012305 | 12 | 39.4768 | 4.1787 | 4.1695 | 1.0013 | 0.0012305
| 284.15 | 4000000 | 4179.7656 | 4172.4204 | 1001.4523 | 0.0012653 | 11 | 39.4768 | 4.1798 | 4.1724 | 1.0015 | 0.0012653
| 283.15 | 4000000 | 4180.9194 | 4175.2251 | 1001.5565 | 0.0013017 | 10 | 39.4768 | 4.1809 | 4.1752 | 1.0016 | 0.0013017
| 282.15 | 4000000 | 4182.1772 | 4177.9487 | 1001.6477 | 0.0013398 | 9 | 39.4768 | 4.1822 | 4.1779 | 1.0016 | 0.0013398
| 281.15 | 4000000 | 4183.5498 | 4180.5903 | 1001.7256 | 0.0013798 | 8 | 39.4768 | 4.1835 | 4.1806 | 1.0017 | 0.0013798
| 280.15 | 4000000 | 4185.0483 | 4183.1504 | 1001.7899 | 0.0014216 | 7 | 39.4768 | 4.185 | 4.1832 | 1.0018 | 0.0014216
| 279.15 | 4000000 | 4186.6855 | 4185.6279 | 1001.84 | 0.0014656 | 6 | 39.4768 | 4.1867 | 4.1856 | 1.0018 | 0.0014656
| 278.15 | 4000000 | 4188.4751 | 4188.0239 | 1001.8755 | 0.0015118 | 5 | 39.4768 | 4.1885 | 4.188 | 1.0019 | 0.0015118
| 277.15 | 4000000 | 4190.4331 | 4190.3384 | 1001.8961 | 0.0015603 | 4 | 39.4768 | 4.1904 | 4.1903 | 1.0019 | 0.0015603
| 276.15 | 4000000 | 4192.5762 | 4192.5718 | 1001.9013 | 0.0016114 | 3 | 39.4768 | 4.1926 | 4.1926 | 1.0019 | 0.0016114
| 275.15 | 4000000 | 4194.9238 | 4194.7256 | 1001.8905 | 0.0016653 | 2 | 39.4768 | 4.1949 | 4.1947 | 1.0019 | 0.0016653
| 274.15 | 4000000 | 4197.4971 | 4196.8003 | 1001.8632 | 0.001722 | 0.99999 | 39.4768 | 4.1975 | 4.1968 | 1.0019 | 0.001722
| 273.15 | 4000000 | 4200.3193 | 4198.7974 | 1001.8188 | 0.0017819 | -6.1035e-06 | 39.4768 | 4.2003 | 4.1988 | 1.0018 | 0.0017819
| 473.15 | 3500000 | 4482.7358 | 3315.5232 | 866.1445 | 0.00013481 | 200 | 34.5422 | 4.4827 | 3.3155 | 0.86614 | 0.00013481
| 472.15 | 3500000 | 4477.6904 | 3319.3037 | 867.3232 | 0.00013553 | 199 | 34.5422 | 4.4777 | 3.3193 | 0.86732 | 0.00013553
| 471.15 | 3500000 | 4472.7188 | 3323.1018 | 868.496 | 0.00013625 | 198 | 34.5422 | 4.4727 | 3.3231 | 0.8685 | 0.00013625
| 470.15 | 3500000 | 4467.8188 | 3326.917 | 869.6631 | 0.00013699 | 197 | 34.5422 | 4.4678 | 3.3269 | 0.86966 | 0.00013699
| 469.15 | 3500000 | 4462.9902 | 3330.7495 | 870.8245 | 0.00013773 | 196 | 34.5422 | 4.463 | 3.3307 | 0.87082 | 0.00013773
| 468.15 | 3500000 | 4458.2314 | 3334.5991 | 871.9803 | 0.00013848 | 195 | 34.5422 | 4.4582 | 3.3346 | 0.87198 | 0.00013848
| 467.15 | 3500000 | 4453.541 | 3338.4658 | 873.1305 | 0.00013923 | 194 | 34.5422 | 4.4535 | 3.3385 | 0.87313 | 0.00013923
| 466.15 | 3500000 | 4448.9175 | 3342.3494 | 874.2751 | 0.00014 | 193 | 34.5422 | 4.4489 | 3.3423 | 0.87428 | 0.00014
| 465.15 | 3500000 | 4444.3608 | 3346.2495 | 875.4142 | 0.00014077 | 192 | 34.5422 | 4.4444 | 3.3462 | 0.87541 | 0.00014077
| 464.15 | 3500000 | 4439.8687 | 3350.1663 | 876.5478 | 0.00014155 | 191 | 34.5422 | 4.4399 | 3.3502 | 0.87655 | 0.00014155
| 463.15 | 3500000 | 4435.4409 | 3354.0996 | 877.676 | 0.00014234 | 190 | 34.5422 | 4.4354 | 3.3541 | 0.87768 | 0.00014234
| 462.15 | 3500000 | 4431.0757 | 3358.0493 | 878.7988 | 0.00014314 | 189 | 34.5422 | 4.4311 | 3.358 | 0.8788 | 0.00014314
| 461.15 | 3500000 | 4426.772 | 3362.0154 | 879.9162 | 0.00014395 | 188 | 34.5422 | 4.4268 | 3.362 | 0.87992 | 0.00014395
| 460.15 | 3500000 | 4422.5293 | 3365.9973 | 881.0283 | 0.00014477 | 187 | 34.5422 | 4.4225 | 3.366 | 0.88103 | 0.00014477
| 459.15 | 3500000 | 4418.3467 | 3369.9954 | 882.1352 | 0.00014559 | 186 | 34.5422 | 4.4183 | 3.37 | 0.88214 | 0.00014559
| 458.15 | 3500000 | 4414.2227 | 3374.0095 | 883.2368 | 0.00014643 | 185 | 34.5422 | 4.4142 | 3.374 | 0.88324 | 0.00014643
| 457.15 | 3500000 | 4410.1562 | 3378.0391 | 884.3332 | 0.00014728 | 184 | 34.5422 | 4.4102 | 3.378 | 0.88433 | 0.00014728
| 456.15 | 3500000 | 4406.1465 | 3382.0847 | 885.4244 | 0.00014813 | 183 | 34.5422 | 4.4061 | 3.3821 | 0.88542 | 0.00014813
| 455.15 | 3500000 | 4402.1934 | 3386.1455 | 886.5105 | 0.000149 | 182 | 34.5422 | 4.4022 | 3.3861 | 0.88651 | 0.000149
| 454.15 | 3500000 | 4398.2949 | 3390.2219 | 887.5915 | 0.00014987 | 181 | 34.5422 | 4.3983 | 3.3902 | 0.88759 | 0.00014987
| 453.15 | 3500000 | 4394.4502 | 3394.3137 | 888.6674 | 0.00015076 | 180 | 34.5422 | 4.3945 | 3.3943 | 0.88867 | 0.00015076
| 452.15 | 3500000 | 4390.6592 | 3398.4207 | 889.7383 | 0.00015165 | 179 | 34.5422 | 4.3907 | 3.3984 | 0.88974 | 0.00015165
| 451.15 | 3500000 | 4386.9204 | 3402.5427 | 890.8041 | 0.00015256 | 178 | 34.5422 | 4.3869 | 3.4025 | 0.8908 | 0.00015256
| 450.15 | 3500000 | 4383.2334 | 3406.6797 | 891.865 | 0.00015348 | 177 | 34.5422 | 4.3832 | 3.4067 | 0.89186 | 0.00015348
| 449.15 | 3500000 | 4379.5972 | 3410.8315 | 892.9209 | 0.00015441 | 176 | 34.5422 | 4.3796 | 3.4108 | 0.89292 | 0.00015441
| 448.15 | 3500000 | 4376.0112 | 3414.9983 | 893.9719 | 0.00015535 | 175 | 34.5422 | 4.376 | 3.415 | 0.89397 | 0.00015535
| 447.15 | 3500000 | 4372.4741 | 3419.1797 | 895.018 | 0.0001563 | 174 | 34.5422 | 4.3725 | 3.4192 | 0.89502 | 0.0001563
| 446.15 | 3500000 | 4368.9854 | 3423.3755 | 896.0593 | 0.00015726 | 173 | 34.5422 | 4.369 | 3.4234 | 0.89606 | 0.00015726
| 445.15 | 3500000 | 4365.5444 | 3427.5859 | 897.0956 | 0.00015824 | 172 | 34.5422 | 4.3655 | 3.4276 | 0.8971 | 0.00015824
| 444.15 | 3500000 | 4362.1504 | 3431.8105 | 898.1273 | 0.00015923 | 171 | 34.5422 | 4.3622 | 3.4318 | 0.89813 | 0.00015923
| 443.15 | 3500000 | 4358.8027 | 3436.0493 | 899.154 | 0.00016023 | 170 | 34.5422 | 4.3588 | 3.436 | 0.89915 | 0.00016023
| 442.15 | 3500000 | 4355.5005 | 3440.3025 | 900.176 | 0.00016124 | 169 | 34.5422 | 4.3555 | 3.4403 | 0.90018 | 0.00016124
| 441.15 | 3500000 | 4352.2432 | 3444.5693 | 901.1933 | 0.00016227 | 168 | 34.5422 | 4.3522 | 3.4446 | 0.90119 | 0.00016227
| 440.15 | 3500000 | 4349.0298 | 3448.8503 | 902.2059 | 0.0001633 | 167 | 34.5422 | 4.349 | 3.4489 | 0.90221 | 0.0001633
| 439.15 | 3500000 | 4345.8604 | 3453.1453 | 903.2137 | 0.00016436 | 166 | 34.5422 | 4.3459 | 3.4531 | 0.90321 | 0.00016436
| 438.15 | 3500000 | 4342.7334 | 3457.4536 | 904.2169 | 0.00016542 | 165 | 34.5422 | 4.3427 | 3.4575 | 0.90422 | 0.00016542
| 437.15 | 3500000 | 4339.6489 | 3461.7759 | 905.2154 | 0.0001665 | 164 | 34.5422 | 4.3396 | 3.4618 | 0.90522 | 0.0001665
| 436.15 | 3500000 | 4336.606 | 3466.1113 | 906.2092 | 0.00016759 | 163 | 34.5422 | 4.3366 | 3.4661 | 0.90621 | 0.00016759
| 435.15 | 3500000 | 4333.6035 | 3470.4604 | 907.1985 | 0.0001687 | 162 | 34.5422 | 4.3336 | 3.4705 | 0.9072 | 0.0001687
| 434.15 | 3500000 | 4330.6421 | 3474.823 | 908.1832 | 0.00016982 | 161 | 34.5422 | 4.3306 | 3.4748 | 0.90818 | 0.00016982
| 433.15 | 3500000 | 4327.7202 | 3479.1985 | 909.1632 | 0.00017096 | 160 | 34.5422 | 4.3277 | 3.4792 | 0.90916 | 0.00017096
| 432.15 | 3500000 | 4324.8374 | 3483.5874 | 910.1387 | 0.00017211 | 159 | 34.5422 | 4.3248 | 3.4836 | 0.91014 | 0.00017211
| 431.15 | 3500000 | 4321.9937 | 3487.9893 | 911.1097 | 0.00017328 | 158 | 34.5422 | 4.322 | 3.488 | 0.91111 | 0.00017328
| 430.15 | 3500000 | 4319.188 | 3492.4041 | 912.0761 | 0.00017447 | 157 | 34.5422 | 4.3192 | 3.4924 | 0.91208 | 0.00017447
| 429.15 | 3500000 | 4316.4194 | 3496.8318 | 913.038 | 0.00017567 | 156 | 34.5422 | 4.3164 | 3.4968 | 0.91304 | 0.00017567
| 428.15 | 3500000 | 4313.6885 | 3501.2722 | 913.9955 | 0.00017688 | 155 | 34.5422 | 4.3137 | 3.5013 | 0.914 | 0.00017688
| 427.15 | 3500000 | 4310.9937 | 3505.7253 | 914.9484 | 0.00017812 | 154 | 34.5422 | 4.311 | 3.5057 | 0.91495 | 0.00017812
| 426.15 | 3500000 | 4308.335 | 3510.1912 | 915.8969 | 0.00017937 | 153 | 34.5422 | 4.3083 | 3.5102 | 0.9159 | 0.00017937
| 425.15 | 3500000 | 4305.7114 | 3514.6694 | 916.8409 | 0.00018064 | 152 | 34.5422 | 4.3057 | 3.5147 | 0.91684 | 0.00018064
| 424.15 | 3500000 | 4303.1235 | 3519.1602 | 917.7805 | 0.00018192 | 151 | 34.5422 | 4.3031 | 3.5192 | 0.91778 | 0.00018192
| 423.15 | 3500000 | 4300.5698 | 3523.6631 | 918.7156 | 0.00018322 | 150 | 34.5422 | 4.3006 | 3.5237 | 0.91872 | 0.00018322
| 422.15 | 3500000 | 4298.0503 | 3528.1785 | 919.6463 | 0.00018455 | 149 | 34.5422 | 4.2981 | 3.5282 | 0.91965 | 0.00018455
| 421.15 | 3500000 | 4295.5645 | 3532.7061 | 920.5726 | 0.00018589 | 148 | 34.5422 | 4.2956 | 3.5327 | 0.92057 | 0.00018589
| 420.15 | 3500000 | 4293.1113 | 3537.2456 | 921.4945 | 0.00018725 | 147 | 34.5422 | 4.2931 | 3.5372 | 0.92149 | 0.00018725
| 419.15 | 3500000 | 4290.6914 | 3541.7971 | 922.412 | 0.00018863 | 146 | 34.5422 | 4.2907 | 3.5418 | 0.92241 | 0.00018863
| 418.15 | 3500000 | 4288.3037 | 3546.3608 | 923.3252 | 0.00019003 | 145 | 34.5422 | 4.2883 | 3.5464 | 0.92333 | 0.00019003
| 417.15 | 3500000 | 4285.9478 | 3550.9363 | 924.234 | 0.00019145 | 144 | 34.5422 | 4.2859 | 3.5509 | 0.92423 | 0.00019145
| 416.15 | 3500000 | 4283.6235 | 3555.5234 | 925.1384 | 0.00019289 | 143 | 34.5422 | 4.2836 | 3.5555 | 0.92514 | 0.00019289
| 415.15 | 3500000 | 4281.3301 | 3560.1223 | 926.0385 | 0.00019435 | 142 | 34.5422 | 4.2813 | 3.5601 | 0.92604 | 0.00019435
| 414.15 | 3500000 | 4279.0674 | 3564.7329 | 926.9342 | 0.00019584 | 141 | 34.5422 | 4.2791 | 3.5647 | 0.92693 | 0.00019584
| 413.15 | 3500000 | 4276.835 | 3569.3547 | 927.8256 | 0.00019734 | 140 | 34.5422 | 4.2768 | 3.5694 | 0.92783 | 0.00019734
| 412.15 | 3500000 | 4274.6323 | 3573.9883 | 928.7126 | 0.00019887 | 139 | 34.5422 | 4.2746 | 3.574 | 0.92871 | 0.00019887
| 411.15 | 3500000 | 4272.459 | 3578.6333 | 929.5954 | 0.00020042 | 138 | 34.5422 | 4.2725 | 3.5786 | 0.9296 | 0.00020042
| 410.15 | 3500000 | 4270.3154 | 3583.2896 | 930.4738 | 0.000202 | 137 | 34.5422 | 4.2703 | 3.5833 | 0.93047 | 0.000202
| 409.15 | 3500000 | 4268.2002 | 3587.9568 | 931.3479 | 0.0002036 | 136 | 34.5422 | 4.2682 | 3.588 | 0.93135 | 0.0002036
| 408.15 | 3500000 | 4266.1138 | 3592.6355 | 932.2177 | 0.00020522 | 135 | 34.5422 | 4.2661 | 3.5926 | 0.93222 | 0.00020522
| 407.15 | 3500000 | 4264.0552 | 3597.325 | 933.0832 | 0.00020687 | 134 | 34.5422 | 4.2641 | 3.5973 | 0.93308 | 0.00020687
| 406.15 | 3500000 | 4262.0244 | 3602.0256 | 933.9444 | 0.00020855 | 133 | 34.5422 | 4.262 | 3.602 | 0.93394 | 0.00020855
| 405.15 | 3500000 | 4260.0215 | 3606.7373 | 934.8013 | 0.00021025 | 132 | 34.5422 | 4.26 | 3.6067 | 0.9348 | 0.00021025
| 404.15 | 3500000 | 4258.0454 | 3611.4597 | 935.6539 | 0.00021198 | 131 | 34.5422 | 4.258 | 3.6115 | 0.93565 | 0.00021198
| 403.15 | 3500000 | 4256.0962 | 3616.1926 | 936.5022 | 0.00021373 | 130 | 34.5422 | 4.2561 | 3.6162 | 0.9365 | 0.00021373
| 402.15 | 3500000 | 4254.1733 | 3620.9365 | 937.3462 | 0.00021551 | 129 | 34.5422 | 4.2542 | 3.6209 | 0.93735 | 0.00021551
| 401.15 | 3500000 | 4252.2773 | 3625.6909 | 938.1859 | 0.00021733 | 128 | 34.5422 | 4.2523 | 3.6257 | 0.93819 | 0.00021733
| 400.15 | 3500000 | 4250.4067 | 3630.4558 | 939.0213 | 0.00021917 | 127 | 34.5422 | 4.2504 | 3.6305 | 0.93902 | 0.00021917
| 399.15 | 3500000 | 4248.562 | 3635.2312 | 939.8524 | 0.00022104 | 126 | 34.5422 | 4.2486 | 3.6352 | 0.93985 | 0.00022104
| 398.15 | 3500000 | 4246.7432 | 3640.0168 | 940.6793 | 0.00022294 | 125 | 34.5422 | 4.2467 | 3.64 | 0.94068 | 0.00022294
| 397.15 | 3500000 | 4244.9487 | 3644.813 | 941.5018 | 0.00022487 | 124 | 34.5422 | 4.2449 | 3.6448 | 0.9415 | 0.00022487
| 396.15 | 3500000 | 4243.1797 | 3649.6189 | 942.32 | 0.00022683 | 123 | 34.5422 | 4.2432 | 3.6496 | 0.94232 | 0.00022683
| 395.15 | 3500000 | 4241.4355 | 3654.4353 | 943.1339 | 0.00022883 | 122 | 34.5422 | 4.2414 | 3.6544 | 0.94313 | 0.00022883
| 394.15 | 3500000 | 4239.7153 | 3659.2615 | 943.9435 | 0.00023086 | 121 | 34.5422 | 4.2397 | 3.6593 | 0.94394 | 0.00023086
| 393.15 | 3500000 | 4238.0195 | 3664.0977 | 944.7488 | 0.00023292 | 120 | 34.5422 | 4.238 | 3.6641 | 0.94475 | 0.00023292
| 392.15 | 3500000 | 4236.3477 | 3668.9436 | 945.5499 | 0.00023502 | 119 | 34.5422 | 4.2363 | 3.6689 | 0.94555 | 0.00023502
| 391.15 | 3500000 | 4234.6997 | 3673.7991 | 946.3466 | 0.00023715 | 118 | 34.5422 | 4.2347 | 3.6738 | 0.94635 | 0.00023715
| 390.15 | 3500000 | 4233.0752 | 3678.6646 | 947.1389 | 0.00023932 | 117 | 34.5422 | 4.2331 | 3.6787 | 0.94714 | 0.00023932
| 389.15 | 3500000 | 4231.4736 | 3683.5393 | 947.9269 | 0.00024152 | 116 | 34.5422 | 4.2315 | 3.6835 | 0.94793 | 0.00024152
| 388.15 | 3500000 | 4229.8955 | 3688.4236 | 948.7106 | 0.00024377 | 115 | 34.5422 | 4.2299 | 3.6884 | 0.94871 | 0.00024377
| 387.15 | 3500000 | 4228.3403 | 3693.3169 | 949.49 | 0.00024605 | 114 | 34.5422 | 4.2283 | 3.6933 | 0.94949 | 0.00024605
| 386.15 | 3500000 | 4226.8081 | 3698.2197 | 950.265 | 0.00024837 | 113 | 34.5422 | 4.2268 | 3.6982 | 0.95027 | 0.00024837
| 385.15 | 3500000 | 4225.2983 | 3703.1316 | 951.0356 | 0.00025074 | 112 | 34.5422 | 4.2253 | 3.7031 | 0.95104 | 0.00025074
| 384.15 | 3500000 | 4223.811 | 3708.0522 | 951.8019 | 0.00025314 | 111 | 34.5422 | 4.2238 | 3.7081 | 0.9518 | 0.00025314
| 383.15 | 3500000 | 4222.3457 | 3712.9819 | 952.5638 | 0.00025559 | 110 | 34.5422 | 4.2223 | 3.713 | 0.95256 | 0.00025559
| 382.15 | 3500000 | 4220.9028 | 3717.9204 | 953.3214 | 0.00025808 | 109 | 34.5422 | 4.2209 | 3.7179 | 0.95332 | 0.00025808
| 381.15 | 3500000 | 4219.4814 | 3722.8672 | 954.0745 | 0.00026062 | 108 | 34.5422 | 4.2195 | 3.7229 | 0.95407 | 0.00026062
| 380.15 | 3500000 | 4218.082 | 3727.8228 | 954.8232 | 0.0002632 | 107 | 34.5422 | 4.2181 | 3.7278 | 0.95482 | 0.0002632
| 379.15 | 3500000 | 4216.7041 | 3732.7864 | 955.5676 | 0.00026583 | 106 | 34.5422 | 4.2167 | 3.7328 | 0.95557 | 0.00026583
| 378.15 | 3500000 | 4215.3477 | 3737.7583 | 956.3074 | 0.00026851 | 105 | 34.5422 | 4.2153 | 3.7378 | 0.95631 | 0.00026851
| 377.15 | 3500000 | 4214.0127 | 3742.7383 | 957.0429 | 0.00027123 | 104 | 34.5422 | 4.214 | 3.7427 | 0.95704 | 0.00027123
| 376.15 | 3500000 | 4212.6987 | 3747.7261 | 957.7739 | 0.00027401 | 103 | 34.5422 | 4.2127 | 3.7477 | 0.95777 | 0.00027401
| 375.15 | 3500000 | 4211.4062 | 3752.7217 | 958.5004 | 0.00027684 | 102 | 34.5422 | 4.2114 | 3.7527 | 0.9585 | 0.00027684
| 374.15 | 3500000 | 4210.1348 | 3757.7249 | 959.2224 | 0.00027972 | 101 | 34.5422 | 4.2101 | 3.7577 | 0.95922 | 0.00027972
| 373.15 | 3500000 | 4208.8838 | 3762.7354 | 959.9399 | 0.00028265 | 100 | 34.5422 | 4.2089 | 3.7627 | 0.95994 | 0.00028265
| 372.15 | 3500000 | 4207.6538 | 3767.7529 | 960.653 | 0.00028565 | 99 | 34.5422 | 4.2077 | 3.7678 | 0.96065 | 0.00028565
| 371.15 | 3500000 | 4206.4443 | 3772.7778 | 961.3615 | 0.00028869 | 98 | 34.5422 | 4.2064 | 3.7728 | 0.96136 | 0.00028869
| 370.15 | 3500000 | 4205.2554 | 3777.8093 | 962.0654 | 0.0002918 | 97 | 34.5422 | 4.2053 | 3.7778 | 0.96207 | 0.0002918
| 369.15 | 3500000 | 4204.0874 | 3782.8474 | 962.7648 | 0.00029497 | 96 | 34.5422 | 4.2041 | 3.7828 | 0.96276 | 0.00029497
| 368.15 | 3500000 | 4202.9395 | 3787.8918 | 963.4595 | 0.0002982 | 95 | 34.5422 | 4.2029 | 3.7879 | 0.96346 | 0.0002982
| 367.15 | 3500000 | 4201.812 | 3792.9426 | 964.1497 | 0.00030149 | 94 | 34.5422 | 4.2018 | 3.7929 | 0.96415 | 0.00030149
| 366.15 | 3500000 | 4200.7046 | 3797.9993 | 964.8353 | 0.00030484 | 93 | 34.5422 | 4.2007 | 3.798 | 0.96484 | 0.00030484
| 365.15 | 3500000 | 4199.6172 | 3803.0615 | 965.5162 | 0.00030827 | 92 | 34.5422 | 4.1996 | 3.8031 | 0.96552 | 0.00030827
| 364.15 | 3500000 | 4198.5503 | 3808.1294 | 966.1924 | 0.00031176 | 91 | 34.5422 | 4.1986 | 3.8081 | 0.96619 | 0.00031176
| 363.15 | 3500000 | 4197.5034 | 3813.2021 | 966.864 | 0.00031532 | 90 | 34.5422 | 4.1975 | 3.8132 | 0.96686 | 0.00031532
| 362.15 | 3500000 | 4196.4766 | 3818.2803 | 967.5308 | 0.00031895 | 89 | 34.5422 | 4.1965 | 3.8183 | 0.96753 | 0.00031895
| 361.15 | 3500000 | 4195.4697 | 3823.3628 | 968.1929 | 0.00032266 | 88 | 34.5422 | 4.1955 | 3.8234 | 0.96819 | 0.00032266
| 360.15 | 3500000 | 4194.4824 | 3828.4495 | 968.8503 | 0.00032645 | 87 | 34.5422 | 4.1945 | 3.8284 | 0.96885 | 0.00032645
| 359.15 | 3500000 | 4193.5151 | 3833.5405 | 969.5029 | 0.00033031 | 86 | 34.5422 | 4.1935 | 3.8335 | 0.9695 | 0.00033031
| 358.15 | 3500000 | 4192.5679 | 3838.635 | 970.1506 | 0.00033425 | 85 | 34.5422 | 4.1926 | 3.8386 | 0.97015 | 0.00033425
| 357.15 | 3500000 | 4191.6401 | 3843.7332 | 970.7935 | 0.00033827 | 84 | 34.5422 | 4.1916 | 3.8437 | 0.97079 | 0.00033827
| 356.15 | 3500000 | 4190.7324 | 3848.834 | 971.4316 | 0.00034238 | 83 | 34.5422 | 4.1907 | 3.8488 | 0.97143 | 0.00034238
| 355.15 | 3500000 | 4189.8442 | 3853.9377 | 972.0648 | 0.00034658 | 82 | 34.5422 | 4.1898 | 3.8539 | 0.97206 | 0.00034658
| 354.15 | 3500000 | 4188.9756 | 3859.0437 | 972.693 | 0.00035087 | 81 | 34.5422 | 4.189 | 3.859 | 0.97269 | 0.00035087
| 353.15 | 3500000 | 4188.1265 | 3864.1516 | 973.3162 | 0.00035525 | 80 | 34.5422 | 4.1881 | 3.8642 | 0.97332 | 0.00035525
| 352.15 | 3500000 | 4187.2974 | 3869.261 | 973.9346 | 0.00035972 | 79 | 34.5422 | 4.1873 | 3.8693 | 0.97393 | 0.00035972
| 351.15 | 3500000 | 4186.4878 | 3874.3713 | 974.5479 | 0.00036429 | 78 | 34.5422 | 4.1865 | 3.8744 | 0.97455 | 0.00036429
| 350.15 | 3500000 | 4185.6978 | 3879.4824 | 975.1561 | 0.00036896 | 77 | 34.5422 | 4.1857 | 3.8795 | 0.97516 | 0.00036896
| 349.15 | 3500000 | 4184.9277 | 3884.5938 | 975.7592 | 0.00037374 | 76 | 34.5422 | 4.1849 | 3.8846 | 0.97576 | 0.00037374
| 348.15 | 3500000 | 4184.1768 | 3889.7046 | 976.3572 | 0.00037862 | 75 | 34.5422 | 4.1842 | 3.8897 | 0.97636 | 0.00037862
| 347.15 | 3500000 | 4183.4458 | 3894.8145 | 976.9501 | 0.00038361 | 74 | 34.5422 | 4.1834 | 3.8948 | 0.97695 | 0.00038361
| 346.15 | 3500000 | 4182.7339 | 3899.9233 | 977.5378 | 0.00038872 | 73 | 34.5422 | 4.1827 | 3.8999 | 0.97754 | 0.00038872
| 345.15 | 3500000 | 4182.042 | 3905.03 | 978.1203 | 0.00039394 | 72 | 34.5422 | 4.182 | 3.905 | 0.97812 | 0.00039394
| 344.15 | 3500000 | 4181.3691 | 3910.1345 | 978.6975 | 0.00039928 | 71 | 34.5422 | 4.1814 | 3.9101 | 0.9787 | 0.00039928
| 343.15 | 3500000 | 4180.7163 | 3915.2358 | 979.2694 | 0.00040475 | 70 | 34.5422 | 4.1807 | 3.9152 | 0.97927 | 0.00040475
| 342.15 | 3500000 | 4180.0825 | 3920.3335 | 979.8359 | 0.00041034 | 69 | 34.5422 | 4.1801 | 3.9203 | 0.97984 | 0.00041034
| 341.15 | 3500000 | 4179.4688 | 3925.427 | 980.3971 | 0.00041607 | 68 | 34.5422 | 4.1795 | 3.9254 | 0.9804 | 0.00041607
| 340.15 | 3500000 | 4178.8745 | 3930.5156 | 980.9528 | 0.00042193 | 67 | 34.5422 | 4.1789 | 3.9305 | 0.98095 | 0.00042193
| 339.15 | 3500000 | 4178.2993 | 3935.5984 | 981.5031 | 0.00042793 | 66 | 34.5422 | 4.1783 | 3.9356 | 0.9815 | 0.00042793
| 338.15 | 3500000 | 4177.7441 | 3940.6753 | 982.0478 | 0.00043408 | 65 | 34.5422 | 4.1777 | 3.9407 | 0.98205 | 0.00043408
| 337.15 | 3500000 | 4177.2085 | 3945.7449 | 982.587 | 0.00044038 | 64 | 34.5422 | 4.1772 | 3.9457 | 0.98259 | 0.00044038
| 336.15 | 3500000 | 4176.6919 | 3950.8066 | 983.1205 | 0.00044683 | 63 | 34.5422 | 4.1767 | 3.9508 | 0.98312 | 0.00044683
| 335.15 | 3500000 | 4176.1953 | 3955.8601 | 983.6484 | 0.00045344 | 62 | 34.5422 | 4.1762 | 3.9559 | 0.98365 | 0.00045344
| 334.15 | 3500000 | 4175.7183 | 3960.9041 | 984.1705 | 0.00046022 | 61 | 34.5422 | 4.1757 | 3.9609 | 0.98417 | 0.00046022
| 333.15 | 3500000 | 4175.2607 | 3965.938 | 984.6869 | 0.00046716 | 60 | 34.5422 | 4.1753 | 3.9659 | 0.98469 | 0.00046716
| 332.15 | 3500000 | 4174.8228 | 3970.9607 | 985.1974 | 0.00047429 | 59 | 34.5422 | 4.1748 | 3.971 | 0.9852 | 0.00047429
| 331.15 | 3500000 | 4174.4043 | 3975.9714 | 985.7021 | 0.00048159 | 58 | 34.5422 | 4.1744 | 3.976 | 0.9857 | 0.00048159
| 330.15 | 3500000 | 4174.0059 | 3980.9692 | 986.2008 | 0.00048909 | 57 | 34.5422 | 4.174 | 3.981 | 0.9862 | 0.00048909
| 329.15 | 3500000 | 4173.6265 | 3985.9534 | 986.6935 | 0.00049678 | 56 | 34.5422 | 4.1736 | 3.986 | 0.98669 | 0.00049678
| 328.15 | 3500000 | 4173.2671 | 3990.9226 | 987.1802 | 0.00050467 | 55 | 34.5422 | 4.1733 | 3.9909 | 0.98718 | 0.00050467
| 327.15 | 3500000 | 4172.9272 | 3995.876 | 987.6608 | 0.00051278 | 54 | 34.5422 | 4.1729 | 3.9959 | 0.98766 | 0.00051278
| 326.15 | 3500000 | 4172.6069 | 4000.8125 | 988.1351 | 0.0005211 | 53 | 34.5422 | 4.1726 | 4.0008 | 0.98814 | 0.0005211
| 325.15 | 3500000 | 4172.3066 | 4005.731 | 988.6033 | 0.00052964 | 52 | 34.5422 | 4.1723 | 4.0057 | 0.9886 | 0.00052964
| 324.15 | 3500000 | 4172.0259 | 4010.6304 | 989.0651 | 0.00053842 | 51 | 34.5422 | 4.172 | 4.0106 | 0.98907 | 0.00053842
| 323.15 | 3500000 | 4171.7646 | 4015.5095 | 989.5205 | 0.00054745 | 50 | 34.5422 | 4.1718 | 4.0155 | 0.98952 | 0.00054745
| 322.15 | 3500000 | 4171.5239 | 4020.3672 | 989.9694 | 0.00055672 | 49 | 34.5422 | 4.1715 | 4.0204 | 0.98997 | 0.00055672
| 321.15 | 3500000 | 4171.3027 | 4025.2021 | 990.4119 | 0.00056625 | 48 | 34.5422 | 4.1713 | 4.0252 | 0.99041 | 0.00056625
| 320.15 | 3500000 | 4171.1016 | 4030.0132 | 990.8477 | 0.00057606 | 47 | 34.5422 | 4.1711 | 4.03 | 0.99085 | 0.00057606
| 319.15 | 3500000 | 4170.9204 | 4034.7991 | 991.2768 | 0.00058615 | 46 | 34.5422 | 4.1709 | 4.0348 | 0.99128 | 0.00058615
| 318.15 | 3500000 | 4170.7593 | 4039.5586 | 991.6992 | 0.00059653 | 45 | 34.5422 | 4.1708 | 4.0396 | 0.9917 | 0.00059653
| 317.15 | 3500000 | 4170.6182 | 4044.29 | 992.1146 | 0.00060721 | 44 | 34.5422 | 4.1706 | 4.0443 | 0.99211 | 0.00060721
| 316.15 | 3500000 | 4170.498 | 4048.9922 | 992.5232 | 0.00061822 | 43 | 34.5422 | 4.1705 | 4.049 | 0.99252 | 0.00061822
| 315.15 | 3500000 | 4170.3979 | 4053.6636 | 992.9247 | 0.00062955 | 42 | 34.5422 | 4.1704 | 4.0537 | 0.99292 | 0.00062955
| 314.15 | 3500000 | 4170.3193 | 4058.3027 | 993.3192 | 0.00064122 | 41 | 34.5422 | 4.1703 | 4.0583 | 0.99332 | 0.00064122
| 313.15 | 3500000 | 4170.2607 | 4062.9082 | 993.7064 | 0.00065326 | 40 | 34.5422 | 4.1703 | 4.0629 | 0.99371 | 0.00065326
| 312.15 | 3500000 | 4170.2241 | 4067.4788 | 994.0862 | 0.00066566 | 39 | 34.5422 | 4.1702 | 4.0675 | 0.99409 | 0.00066566
| 311.15 | 3500000 | 4170.2085 | 4072.0122 | 994.4587 | 0.00067846 | 38 | 34.5422 | 4.1702 | 4.072 | 0.99446 | 0.00067846
| 310.15 | 3500000 | 4170.2148 | 4076.5076 | 994.8237 | 0.00069166 | 37 | 34.5422 | 4.1702 | 4.0765 | 0.99482 | 0.00069166
| 309.15 | 3500000 | 4170.2432 | 4080.9629 | 995.181 | 0.00070528 | 36 | 34.5422 | 4.1702 | 4.081 | 0.99518 | 0.00070528
| 308.15 | 3500000 | 4170.2944 | 4085.3765 | 995.5306 | 0.00071935 | 35 | 34.5422 | 4.1703 | 4.0854 | 0.99553 | 0.00071935
| 307.15 | 3500000 | 4170.3687 | 4089.7468 | 995.8723 | 0.00073388 | 34 | 34.5422 | 4.1704 | 4.0897 | 0.99587 | 0.00073388
| 306.15 | 3500000 | 4170.4663 | 4094.0723 | 996.2061 | 0.00074889 | 33 | 34.5422 | 4.1705 | 4.0941 | 0.99621 | 0.00074889
| 305.15 | 3500000 | 4170.5884 | 4098.3511 | 996.5317 | 0.0007644 | 32 | 34.5422 | 4.1706 | 4.0984 | 0.99653 | 0.0007644
| 304.15 | 3500000 | 4170.7358 | 4102.5815 | 996.8492 | 0.00078044 | 31 | 34.5422 | 4.1707 | 4.1026 | 0.99685 | 0.00078044
| 303.15 | 3500000 | 4170.9087 | 4106.7617 | 997.1582 | 0.00079704 | 30 | 34.5422 | 4.1709 | 4.1068 | 0.99716 | 0.00079704
| 302.15 | 3500000 | 4171.1089 | 4110.8901 | 997.4588 | 0.00081422 | 29 | 34.5422 | 4.1711 | 4.1109 | 0.99746 | 0.00081422
| 301.15 | 3500000 | 4171.3369 | 4114.9644 | 997.7507 | 0.000832 | 28 | 34.5422 | 4.1713 | 4.115 | 0.99775 | 0.000832
| 300.15 | 3500000 | 4171.5938 | 4118.9839 | 998.0338 | 0.00085042 | 27 | 34.5422 | 4.1716 | 4.119 | 0.99803 | 0.00085042
| 299.15 | 3500000 | 4171.8813 | 4122.9453 | 998.308 | 0.00086952 | 26 | 34.5422 | 4.1719 | 4.1229 | 0.99831 | 0.00086952
| 298.15 | 3500000 | 4172.2007 | 4126.8486 | 998.5731 | 0.00088931 | 25 | 34.5422 | 4.1722 | 4.1268 | 0.99857 | 0.00088931
| 297.15 | 3500000 | 4172.5542 | 4130.6904 | 998.8289 | 0.00090985 | 24 | 34.5422 | 4.1726 | 4.1307 | 0.99883 | 0.00090985
| 296.15 | 3500000 | 4172.9434 | 4134.4702 | 999.0751 | 0.00093116 | 23 | 34.5422 | 4.1729 | 4.1345 | 0.99908 | 0.00093116
| 295.15 | 3500000 | 4173.3706 | 4138.1855 | 999.3118 | 0.00095329 | 22 | 34.5422 | 4.1734 | 4.1382 | 0.99931 | 0.00095329
| 294.15 | 3500000 | 4173.8384 | 4141.8354 | 999.5386 | 0.00097628 | 21 | 34.5422 | 4.1738 | 4.1418 | 0.99954 | 0.00097628
| 293.15 | 3500000 | 4174.3496 | 4145.4175 | 999.7554 | 0.0010002 | 20 | 34.5422 | 4.1743 | 4.1454 | 0.99976 | 0.0010002
| 292.15 | 3500000 | 4174.9067 | 4148.9302 | 999.962 | 0.001025 | 19 | 34.5422 | 4.1749 | 4.1489 | 0.99996 | 0.001025
| 291.15 | 3500000 | 4175.5146 | 4152.3726 | 1000.158 | 0.0010509 | 18 | 34.5422 | 4.1755 | 4.1524 | 1.0002 | 0.0010509
| 290.15 | 3500000 | 4176.1758 | 4155.7427 | 1000.3434 | 0.0010779 | 17 | 34.5422 | 4.1762 | 4.1557 | 1.0003 | 0.0010779
| 289.15 | 3500000 | 4176.8955 | 4159.0391 | 1000.5178 | 0.0011059 | 16 | 34.5422 | 4.1769 | 4.159 | 1.0005 | 0.0011059
| 288.15 | 3500000 | 4177.6782 | 4162.2607 | 1000.681 | 0.0011352 | 15 | 34.5422 | 4.1777 | 4.1623 | 1.0007 | 0.0011352
| 287.15 | 3500000 | 4178.5298 | 4165.4062 | 1000.8328 | 0.0011658 | 14 | 34.5422 | 4.1785 | 4.1654 | 1.0008 | 0.0011658
| 286.15 | 3500000 | 4179.4561 | 4168.4741 | 1000.9728 | 0.0011976 | 13 | 34.5422 | 4.1795 | 4.1685 | 1.001 | 0.0011976
| 285.15 | 3500000 | 4180.4639 | 4171.4644 | 1001.1008 | 0.001231 | 12 | 34.5422 | 4.1805 | 4.1715 | 1.0011 | 0.001231
| 284.15 | 3500000 | 4181.5605 | 4174.375 | 1001.2165 | 0.0012658 | 11 | 34.5422 | 4.1816 | 4.1744 | 1.0012 | 0.0012658
| 283.15 | 3500000 | 4182.7549 | 4177.2061 | 1001.3195 | 0.0013022 | 10 | 34.5422 | 4.1828 | 4.1772 | 1.0013 | 0.0013022
| 282.15 | 3500000 | 4184.0562 | 4179.957 | 1001.4094 | 0.0013404 | 9 | 34.5422 | 4.1841 | 4.18 | 1.0014 | 0.0013404
| 281.15 | 3500000 | 4185.4746 | 4182.627 | 1001.486 | 0.0013804 | 8 | 34.5422 | 4.1855 | 4.1826 | 1.0015 | 0.0013804
| 280.15 | 3500000 | 4187.0215 | 4185.2158 | 1001.5489 | 0.0014223 | 7 | 34.5422 | 4.187 | 4.1852 | 1.0015 | 0.0014223
| 279.15 | 3500000 | 4188.7104 | 4187.7236 | 1001.5976 | 0.0014663 | 6 | 34.5422 | 4.1887 | 4.1877 | 1.0016 | 0.0014663
| 278.15 | 3500000 | 4190.5547 | 4190.1509 | 1001.6317 | 0.0015126 | 5 | 34.5422 | 4.1906 | 4.1902 | 1.0016 | 0.0015126
| 277.15 | 3500000 | 4192.5708 | 4192.498 | 1001.6508 | 0.0015612 | 4 | 34.5422 | 4.1926 | 4.1925 | 1.0017 | 0.0015612
| 276.15 | 3500000 | 4194.7764 | 4194.7656 | 1001.6543 | 0.0016124 | 3 | 34.5422 | 4.1948 | 4.1948 | 1.0017 | 0.0016124
| 275.15 | 3500000 | 4197.1899 | 4196.9546 | 1001.6418 | 0.0016663 | 2 | 34.5422 | 4.1972 | 4.197 | 1.0016 | 0.0016663
| 274.15 | 3500000 | 4199.8335 | 4199.0659 | 1001.6128 | 0.0017231 | 0.99999 | 34.5422 | 4.1998 | 4.1991 | 1.0016 | 0.0017231
| 273.15 | 3500000 | 4202.7305 | 4201.1016 | 1001.5666 | 0.0017831 | -6.1035e-06 | 34.5422 | 4.2027 | 4.2011 | 1.0016 | 0.0017831
| 473.15 | 3000000 | 4485.6035 | 3315.9001 | 865.7667 | 0.00013468 | 200 | 29.6076 | 4.4856 | 3.3159 | 0.86577 | 0.00013468
| 472.15 | 3000000 | 4480.5176 | 3319.6807 | 866.9481 | 0.0001354 | 199 | 29.6076 | 4.4805 | 3.3197 | 0.86695 | 0.0001354
| 471.15 | 3000000 | 4475.5059 | 3323.4788 | 868.1235 | 0.00013613 | 198 | 29.6076 | 4.4755 | 3.3235 | 0.86812 | 0.00013613
| 470.15 | 3000000 | 4470.5669 | 3327.2944 | 869.2933 | 0.00013686 | 197 | 29.6076 | 4.4706 | 3.3273 | 0.86929 | 0.00013686
| 469.15 | 3000000 | 4465.7002 | 3331.1272 | 870.4572 | 0.0001376 | 196 | 29.6076 | 4.4657 | 3.3311 | 0.87046 | 0.0001376
| 468.15 | 3000000 | 4460.9038 | 3334.9771 | 871.6155 | 0.00013835 | 195 | 29.6076 | 4.4609 | 3.335 | 0.87162 | 0.00013835
| 467.15 | 3000000 | 4456.1768 | 3338.844 | 872.7682 | 0.00013911 | 194 | 29.6076 | 4.4562 | 3.3388 | 0.87277 | 0.00013911
| 466.15 | 3000000 | 4451.5176 | 3342.728 | 873.9153 | 0.00013987 | 193 | 29.6076 | 4.4515 | 3.3427 | 0.87392 | 0.00013987
| 465.15 | 3000000 | 4446.9258 | 3346.6287 | 875.0568 | 0.00014065 | 192 | 29.6076 | 4.4469 | 3.3466 | 0.87506 | 0.00014065
| 464.15 | 3000000 | 4442.3994 | 3350.5461 | 876.1927 | 0.00014143 | 191 | 29.6076 | 4.4424 | 3.3505 | 0.87619 | 0.00014143
| 463.15 | 3000000 | 4437.9375 | 3354.48 | 877.3233 | 0.00014222 | 190 | 29.6076 | 4.4379 | 3.3545 | 0.87732 | 0.00014222
| 462.15 | 3000000 | 4433.5396 | 3358.4302 | 878.4484 | 0.00014302 | 189 | 29.6076 | 4.4335 | 3.3584 | 0.87845 | 0.00014302
| 461.15 | 3000000 | 4429.2041 | 3362.397 | 879.5681 | 0.00014383 | 188 | 29.6076 | 4.4292 | 3.3624 | 0.87957 | 0.00014383
| 460.15 | 3000000 | 4424.9297 | 3366.3799 | 880.6825 | 0.00014464 | 187 | 29.6076 | 4.4249 | 3.3664 | 0.88068 | 0.00014464
| 459.15 | 3000000 | 4420.7158 | 3370.3787 | 881.7916 | 0.00014547 | 186 | 29.6076 | 4.4207 | 3.3704 | 0.88179 | 0.00014547
| 458.15 | 3000000 | 4416.5615 | 3374.3936 | 882.8954 | 0.00014631 | 185 | 29.6076 | 4.4166 | 3.3744 | 0.8829 | 0.00014631
| 457.15 | 3000000 | 4412.4658 | 3378.4243 | 883.9939 | 0.00014715 | 184 | 29.6076 | 4.4125 | 3.3784 | 0.88399 | 0.00014715
| 456.15 | 3000000 | 4408.4272 | 3382.4707 | 885.0873 | 0.00014801 | 183 | 29.6076 | 4.4084 | 3.3825 | 0.88509 | 0.00014801
| 455.15 | 3000000 | 4404.4453 | 3386.5327 | 886.1754 | 0.00014887 | 182 | 29.6076 | 4.4044 | 3.3865 | 0.88618 | 0.00014887
| 454.15 | 3000000 | 4400.5186 | 3390.6104 | 887.2585 | 0.00014975 | 181 | 29.6076 | 4.4005 | 3.3906 | 0.88726 | 0.00014975
| 453.15 | 3000000 | 4396.647 | 3394.7034 | 888.3364 | 0.00015063 | 180 | 29.6076 | 4.3966 | 3.3947 | 0.88834 | 0.00015063
| 452.15 | 3000000 | 4392.8291 | 3398.8115 | 889.4093 | 0.00015153 | 179 | 29.6076 | 4.3928 | 3.3988 | 0.88941 | 0.00015153
| 451.15 | 3000000 | 4389.0645 | 3402.9351 | 890.4772 | 0.00015244 | 178 | 29.6076 | 4.3891 | 3.4029 | 0.89048 | 0.00015244
| 450.15 | 3000000 | 4385.3516 | 3407.0735 | 891.54 | 0.00015336 | 177 | 29.6076 | 4.3854 | 3.4071 | 0.89154 | 0.00015336
| 449.15 | 3000000 | 4381.6899 | 3411.2268 | 892.5978 | 0.00015428 | 176 | 29.6076 | 4.3817 | 3.4112 | 0.8926 | 0.00015428
| 448.15 | 3000000 | 4378.0791 | 3415.395 | 893.6508 | 0.00015522 | 175 | 29.6076 | 4.3781 | 3.4154 | 0.89365 | 0.00015522
| 447.15 | 3000000 | 4374.5181 | 3419.5779 | 894.6987 | 0.00015618 | 174 | 29.6076 | 4.3745 | 3.4196 | 0.8947 | 0.00015618
| 446.15 | 3000000 | 4371.0054 | 3423.7754 | 895.7418 | 0.00015714 | 173 | 29.6076 | 4.371 | 3.4238 | 0.89574 | 0.00015714
| 445.15 | 3000000 | 4367.5415 | 3427.9875 | 896.78 | 0.00015812 | 172 | 29.6076 | 4.3675 | 3.428 | 0.89678 | 0.00015812
| 444.15 | 3000000 | 4364.1245 | 3432.2139 | 897.8134 | 0.0001591 | 171 | 29.6076 | 4.3641 | 3.4322 | 0.89781 | 0.0001591
| 443.15 | 3000000 | 4360.7544 | 3436.4548 | 898.842 | 0.0001601 | 170 | 29.6076 | 4.3608 | 3.4365 | 0.89884 | 0.0001601
| 442.15 | 3000000 | 4357.4302 | 3440.7097 | 899.8657 | 0.00016112 | 169 | 29.6076 | 4.3574 | 3.4407 | 0.89987 | 0.00016112
| 441.15 | 3000000 | 4354.1514 | 3444.9788 | 900.8847 | 0.00016214 | 168 | 29.6076 | 4.3542 | 3.445 | 0.90088 | 0.00016214
| 440.15 | 3000000 | 4350.917 | 3449.2617 | 901.899 | 0.00016318 | 167 | 29.6076 | 4.3509 | 3.4493 | 0.9019 | 0.00016318
| 439.15 | 3000000 | 4347.7271 | 3453.5588 | 902.9085 | 0.00016423 | 166 | 29.6076 | 4.3477 | 3.4536 | 0.90291 | 0.00016423
| 438.15 | 3000000 | 4344.5796 | 3457.8694 | 903.9133 | 0.0001653 | 165 | 29.6076 | 4.3446 | 3.4579 | 0.90391 | 0.0001653
| 437.15 | 3000000 | 4341.4751 | 3462.1938 | 904.9135 | 0.00016638 | 164 | 29.6076 | 4.3415 | 3.4622 | 0.90491 | 0.00016638
| 436.15 | 3000000 | 4338.4126 | 3466.532 | 905.909 | 0.00016747 | 163 | 29.6076 | 4.3384 | 3.4665 | 0.90591 | 0.00016747
| 435.15 | 3000000 | 4335.3916 | 3470.8833 | 906.8998 | 0.00016858 | 162 | 29.6076 | 4.3354 | 3.4709 | 0.9069 | 0.00016858
| 434.15 | 3000000 | 4332.4111 | 3475.2483 | 907.886 | 0.0001697 | 161 | 29.6076 | 4.3324 | 3.4752 | 0.90789 | 0.0001697
| 433.15 | 3000000 | 4329.4712 | 3479.6265 | 908.8677 | 0.00017084 | 160 | 29.6076 | 4.3295 | 3.4796 | 0.90887 | 0.00017084
| 432.15 | 3000000 | 4326.5708 | 3484.0181 | 909.8447 | 0.00017199 | 159 | 29.6076 | 4.3266 | 3.484 | 0.90984 | 0.00017199
| 431.15 | 3000000 | 4323.709 | 3488.4226 | 910.8172 | 0.00017316 | 158 | 29.6076 | 4.3237 | 3.4884 | 0.91082 | 0.00017316
| 430.15 | 3000000 | 4320.8857 | 3492.8401 | 911.7851 | 0.00017434 | 157 | 29.6076 | 4.3209 | 3.4928 | 0.91179 | 0.00017434
| 429.15 | 3000000 | 4318.1006 | 3497.2708 | 912.7485 | 0.00017554 | 156 | 29.6076 | 4.3181 | 3.4973 | 0.91275 | 0.00017554
| 428.15 | 3000000 | 4315.3525 | 3501.7141 | 913.7074 | 0.00017676 | 155 | 29.6076 | 4.3154 | 3.5017 | 0.91371 | 0.00017676
| 427.15 | 3000000 | 4312.6416 | 3506.1702 | 914.6617 | 0.00017799 | 154 | 29.6076 | 4.3126 | 3.5062 | 0.91466 | 0.00017799
| 426.15 | 3000000 | 4309.9668 | 3510.6392 | 915.6116 | 0.00017924 | 153 | 29.6076 | 4.31 | 3.5106 | 0.91561 | 0.00017924
| 425.15 | 3000000 | 4307.3281 | 3515.1206 | 916.557 | 0.00018051 | 152 | 29.6076 | 4.3073 | 3.5151 | 0.91656 | 0.00018051
| 424.15 | 3000000 | 4304.7246 | 3519.6145 | 917.498 | 0.00018179 | 151 | 29.6076 | 4.3047 | 3.5196 | 0.9175 | 0.00018179
| 423.15 | 3000000 | 4302.1558 | 3524.1208 | 918.4345 | 0.0001831 | 150 | 29.6076 | 4.3022 | 3.5241 | 0.91843 | 0.0001831
| 422.15 | 3000000 | 4299.6216 | 3528.6396 | 919.3665 | 0.00018442 | 149 | 29.6076 | 4.2996 | 3.5286 | 0.91937 | 0.00018442
| 421.15 | 3000000 | 4297.1211 | 3533.1707 | 920.2942 | 0.00018576 | 148 | 29.6076 | 4.2971 | 3.5332 | 0.92029 | 0.00018576
| 420.15 | 3000000 | 4294.6543 | 3537.7136 | 921.2174 | 0.00018712 | 147 | 29.6076 | 4.2947 | 3.5377 | 0.92122 | 0.00018712
| 419.15 | 3000000 | 4292.2202 | 3542.269 | 922.1362 | 0.0001885 | 146 | 29.6076 | 4.2922 | 3.5423 | 0.92214 | 0.0001885
| 418.15 | 3000000 | 4289.8188 | 3546.8362 | 923.0507 | 0.0001899 | 145 | 29.6076 | 4.2898 | 3.5468 | 0.92305 | 0.0001899
| 417.15 | 3000000 | 4287.4497 | 3551.4153 | 923.9607 | 0.00019132 | 144 | 29.6076 | 4.2874 | 3.5514 | 0.92396 | 0.00019132
| 416.15 | 3000000 | 4285.1118 | 3556.0063 | 924.8663 | 0.00019276 | 143 | 29.6076 | 4.2851 | 3.556 | 0.92487 | 0.00019276
| 415.15 | 3000000 | 4282.8057 | 3560.6091 | 925.7676 | 0.00019423 | 142 | 29.6076 | 4.2828 | 3.5606 | 0.92577 | 0.00019423
| 414.15 | 3000000 | 4280.5308 | 3565.2236 | 926.6646 | 0.00019571 | 141 | 29.6076 | 4.2805 | 3.5652 | 0.92666 | 0.00019571
| 413.15 | 3000000 | 4278.2856 | 3569.8499 | 927.5571 | 0.00019722 | 140 | 29.6076 | 4.2783 | 3.5698 | 0.92756 | 0.00019722
| 412.15 | 3000000 | 4276.0713 | 3574.4875 | 928.4454 | 0.00019874 | 139 | 29.6076 | 4.2761 | 3.5745 | 0.92845 | 0.00019874
| 411.15 | 3000000 | 4273.8862 | 3579.1367 | 929.3293 | 0.0002003 | 138 | 29.6076 | 4.2739 | 3.5791 | 0.92933 | 0.0002003
| 410.15 | 3000000 | 4271.731 | 3583.7971 | 930.2089 | 0.00020187 | 137 | 29.6076 | 4.2717 | 3.5838 | 0.93021 | 0.00020187
| 409.15 | 3000000 | 4269.6045 | 3588.469 | 931.0841 | 0.00020347 | 136 | 29.6076 | 4.2696 | 3.5885 | 0.93108 | 0.00020347
| 408.15 | 3000000 | 4267.5068 | 3593.1521 | 931.955 | 0.0002051 | 135 | 29.6076 | 4.2675 | 3.5932 | 0.93196 | 0.0002051
| 407.15 | 3000000 | 4265.4375 | 3597.8462 | 932.8216 | 0.00020674 | 134 | 29.6076 | 4.2654 | 3.5978 | 0.93282 | 0.00020674
| 406.15 | 3000000 | 4263.396 | 3602.5515 | 933.6838 | 0.00020842 | 133 | 29.6076 | 4.2634 | 3.6026 | 0.93368 | 0.00020842
| 405.15 | 3000000 | 4261.3823 | 3607.2676 | 934.5418 | 0.00021012 | 132 | 29.6076 | 4.2614 | 3.6073 | 0.93454 | 0.00021012
| 404.15 | 3000000 | 4259.3965 | 3611.9949 | 935.3954 | 0.00021185 | 131 | 29.6076 | 4.2594 | 3.612 | 0.9354 | 0.00021185
| 403.15 | 3000000 | 4257.437 | 3616.7329 | 936.2448 | 0.0002136 | 130 | 29.6076 | 4.2574 | 3.6167 | 0.93624 | 0.0002136
| 402.15 | 3000000 | 4255.5049 | 3621.4817 | 937.0898 | 0.00021538 | 129 | 29.6076 | 4.2555 | 3.6215 | 0.93709 | 0.00021538
| 401.15 | 3000000 | 4253.5986 | 3626.2412 | 937.9305 | 0.0002172 | 128 | 29.6076 | 4.2536 | 3.6262 | 0.93793 | 0.0002172
| 400.15 | 3000000 | 4251.7192 | 3631.0112 | 938.767 | 0.00021904 | 127 | 29.6076 | 4.2517 | 3.631 | 0.93877 | 0.00021904
| 399.15 | 3000000 | 4249.8652 | 3635.7917 | 939.5991 | 0.00022091 | 126 | 29.6076 | 4.2499 | 3.6358 | 0.9396 | 0.00022091
| 398.15 | 3000000 | 4248.0371 | 3640.5828 | 940.4268 | 0.00022281 | 125 | 29.6076 | 4.248 | 3.6406 | 0.94043 | 0.00022281
| 397.15 | 3000000 | 4246.2344 | 3645.384 | 941.2503 | 0.00022474 | 124 | 29.6076 | 4.2462 | 3.6454 | 0.94125 | 0.00022474
| 396.15 | 3000000 | 4244.4565 | 3650.1958 | 942.0695 | 0.0002267 | 123 | 29.6076 | 4.2445 | 3.6502 | 0.94207 | 0.0002267
| 395.15 | 3000000 | 4242.7041 | 3655.0176 | 942.8843 | 0.0002287 | 122 | 29.6076 | 4.2427 | 3.655 | 0.94288 | 0.0002287
| 394.15 | 3000000 | 4240.9761 | 3659.8494 | 943.6949 | 0.00023072 | 121 | 29.6076 | 4.241 | 3.6598 | 0.94369 | 0.00023072
| 393.15 | 3000000 | 4239.272 | 3664.6912 | 944.5011 | 0.00023279 | 120 | 29.6076 | 4.2393 | 3.6647 | 0.9445 | 0.00023279
| 392.15 | 3000000 | 4237.5923 | 3669.543 | 945.303 | 0.00023488 | 119 | 29.6076 | 4.2376 | 3.6695 | 0.9453 | 0.00023488
| 391.15 | 3000000 | 4235.937 | 3674.4045 | 946.1006 | 0.00023702 | 118 | 29.6076 | 4.2359 | 3.6744 | 0.9461 | 0.00023702
| 390.15 | 3000000 | 4234.3047 | 3679.2759 | 946.8938 | 0.00023919 | 117 | 29.6076 | 4.2343 | 3.6793 | 0.94689 | 0.00023919
| 389.15 | 3000000 | 4232.6963 | 3684.1567 | 947.6827 | 0.00024139 | 116 | 29.6076 | 4.2327 | 3.6842 | 0.94768 | 0.00024139
| 388.15 | 3000000 | 4231.1113 | 3689.0471 | 948.4672 | 0.00024364 | 115 | 29.6076 | 4.2311 | 3.689 | 0.94847 | 0.00024364
| 387.15 | 3000000 | 4229.5493 | 3693.947 | 949.2474 | 0.00024592 | 114 | 29.6076 | 4.2295 | 3.6939 | 0.94925 | 0.00024592
| 386.15 | 3000000 | 4228.0103 | 3698.8562 | 950.0233 | 0.00024824 | 113 | 29.6076 | 4.228 | 3.6989 | 0.95002 | 0.00024824
| 385.15 | 3000000 | 4226.4941 | 3703.7744 | 950.7947 | 0.00025061 | 112 | 29.6076 | 4.2265 | 3.7038 | 0.95079 | 0.00025061
| 384.15 | 3000000 | 4225.0005 | 3708.7017 | 951.5618 | 0.00025301 | 111 | 29.6076 | 4.225 | 3.7087 | 0.95156 | 0.00025301
| 383.15 | 3000000 | 4223.5293 | 3713.6382 | 952.3245 | 0.00025546 | 110 | 29.6076 | 4.2235 | 3.7136 | 0.95232 | 0.00025546
| 382.15 | 3000000 | 4222.0801 | 3718.5833 | 953.0828 | 0.00025795 | 109 | 29.6076 | 4.2221 | 3.7186 | 0.95308 | 0.00025795
| 381.15 | 3000000 | 4220.6533 | 3723.5371 | 953.8366 | 0.00026049 | 108 | 29.6076 | 4.2207 | 3.7235 | 0.95384 | 0.00026049
| 380.15 | 3000000 | 4219.248 | 3728.4995 | 954.5861 | 0.00026307 | 107 | 29.6076 | 4.2192 | 3.7285 | 0.95459 | 0.00026307
| 379.15 | 3000000 | 4217.8647 | 3733.4702 | 955.3311 | 0.0002657 | 106 | 29.6076 | 4.2179 | 3.7335 | 0.95533 | 0.0002657
| 378.15 | 3000000 | 4216.5034 | 3738.4492 | 956.0717 | 0.00026837 | 105 | 29.6076 | 4.2165 | 3.7384 | 0.95607 | 0.00026837
| 377.15 | 3000000 | 4215.1631 | 3743.4365 | 956.8079 | 0.0002711 | 104 | 29.6076 | 4.2152 | 3.7434 | 0.95681 | 0.0002711
| 376.15 | 3000000 | 4213.8442 | 3748.4316 | 957.5396 | 0.00027388 | 103 | 29.6076 | 4.2138 | 3.7484 | 0.95754 | 0.00027388
| 375.15 | 3000000 | 4212.5469 | 3753.4348 | 958.2667 | 0.0002767 | 102 | 29.6076 | 4.2125 | 3.7534 | 0.95827 | 0.0002767
| 374.15 | 3000000 | 4211.2705 | 3758.4453 | 958.9894 | 0.00027958 | 101 | 29.6076 | 4.2113 | 3.7584 | 0.95899 | 0.00027958
| 373.15 | 3000000 | 4210.0156 | 3763.4636 | 959.7076 | 0.00028252 | 100 | 29.6076 | 4.21 | 3.7635 | 0.95971 | 0.00028252
| 372.15 | 3000000 | 4208.7812 | 3768.489 | 960.4213 | 0.00028551 | 99 | 29.6076 | 4.2088 | 3.7685 | 0.96042 | 0.00028551
| 371.15 | 3000000 | 4207.5679 | 3773.5215 | 961.1304 | 0.00028856 | 98 | 29.6076 | 4.2076 | 3.7735 | 0.96113 | 0.00028856
| 370.15 | 3000000 | 4206.375 | 3778.561 | 961.835 | 0.00029167 | 97 | 29.6076 | 4.2064 | 3.7786 | 0.96183 | 0.00029167
| 369.15 | 3000000 | 4205.2031 | 3783.6072 | 962.5349 | 0.00029483 | 96 | 29.6076 | 4.2052 | 3.7836 | 0.96253 | 0.00029483
| 368.15 | 3000000 | 4204.0518 | 3788.6599 | 963.2303 | 0.00029806 | 95 | 29.6076 | 4.2041 | 3.7887 | 0.96323 | 0.00029806
| 367.15 | 3000000 | 4202.9204 | 3793.7188 | 963.921 | 0.00030135 | 94 | 29.6076 | 4.2029 | 3.7937 | 0.96392 | 0.00030135
| 366.15 | 3000000 | 4201.8101 | 3798.7839 | 964.6072 | 0.00030471 | 93 | 29.6076 | 4.2018 | 3.7988 | 0.96461 | 0.00030471
| 365.15 | 3000000 | 4200.7197 | 3803.8547 | 965.2886 | 0.00030813 | 92 | 29.6076 | 4.2007 | 3.8039 | 0.96529 | 0.00030813
| 364.15 | 3000000 | 4199.6499 | 3808.9312 | 965.9654 | 0.00031162 | 91 | 29.6076 | 4.1996 | 3.8089 | 0.96597 | 0.00031162
| 363.15 | 3000000 | 4198.6001 | 3814.0127 | 966.6375 | 0.00031519 | 90 | 29.6076 | 4.1986 | 3.814 | 0.96664 | 0.00031519
| 362.15 | 3000000 | 4197.5703 | 3819.0994 | 967.3049 | 0.00031882 | 89 | 29.6076 | 4.1976 | 3.8191 | 0.9673 | 0.00031882
| 361.15 | 3000000 | 4196.561 | 3824.1909 | 967.9675 | 0.00032253 | 88 | 29.6076 | 4.1966 | 3.8242 | 0.96797 | 0.00032253
| 360.15 | 3000000 | 4195.5718 | 3829.2869 | 968.6253 | 0.00032631 | 87 | 29.6076 | 4.1956 | 3.8293 | 0.96863 | 0.00032631
| 359.15 | 3000000 | 4194.6025 | 3834.387 | 969.2784 | 0.00033017 | 86 | 29.6076 | 4.1946 | 3.8344 | 0.96928 | 0.00033017
| 358.15 | 3000000 | 4193.6528 | 3839.4907 | 969.9266 | 0.00033412 | 85 | 29.6076 | 4.1937 | 3.8395 | 0.96993 | 0.00033412
| 357.15 | 3000000 | 4192.7236 | 3844.5981 | 970.5699 | 0.00033814 | 84 | 29.6076 | 4.1927 | 3.8446 | 0.97057 | 0.00033814
| 356.15 | 3000000 | 4191.814 | 3849.7087 | 971.2084 | 0.00034225 | 83 | 29.6076 | 4.1918 | 3.8497 | 0.97121 | 0.00034225
| 355.15 | 3000000 | 4190.9243 | 3854.822 | 971.842 | 0.00034645 | 82 | 29.6076 | 4.1909 | 3.8548 | 0.97184 | 0.00034645
| 354.15 | 3000000 | 4190.0547 | 3859.9377 | 972.4707 | 0.00035074 | 81 | 29.6076 | 4.1901 | 3.8599 | 0.97247 | 0.00035074
| 353.15 | 3000000 | 4189.2046 | 3865.0554 | 973.0944 | 0.00035511 | 80 | 29.6076 | 4.1892 | 3.8651 | 0.97309 | 0.00035511
| 352.15 | 3000000 | 4188.3745 | 3870.1748 | 973.7131 | 0.00035959 | 79 | 29.6076 | 4.1884 | 3.8702 | 0.97371 | 0.00035959
| 351.15 | 3000000 | 4187.5645 | 3875.2952 | 974.3267 | 0.00036416 | 78 | 29.6076 | 4.1876 | 3.8753 | 0.97433 | 0.00036416
| 350.15 | 3000000 | 4186.7739 | 3880.4165 | 974.9354 | 0.00036883 | 77 | 29.6076 | 4.1868 | 3.8804 | 0.97494 | 0.00036883
| 349.15 | 3000000 | 4186.0029 | 3885.5378 | 975.5389 | 0.00037361 | 76 | 29.6076 | 4.186 | 3.8855 | 0.97554 | 0.00037361
| 348.15 | 3000000 | 4185.252 | 3890.6592 | 976.1373 | 0.00037849 | 75 | 29.6076 | 4.1853 | 3.8907 | 0.97614 | 0.00037849
| 347.15 | 3000000 | 4184.5205 | 3895.7798 | 976.7305 | 0.00038349 | 74 | 29.6076 | 4.1845 | 3.8958 | 0.97673 | 0.00038349
| 346.15 | 3000000 | 4183.8091 | 3900.8992 | 977.3185 | 0.00038859 | 73 | 29.6076 | 4.1838 | 3.9009 | 0.97732 | 0.00038859
| 345.15 | 3000000 | 4183.1172 | 3906.0168 | 977.9012 | 0.00039381 | 72 | 29.6076 | 4.1831 | 3.906 | 0.9779 | 0.00039381
| 344.15 | 3000000 | 4182.4453 | 3911.1321 | 978.4787 | 0.00039916 | 71 | 29.6076 | 4.1824 | 3.9111 | 0.97848 | 0.00039916
| 343.15 | 3000000 | 4181.793 | 3916.2444 | 979.0509 | 0.00040462 | 70 | 29.6076 | 4.1818 | 3.9162 | 0.97905 | 0.00040462
| 342.15 | 3000000 | 4181.1602 | 3921.3533 | 979.6177 | 0.00041022 | 69 | 29.6076 | 4.1812 | 3.9214 | 0.97962 | 0.00041022
| 341.15 | 3000000 | 4180.5474 | 3926.458 | 980.1791 | 0.00041595 | 68 | 29.6076 | 4.1805 | 3.9265 | 0.98018 | 0.00041595
| 340.15 | 3000000 | 4179.9541 | 3931.5581 | 980.735 | 0.00042181 | 67 | 29.6076 | 4.18 | 3.9316 | 0.98074 | 0.00042181
| 339.15 | 3000000 | 4179.3809 | 3936.6526 | 981.2855 | 0.00042781 | 66 | 29.6076 | 4.1794 | 3.9367 | 0.98129 | 0.00042781
| 338.15 | 3000000 | 4178.8271 | 3941.741 | 981.8305 | 0.00043396 | 65 | 29.6076 | 4.1788 | 3.9417 | 0.98183 | 0.00043396
| 337.15 | 3000000 | 4178.293 | 3946.8223 | 982.3698 | 0.00044026 | 64 | 29.6076 | 4.1783 | 3.9468 | 0.98237 | 0.00044026
| 336.15 | 3000000 | 4177.7788 | 3951.8962 | 982.9036 | 0.00044671 | 63 | 29.6076 | 4.1778 | 3.9519 | 0.9829 | 0.00044671
| 335.15 | 3000000 | 4177.2847 | 3956.9614 | 983.4316 | 0.00045332 | 62 | 29.6076 | 4.1773 | 3.957 | 0.98343 | 0.00045332
| 334.15 | 3000000 | 4176.8101 | 3962.0176 | 983.9539 | 0.0004601 | 61 | 29.6076 | 4.1768 | 3.962 | 0.98395 | 0.0004601
| 333.15 | 3000000 | 4176.3555 | 3967.0637 | 984.4704 | 0.00046705 | 60 | 29.6076 | 4.1764 | 3.9671 | 0.98447 | 0.00046705
| 332.15 | 3000000 | 4175.9204 | 3972.0989 | 984.981 | 0.00047418 | 59 | 29.6076 | 4.1759 | 3.9721 | 0.98498 | 0.00047418
| 331.15 | 3000000 | 4175.5054 | 3977.1223 | 985.4858 | 0.00048148 | 58 | 29.6076 | 4.1755 | 3.9771 | 0.98549 | 0.00048148
| 330.15 | 3000000 | 4175.1099 | 3982.1328 | 985.9846 | 0.00048898 | 57 | 29.6076 | 4.1751 | 3.9821 | 0.98598 | 0.00048898
| 329.15 | 3000000 | 4174.7344 | 3987.1299 | 986.4774 | 0.00049668 | 56 | 29.6076 | 4.1747 | 3.9871 | 0.98648 | 0.00049668
| 328.15 | 3000000 | 4174.3789 | 3992.1121 | 986.9642 | 0.00050457 | 55 | 29.6076 | 4.1744 | 3.9921 | 0.98696 | 0.00050457
| 327.15 | 3000000 | 4174.0435 | 3997.0784 | 987.4448 | 0.00051268 | 54 | 29.6076 | 4.174 | 3.9971 | 0.98744 | 0.00051268
| 326.15 | 3000000 | 4173.7275 | 4002.0281 | 987.9191 | 0.000521 | 53 | 29.6076 | 4.1737 | 4.002 | 0.98792 | 0.000521
| 325.15 | 3000000 | 4173.4321 | 4006.96 | 988.3873 | 0.00052955 | 52 | 29.6076 | 4.1734 | 4.007 | 0.98839 | 0.00052955
| 324.15 | 3000000 | 4173.1562 | 4011.873 | 988.8491 | 0.00053833 | 51 | 29.6076 | 4.1732 | 4.0119 | 0.98885 | 0.00053833
| 323.15 | 3000000 | 4172.9009 | 4016.7656 | 989.3044 | 0.00054736 | 50 | 29.6076 | 4.1729 | 4.0168 | 0.9893 | 0.00054736
| 322.15 | 3000000 | 4172.6655 | 4021.6372 | 989.7534 | 0.00055663 | 49 | 29.6076 | 4.1727 | 4.0216 | 0.98975 | 0.00055663
| 321.15 | 3000000 | 4172.4502 | 4026.4861 | 990.1957 | 0.00056617 | 48 | 29.6076 | 4.1725 | 4.0265 | 0.9902 | 0.00056617
| 320.15 | 3000000 | 4172.2554 | 4031.3113 | 990.6314 | 0.00057598 | 47 | 29.6076 | 4.1723 | 4.0313 | 0.99063 | 0.00057598
| 319.15 | 3000000 | 4172.0806 | 4036.1116 | 991.0604 | 0.00058607 | 46 | 29.6076 | 4.1721 | 4.0361 | 0.99106 | 0.00058607
| 318.15 | 3000000 | 4171.9268 | 4040.8853 | 991.4827 | 0.00059646 | 45 | 29.6076 | 4.1719 | 4.0409 | 0.99148 | 0.00059646
| 317.15 | 3000000 | 4171.7935 | 4045.6313 | 991.898 | 0.00060715 | 44 | 29.6076 | 4.1718 | 4.0456 | 0.9919 | 0.00060715
| 316.15 | 3000000 | 4171.6807 | 4050.3481 | 992.3064 | 0.00061816 | 43 | 29.6076 | 4.1717 | 4.0503 | 0.99231 | 0.00061816
| 315.15 | 3000000 | 4171.5889 | 4055.0344 | 992.7078 | 0.0006295 | 42 | 29.6076 | 4.1716 | 4.055 | 0.99271 | 0.0006295
| 314.15 | 3000000 | 4171.5186 | 4059.6887 | 993.102 | 0.00064118 | 41 | 29.6076 | 4.1715 | 4.0597 | 0.9931 | 0.00064118
| 313.15 | 3000000 | 4171.4692 | 4064.3096 | 993.489 | 0.00065322 | 40 | 29.6076 | 4.1715 | 4.0643 | 0.99349 | 0.00065322
| 312.15 | 3000000 | 4171.4419 | 4068.8953 | 993.8686 | 0.00066563 | 39 | 29.6076 | 4.1714 | 4.0689 | 0.99387 | 0.00066563
| 311.15 | 3000000 | 4171.436 | 4073.4443 | 994.2408 | 0.00067843 | 38 | 29.6076 | 4.1714 | 4.0734 | 0.99424 | 0.00067843
| 310.15 | 3000000 | 4171.4531 | 4077.9553 | 994.6055 | 0.00069164 | 37 | 29.6076 | 4.1715 | 4.078 | 0.99461 | 0.00069164
| 309.15 | 3000000 | 4171.4922 | 4082.4268 | 994.9625 | 0.00070527 | 36 | 29.6076 | 4.1715 | 4.0824 | 0.99496 | 0.00070527
| 308.15 | 3000000 | 4171.5547 | 4086.8564 | 995.3117 | 0.00071934 | 35 | 29.6076 | 4.1716 | 4.0869 | 0.99531 | 0.00071934
| 307.15 | 3000000 | 4171.6411 | 4091.2432 | 995.6531 | 0.00073388 | 34 | 29.6076 | 4.1716 | 4.0912 | 0.99565 | 0.00073388
| 306.15 | 3000000 | 4171.7515 | 4095.5852 | 995.9865 | 0.0007489 | 33 | 29.6076 | 4.1718 | 4.0956 | 0.99599 | 0.0007489
| 305.15 | 3000000 | 4171.8867 | 4099.8809 | 996.3117 | 0.00076442 | 32 | 29.6076 | 4.1719 | 4.0999 | 0.99631 | 0.00076442
| 304.15 | 3000000 | 4172.0479 | 4104.1279 | 996.6287 | 0.00078047 | 31 | 29.6076 | 4.172 | 4.1041 | 0.99663 | 0.00078047
| 303.15 | 3000000 | 4172.2354 | 4108.3257 | 996.9373 | 0.00079708 | 30 | 29.6076 | 4.1722 | 4.1083 | 0.99694 | 0.00079708
| 302.15 | 3000000 | 4172.4507 | 4112.4712 | 997.2374 | 0.00081427 | 29 | 29.6076 | 4.1725 | 4.1125 | 0.99724 | 0.00081427
| 301.15 | 3000000 | 4172.6948 | 4116.5635 | 997.5287 | 0.00083207 | 28 | 29.6076 | 4.1727 | 4.1166 | 0.99753 | 0.00083207
| 300.15 | 3000000 | 4172.9683 | 4120.6011 | 997.8113 | 0.0008505 | 27 | 29.6076 | 4.173 | 4.1206 | 0.99781 | 0.0008505
| 299.15 | 3000000 | 4173.2734 | 4124.5811 | 998.0849 | 0.00086961 | 26 | 29.6076 | 4.1733 | 4.1246 | 0.99808 | 0.00086961
| 298.15 | 3000000 | 4173.6118 | 4128.5029 | 998.3494 | 0.00088942 | 25 | 29.6076 | 4.1736 | 4.1285 | 0.99835 | 0.00088942
| 297.15 | 3000000 | 4173.9849 | 4132.3638 | 998.6045 | 0.00090997 | 24 | 29.6076 | 4.174 | 4.1324 | 0.9986 | 0.00090997
| 296.15 | 3000000 | 4174.3945 | 4136.1626 | 998.8501 | 0.0009313 | 23 | 29.6076 | 4.1744 | 4.1362 | 0.99885 | 0.0009313
| 295.15 | 3000000 | 4174.8433 | 4139.8979 | 999.0861 | 0.00095345 | 22 | 29.6076 | 4.1748 | 4.1399 | 0.99909 | 0.00095345
| 294.15 | 3000000 | 4175.3335 | 4143.5679 | 999.3121 | 0.00097647 | 21 | 29.6076 | 4.1753 | 4.1436 | 0.99931 | 0.00097647
| 293.15 | 3000000 | 4175.8687 | 4147.1704 | 999.5281 | 0.0010004 | 20 | 29.6076 | 4.1759 | 4.1472 | 0.99953 | 0.0010004
| 292.15 | 3000000 | 4176.4512 | 4150.7041 | 999.7339 | 0.0010253 | 19 | 29.6076 | 4.1765 | 4.1507 | 0.99973 | 0.0010253
| 291.15 | 3000000 | 4177.0854 | 4154.1675 | 999.9291 | 0.0010512 | 18 | 29.6076 | 4.1771 | 4.1542 | 0.99993 | 0.0010512
| 290.15 | 3000000 | 4177.7744 | 4157.5596 | 1000.1135 | 0.0010781 | 17 | 29.6076 | 4.1778 | 4.1576 | 1.0001 | 0.0010781
| 289.15 | 3000000 | 4178.5239 | 4160.8784 | 1000.287 | 0.0011062 | 16 | 29.6076 | 4.1785 | 4.1609 | 1.0003 | 0.0011062
| 288.15 | 3000000 | 4179.3374 | 4164.123 | 1000.4493 | 0.0011356 | 15 | 29.6076 | 4.1793 | 4.1641 | 1.0004 | 0.0011356
| 287.15 | 3000000 | 4180.2222 | 4167.292 | 1000.6 | 0.0011661 | 14 | 29.6076 | 4.1802 | 4.1673 | 1.0006 | 0.0011661
| 286.15 | 3000000 | 4181.1826 | 4170.3848 | 1000.739 | 0.0011981 | 13 | 29.6076 | 4.1812 | 4.1704 | 1.0007 | 0.0011981
| 285.15 | 3000000 | 4182.2271 | 4173.3994 | 1000.8659 | 0.0012314 | 12 | 29.6076 | 4.1822 | 4.1734 | 1.0009 | 0.0012314
| 284.15 | 3000000 | 4183.3628 | 4176.3359 | 1000.9804 | 0.0012663 | 11 | 29.6076 | 4.1834 | 4.1763 | 1.001 | 0.0012663
| 283.15 | 3000000 | 4184.5981 | 4179.1934 | 1001.0822 | 0.0013028 | 10 | 29.6076 | 4.1846 | 4.1792 | 1.0011 | 0.0013028
| 282.15 | 3000000 | 4185.9429 | 4181.9717 | 1001.1709 | 0.001341 | 9 | 29.6076 | 4.1859 | 4.182 | 1.0012 | 0.001341
| 281.15 | 3000000 | 4187.4077 | 4184.6699 | 1001.2462 | 0.001381 | 8 | 29.6076 | 4.1874 | 4.1847 | 1.0012 | 0.001381
| 280.15 | 3000000 | 4189.0039 | 4187.2881 | 1001.3077 | 0.001423 | 7 | 29.6076 | 4.189 | 4.1873 | 1.0013 | 0.001423
| 279.15 | 3000000 | 4190.7446 | 4189.8262 | 1001.3549 | 0.0014671 | 6 | 29.6076 | 4.1907 | 4.1898 | 1.0014 | 0.0014671
| 278.15 | 3000000 | 4192.644 | 4192.2852 | 1001.3875 | 0.0015134 | 5 | 29.6076 | 4.1926 | 4.1923 | 1.0014 | 0.0015134
| 277.15 | 3000000 | 4194.7188 | 4194.665 | 1001.405 | 0.0015621 | 4 | 29.6076 | 4.1947 | 4.1947 | 1.0014 | 0.0015621
| 276.15 | 3000000 | 4196.9863 | 4196.9663 | 1001.407 | 0.0016133 | 3 | 29.6076 | 4.197 | 4.197 | 1.0014 | 0.0016133
| 275.15 | 3000000 | 4199.4663 | 4199.1904 | 1001.3928 | 0.0016673 | 2 | 29.6076 | 4.1995 | 4.1992 | 1.0014 | 0.0016673
| 274.15 | 3000000 | 4202.1807 | 4201.3389 | 1001.3621 | 0.0017242 | 0.99999 | 29.6076 | 4.2022 | 4.2013 | 1.0014 | 0.0017242
| 273.15 | 3000000 | 4205.1533 | 4203.4131 | 1001.314 | 0.0017843 | -6.1035e-06 | 29.6076 | 4.2052 | 4.2034 | 1.0013 | 0.0017843
| 473.15 | 2500000 | 4488.4922 | 3316.2795 | 865.3877 | 0.00013456 | 200 | 24.673 | 4.4885 | 3.3163 | 0.86539 | 0.00013456
| 472.15 | 2500000 | 4483.3647 | 3320.0601 | 866.5717 | 0.00013528 | 199 | 24.673 | 4.4834 | 3.3201 | 0.86657 | 0.00013528
| 471.15 | 2500000 | 4478.3125 | 3323.8584 | 867.7499 | 0.000136 | 198 | 24.673 | 4.4783 | 3.3239 | 0.86775 | 0.000136
| 470.15 | 2500000 | 4473.334 | 3327.6741 | 868.9222 | 0.00013674 | 197 | 24.673 | 4.4733 | 3.3277 | 0.86892 | 0.00013674
| 469.15 | 2500000 | 4468.4287 | 3331.5071 | 870.0887 | 0.00013748 | 196 | 24.673 | 4.4684 | 3.3315 | 0.87009 | 0.00013748
| 468.15 | 2500000 | 4463.5942 | 3335.3572 | 871.2496 | 0.00013823 | 195 | 24.673 | 4.4636 | 3.3354 | 0.87125 | 0.00013823
| 467.15 | 2500000 | 4458.8301 | 3339.2246 | 872.4048 | 0.00013898 | 194 | 24.673 | 4.4588 | 3.3392 | 0.8724 | 0.00013898
| 466.15 | 2500000 | 4454.1353 | 3343.1089 | 873.5543 | 0.00013975 | 193 | 24.673 | 4.4541 | 3.3431 | 0.87355 | 0.00013975
| 465.15 | 2500000 | 4449.5073 | 3347.01 | 874.6982 | 0.00014052 | 192 | 24.673 | 4.4495 | 3.347 | 0.8747 | 0.00014052
| 464.15 | 2500000 | 4444.9463 | 3350.9277 | 875.8367 | 0.0001413 | 191 | 24.673 | 4.4449 | 3.3509 | 0.87584 | 0.0001413
| 463.15 | 2500000 | 4440.4507 | 3354.8623 | 876.9695 | 0.00014209 | 190 | 24.673 | 4.4405 | 3.3549 | 0.87697 | 0.00014209
| 462.15 | 2500000 | 4436.0195 | 3358.8132 | 878.097 | 0.00014289 | 189 | 24.673 | 4.436 | 3.3588 | 0.8781 | 0.00014289
| 461.15 | 2500000 | 4431.6514 | 3362.7805 | 879.219 | 0.0001437 | 188 | 24.673 | 4.4317 | 3.3628 | 0.87922 | 0.0001437
| 460.15 | 2500000 | 4427.3452 | 3366.7642 | 880.3356 | 0.00014452 | 187 | 24.673 | 4.4273 | 3.3668 | 0.88034 | 0.00014452
| 459.15 | 2500000 | 4423.1001 | 3370.7639 | 881.447 | 0.00014535 | 186 | 24.673 | 4.4231 | 3.3708 | 0.88145 | 0.00014535
| 458.15 | 2500000 | 4418.915 | 3374.7795 | 882.553 | 0.00014618 | 185 | 24.673 | 4.4189 | 3.3748 | 0.88255 | 0.00014618
| 457.15 | 2500000 | 4414.7891 | 3378.8113 | 883.6537 | 0.00014703 | 184 | 24.673 | 4.4148 | 3.3788 | 0.88365 | 0.00014703
| 456.15 | 2500000 | 4410.7212 | 3382.8586 | 884.7491 | 0.00014788 | 183 | 24.673 | 4.4107 | 3.3829 | 0.88475 | 0.00014788
| 455.15 | 2500000 | 4406.7104 | 3386.9219 | 885.8395 | 0.00014875 | 182 | 24.673 | 4.4067 | 3.3869 | 0.88584 | 0.00014875
| 454.15 | 2500000 | 4402.7559 | 3391.0005 | 886.9246 | 0.00014962 | 181 | 24.673 | 4.4028 | 3.391 | 0.88692 | 0.00014962
| 453.15 | 2500000 | 4398.8564 | 3395.0945 | 888.0046 | 0.00015051 | 180 | 24.673 | 4.3989 | 3.3951 | 0.888 | 0.00015051
| 452.15 | 2500000 | 4395.0117 | 3399.2041 | 889.0795 | 0.00015141 | 179 | 24.673 | 4.395 | 3.3992 | 0.88908 | 0.00015141
| 451.15 | 2500000 | 4391.2202 | 3403.3289 | 890.1493 | 0.00015231 | 178 | 24.673 | 4.3912 | 3.4033 | 0.89015 | 0.00015231
| 450.15 | 2500000 | 4387.4814 | 3407.4685 | 891.2141 | 0.00015323 | 177 | 24.673 | 4.3875 | 3.4075 | 0.89121 | 0.00015323
| 449.15 | 2500000 | 4383.7944 | 3411.6233 | 892.2739 | 0.00015416 | 176 | 24.673 | 4.3838 | 3.4116 | 0.89227 | 0.00015416
| 448.15 | 2500000 | 4380.1587 | 3415.7932 | 893.3287 | 0.0001551 | 175 | 24.673 | 4.3802 | 3.4158 | 0.89333 | 0.0001551
| 447.15 | 2500000 | 4376.5732 | 3419.9775 | 894.3786 | 0.00015605 | 174 | 24.673 | 4.3766 | 3.42 | 0.89438 | 0.00015605
| 446.15 | 2500000 | 4373.0366 | 3424.1768 | 895.4235 | 0.00015702 | 173 | 24.673 | 4.373 | 3.4242 | 0.89542 | 0.00015702
| 445.15 | 2500000 | 4369.5488 | 3428.3906 | 896.4636 | 0.00015799 | 172 | 24.673 | 4.3695 | 3.4284 | 0.89646 | 0.00015799
| 444.15 | 2500000 | 4366.1094 | 3432.6189 | 897.4988 | 0.00015898 | 171 | 24.673 | 4.3661 | 3.4326 | 0.8975 | 0.00015898
| 443.15 | 2500000 | 4362.7163 | 3436.8613 | 898.5291 | 0.00015998 | 170 | 24.673 | 4.3627 | 3.4369 | 0.89853 | 0.00015998
| 442.15 | 2500000 | 4359.3701 | 3441.1182 | 899.5547 | 0.00016099 | 169 | 24.673 | 4.3594 | 3.4411 | 0.89955 | 0.00016099
| 441.15 | 2500000 | 4356.0698 | 3445.3894 | 900.5754 | 0.00016202 | 168 | 24.673 | 4.3561 | 3.4454 | 0.90058 | 0.00016202
| 440.15 | 2500000 | 4352.814 | 3449.6743 | 901.5914 | 0.00016305 | 167 | 24.673 | 4.3528 | 3.4497 | 0.90159 | 0.00016305
| 439.15 | 2500000 | 4349.603 | 3453.9734 | 902.6026 | 0.00016411 | 166 | 24.673 | 4.3496 | 3.454 | 0.9026 | 0.00016411
| 438.15 | 2500000 | 4346.4355 | 3458.2864 | 903.6091 | 0.00016517 | 165 | 24.673 | 4.3464 | 3.4583 | 0.90361 | 0.00016517
| 437.15 | 2500000 | 4343.311 | 3462.613 | 904.6109 | 0.00016625 | 164 | 24.673 | 4.3433 | 3.4626 | 0.90461 | 0.00016625
| 436.15 | 2500000 | 4340.229 | 3466.9534 | 905.608 | 0.00016734 | 163 | 24.673 | 4.3402 | 3.467 | 0.90561 | 0.00016734
| 435.15 | 2500000 | 4337.1885 | 3471.3074 | 906.6005 | 0.00016845 | 162 | 24.673 | 4.3372 | 3.4713 | 0.9066 | 0.00016845
| 434.15 | 2500000 | 4334.1895 | 3475.6748 | 907.5883 | 0.00016957 | 161 | 24.673 | 4.3342 | 3.4757 | 0.90759 | 0.00016957
| 433.15 | 2500000 | 4331.2305 | 3480.0554 | 908.5715 | 0.00017071 | 160 | 24.673 | 4.3312 | 3.4801 | 0.90857 | 0.00017071
| 432.15 | 2500000 | 4328.312 | 3484.4495 | 909.55 | 0.00017186 | 159 | 24.673 | 4.3283 | 3.4844 | 0.90955 | 0.00017186
| 431.15 | 2500000 | 4325.4326 | 3488.8569 | 910.524 | 0.00017303 | 158 | 24.673 | 4.3254 | 3.4889 | 0.91052 | 0.00017303
| 430.15 | 2500000 | 4322.5918 | 3493.2771 | 911.4935 | 0.00017422 | 157 | 24.673 | 4.3226 | 3.4933 | 0.91149 | 0.00017422
| 429.15 | 2500000 | 4319.7896 | 3497.7107 | 912.4583 | 0.00017542 | 156 | 24.673 | 4.3198 | 3.4977 | 0.91246 | 0.00017542
| 428.15 | 2500000 | 4317.0249 | 3502.157 | 913.4186 | 0.00017663 | 155 | 24.673 | 4.317 | 3.5022 | 0.91342 | 0.00017663
| 427.15 | 2500000 | 4314.2974 | 3506.616 | 914.3745 | 0.00017787 | 154 | 24.673 | 4.3143 | 3.5066 | 0.91437 | 0.00017787
| 426.15 | 2500000 | 4311.6064 | 3511.0879 | 915.3258 | 0.00017912 | 153 | 24.673 | 4.3116 | 3.5111 | 0.91533 | 0.00017912
| 425.15 | 2500000 | 4308.9521 | 3515.5725 | 916.2726 | 0.00018038 | 152 | 24.673 | 4.309 | 3.5156 | 0.91627 | 0.00018038
| 424.15 | 2500000 | 4306.333 | 3520.0698 | 917.2149 | 0.00018167 | 151 | 24.673 | 4.3063 | 3.5201 | 0.91721 | 0.00018167
| 423.15 | 2500000 | 4303.749 | 3524.5793 | 918.1528 | 0.00018297 | 150 | 24.673 | 4.3037 | 3.5246 | 0.91815 | 0.00018297
| 422.15 | 2500000 | 4301.1997 | 3529.1016 | 919.0862 | 0.00018429 | 149 | 24.673 | 4.3012 | 3.5291 | 0.91909 | 0.00018429
| 421.15 | 2500000 | 4298.6846 | 3533.6357 | 920.0152 | 0.00018564 | 148 | 24.673 | 4.2987 | 3.5336 | 0.92002 | 0.00018564
| 420.15 | 2500000 | 4296.2036 | 3538.1826 | 920.9397 | 0.000187 | 147 | 24.673 | 4.2962 | 3.5382 | 0.92094 | 0.000187
| 419.15 | 2500000 | 4293.7554 | 3542.7415 | 921.8598 | 0.00018837 | 146 | 24.673 | 4.2938 | 3.5427 | 0.92186 | 0.00018837
| 418.15 | 2500000 | 4291.3403 | 3547.3123 | 922.7755 | 0.00018977 | 145 | 24.673 | 4.2913 | 3.5473 | 0.92278 | 0.00018977
| 417.15 | 2500000 | 4288.9575 | 3551.8953 | 923.6868 | 0.00019119 | 144 | 24.673 | 4.289 | 3.5519 | 0.92369 | 0.00019119
| 416.15 | 2500000 | 4286.6069 | 3556.49 | 924.5938 | 0.00019264 | 143 | 24.673 | 4.2866 | 3.5565 | 0.92459 | 0.00019264
| 415.15 | 2500000 | 4284.2876 | 3561.0967 | 925.4963 | 0.0001941 | 142 | 24.673 | 4.2843 | 3.5611 | 0.9255 | 0.0001941
| 414.15 | 2500000 | 4282 | 3565.7153 | 926.3944 | 0.00019558 | 141 | 24.673 | 4.282 | 3.5657 | 0.92639 | 0.00019558
| 413.15 | 2500000 | 4279.7427 | 3570.3455 | 927.2882 | 0.00019709 | 140 | 24.673 | 4.2797 | 3.5703 | 0.92729 | 0.00019709
| 412.15 | 2500000 | 4277.5156 | 3574.9873 | 928.1776 | 0.00019862 | 139 | 24.673 | 4.2775 | 3.575 | 0.92818 | 0.00019862
| 411.15 | 2500000 | 4275.3188 | 3579.6406 | 929.0627 | 0.00020017 | 138 | 24.673 | 4.2753 | 3.5796 | 0.92906 | 0.00020017
| 410.15 | 2500000 | 4273.1519 | 3584.3054 | 929.9434 | 0.00020174 | 137 | 24.673 | 4.2732 | 3.5843 | 0.92994 | 0.00020174
| 409.15 | 2500000 | 4271.0142 | 3588.9817 | 930.8198 | 0.00020334 | 136 | 24.673 | 4.271 | 3.589 | 0.93082 | 0.00020334
| 408.15 | 2500000 | 4268.9053 | 3593.6692 | 931.6918 | 0.00020497 | 135 | 24.673 | 4.2689 | 3.5937 | 0.93169 | 0.00020497
| 407.15 | 2500000 | 4266.8247 | 3598.3679 | 932.5595 | 0.00020662 | 134 | 24.673 | 4.2668 | 3.5984 | 0.93256 | 0.00020662
| 406.15 | 2500000 | 4264.7729 | 3603.0776 | 933.4229 | 0.00020829 | 133 | 24.673 | 4.2648 | 3.6031 | 0.93342 | 0.00020829
| 405.15 | 2500000 | 4262.7485 | 3607.7988 | 934.2819 | 0.00020999 | 132 | 24.673 | 4.2627 | 3.6078 | 0.93428 | 0.00020999
| 404.15 | 2500000 | 4260.7524 | 3612.5308 | 935.1366 | 0.00021172 | 131 | 24.673 | 4.2608 | 3.6125 | 0.93514 | 0.00021172
| 403.15 | 2500000 | 4258.7832 | 3617.2737 | 935.9869 | 0.00021347 | 130 | 24.673 | 4.2588 | 3.6173 | 0.93599 | 0.00021347
| 402.15 | 2500000 | 4256.8408 | 3622.0273 | 936.833 | 0.00021525 | 129 | 24.673 | 4.2568 | 3.622 | 0.93683 | 0.00021525
| 401.15 | 2500000 | 4254.9253 | 3626.7917 | 937.6747 | 0.00021707 | 128 | 24.673 | 4.2549 | 3.6268 | 0.93767 | 0.00021707
| 400.15 | 2500000 | 4253.0361 | 3631.5669 | 938.5122 | 0.00021891 | 127 | 24.673 | 4.253 | 3.6316 | 0.93851 | 0.00021891
| 399.15 | 2500000 | 4251.1733 | 3636.3528 | 939.3453 | 0.00022078 | 126 | 24.673 | 4.2512 | 3.6364 | 0.93935 | 0.00022078
| 398.15 | 2500000 | 4249.3359 | 3641.1492 | 940.174 | 0.00022268 | 125 | 24.673 | 4.2493 | 3.6411 | 0.94017 | 0.00022268
| 397.15 | 2500000 | 4247.5244 | 3645.9558 | 940.9985 | 0.00022461 | 124 | 24.673 | 4.2475 | 3.646 | 0.941 | 0.00022461
| 396.15 | 2500000 | 4245.7383 | 3650.7729 | 941.8186 | 0.00022657 | 123 | 24.673 | 4.2457 | 3.6508 | 0.94182 | 0.00022657
| 395.15 | 2500000 | 4243.9771 | 3655.6003 | 942.6344 | 0.00022856 | 122 | 24.673 | 4.244 | 3.6556 | 0.94263 | 0.00022856
| 394.15 | 2500000 | 4242.2407 | 3660.4377 | 943.4459 | 0.00023059 | 121 | 24.673 | 4.2422 | 3.6604 | 0.94345 | 0.00023059
| 393.15 | 2500000 | 4240.5288 | 3665.2854 | 944.253 | 0.00023266 | 120 | 24.673 | 4.2405 | 3.6653 | 0.94425 | 0.00023266
| 392.15 | 2500000 | 4238.8418 | 3670.1431 | 945.0558 | 0.00023475 | 119 | 24.673 | 4.2388 | 3.6701 | 0.94506 | 0.00023475
| 391.15 | 2500000 | 4237.1782 | 3675.0105 | 945.8542 | 0.00023689 | 118 | 24.673 | 4.2372 | 3.675 | 0.94585 | 0.00023689
| 390.15 | 2500000 | 4235.5391 | 3679.8879 | 946.6483 | 0.00023905 | 117 | 24.673 | 4.2355 | 3.6799 | 0.94665 | 0.00023905
| 389.15 | 2500000 | 4233.9233 | 3684.7749 | 947.438 | 0.00024126 | 116 | 24.673 | 4.2339 | 3.6848 | 0.94744 | 0.00024126
| 388.15 | 2500000 | 4232.3311 | 3689.6716 | 948.2234 | 0.0002435 | 115 | 24.673 | 4.2323 | 3.6897 | 0.94822 | 0.0002435
| 387.15 | 2500000 | 4230.7622 | 3694.5776 | 949.0045 | 0.00024579 | 114 | 24.673 | 4.2308 | 3.6946 | 0.949 | 0.00024579
| 386.15 | 2500000 | 4229.2168 | 3699.4932 | 949.7811 | 0.00024811 | 113 | 24.673 | 4.2292 | 3.6995 | 0.94978 | 0.00024811
| 385.15 | 2500000 | 4227.6938 | 3704.418 | 950.5533 | 0.00025047 | 112 | 24.673 | 4.2277 | 3.7044 | 0.95055 | 0.00025047
| 384.15 | 2500000 | 4226.1938 | 3709.3518 | 951.3212 | 0.00025288 | 111 | 24.673 | 4.2262 | 3.7094 | 0.95132 | 0.00025288
| 383.15 | 2500000 | 4224.7163 | 3714.2949 | 952.0847 | 0.00025533 | 110 | 24.673 | 4.2247 | 3.7143 | 0.95208 | 0.00025533
| 382.15 | 2500000 | 4223.2612 | 3719.2468 | 952.8438 | 0.00025782 | 109 | 24.673 | 4.2233 | 3.7192 | 0.95284 | 0.00025782
| 381.15 | 2500000 | 4221.8286 | 3724.2075 | 953.5984 | 0.00026035 | 108 | 24.673 | 4.2218 | 3.7242 | 0.9536 | 0.00026035
| 380.15 | 2500000 | 4220.418 | 3729.1768 | 954.3486 | 0.00026293 | 107 | 24.673 | 4.2204 | 3.7292 | 0.95435 | 0.00026293
| 379.15 | 2500000 | 4219.0293 | 3734.1545 | 955.0944 | 0.00026556 | 106 | 24.673 | 4.219 | 3.7342 | 0.95509 | 0.00026556
| 378.15 | 2500000 | 4217.6621 | 3739.1409 | 955.8356 | 0.00026824 | 105 | 24.673 | 4.2177 | 3.7391 | 0.95584 | 0.00026824
| 377.15 | 2500000 | 4216.3169 | 3744.1353 | 956.5725 | 0.00027097 | 104 | 24.673 | 4.2163 | 3.7441 | 0.95657 | 0.00027097
| 376.15 | 2500000 | 4214.9937 | 3749.1379 | 957.3049 | 0.00027374 | 103 | 24.673 | 4.215 | 3.7491 | 0.9573 | 0.00027374
| 375.15 | 2500000 | 4213.6914 | 3754.1484 | 958.0328 | 0.00027657 | 102 | 24.673 | 4.2137 | 3.7541 | 0.95803 | 0.00027657
| 374.15 | 2500000 | 4212.4102 | 3759.1667 | 958.7561 | 0.00027945 | 101 | 24.673 | 4.2124 | 3.7592 | 0.95876 | 0.00027945
| 373.15 | 2500000 | 4211.1509 | 3764.1924 | 959.475 | 0.00028239 | 100 | 24.673 | 4.2112 | 3.7642 | 0.95947 | 0.00028239
| 372.15 | 2500000 | 4209.9121 | 3769.2256 | 960.1893 | 0.00028538 | 99 | 24.673 | 4.2099 | 3.7692 | 0.96019 | 0.00028538
| 371.15 | 2500000 | 4208.6948 | 3774.2661 | 960.899 | 0.00028843 | 98 | 24.673 | 4.2087 | 3.7743 | 0.9609 | 0.00028843
| 370.15 | 2500000 | 4207.498 | 3779.3135 | 961.6042 | 0.00029153 | 97 | 24.673 | 4.2075 | 3.7793 | 0.9616 | 0.00029153
| 369.15 | 2500000 | 4206.3223 | 3784.3679 | 962.3047 | 0.0002947 | 96 | 24.673 | 4.2063 | 3.7844 | 0.9623 | 0.0002947
| 368.15 | 2500000 | 4205.167 | 3789.4287 | 963.0007 | 0.00029793 | 95 | 24.673 | 4.2052 | 3.7894 | 0.963 | 0.00029793
| 367.15 | 2500000 | 4204.0327 | 3794.4961 | 963.6921 | 0.00030122 | 94 | 24.673 | 4.204 | 3.7945 | 0.96369 | 0.00030122
| 366.15 | 2500000 | 4202.9189 | 3799.5693 | 964.3787 | 0.00030458 | 93 | 24.673 | 4.2029 | 3.7996 | 0.96438 | 0.00030458
| 365.15 | 2500000 | 4201.8252 | 3804.6487 | 965.0608 | 0.000308 | 92 | 24.673 | 4.2018 | 3.8046 | 0.96506 | 0.000308
| 364.15 | 2500000 | 4200.7524 | 3809.7339 | 965.7381 | 0.00031149 | 91 | 24.673 | 4.2008 | 3.8097 | 0.96574 | 0.00031149
| 363.15 | 2500000 | 4199.7002 | 3814.8242 | 966.4107 | 0.00031505 | 90 | 24.673 | 4.1997 | 3.8148 | 0.96641 | 0.00031505
| 362.15 | 2500000 | 4198.668 | 3819.9197 | 967.0786 | 0.00031869 | 89 | 24.673 | 4.1987 | 3.8199 | 0.96708 | 0.00031869
| 361.15 | 2500000 | 4197.6558 | 3825.0203 | 967.7417 | 0.00032239 | 88 | 24.673 | 4.1977 | 3.825 | 0.96774 | 0.00032239
| 360.15 | 2500000 | 4196.6641 | 3830.1252 | 968.4001 | 0.00032618 | 87 | 24.673 | 4.1967 | 3.8301 | 0.9684 | 0.00032618
| 359.15 | 2500000 | 4195.6929 | 3835.2344 | 969.0536 | 0.00033004 | 86 | 24.673 | 4.1957 | 3.8352 | 0.96905 | 0.00033004
| 358.15 | 2500000 | 4194.7412 | 3840.3477 | 969.7023 | 0.00033398 | 85 | 24.673 | 4.1947 | 3.8403 | 0.9697 | 0.00033398
| 357.15 | 2500000 | 4193.8101 | 3845.4644 | 970.3461 | 0.00033801 | 84 | 24.673 | 4.1938 | 3.8455 | 0.97035 | 0.00033801
| 356.15 | 2500000 | 4192.8989 | 3850.5845 | 970.985 | 0.00034212 | 83 | 24.673 | 4.1929 | 3.8506 | 0.97099 | 0.00034212
| 355.15 | 2500000 | 4192.0078 | 3855.7073 | 971.6191 | 0.00034632 | 82 | 24.673 | 4.192 | 3.8557 | 0.97162 | 0.00034632
| 354.15 | 2500000 | 4191.1367 | 3860.8328 | 972.2482 | 0.0003506 | 81 | 24.673 | 4.1911 | 3.8608 | 0.97225 | 0.0003506
| 353.15 | 2500000 | 4190.2856 | 3865.9604 | 972.8723 | 0.00035498 | 80 | 24.673 | 4.1903 | 3.866 | 0.97287 | 0.00035498
| 352.15 | 2500000 | 4189.4546 | 3871.0898 | 973.4913 | 0.00035946 | 79 | 24.673 | 4.1895 | 3.8711 | 0.97349 | 0.00035946
| 351.15 | 2500000 | 4188.6436 | 3876.2205 | 974.1054 | 0.00036403 | 78 | 24.673 | 4.1886 | 3.8762 | 0.97411 | 0.00036403
| 350.15 | 2500000 | 4187.8525 | 3881.3518 | 974.7144 | 0.0003687 | 77 | 24.673 | 4.1879 | 3.8814 | 0.97471 | 0.0003687
| 349.15 | 2500000 | 4187.0811 | 3886.4836 | 975.3182 | 0.00037348 | 76 | 24.673 | 4.1871 | 3.8865 | 0.97532 | 0.00037348
| 348.15 | 2500000 | 4186.3301 | 3891.6155 | 975.917 | 0.00037836 | 75 | 24.673 | 4.1863 | 3.8916 | 0.97592 | 0.00037836
| 347.15 | 2500000 | 4185.5986 | 3896.7466 | 976.5105 | 0.00038336 | 74 | 24.673 | 4.1856 | 3.8967 | 0.97651 | 0.00038336
| 346.15 | 2500000 | 4184.8872 | 3901.8767 | 977.0989 | 0.00038846 | 73 | 24.673 | 4.1849 | 3.9019 | 0.9771 | 0.00038846
| 345.15 | 2500000 | 4184.1958 | 3907.0051 | 977.6819 | 0.00039369 | 72 | 24.673 | 4.1842 | 3.907 | 0.97768 | 0.00039369
| 344.15 | 2500000 | 4183.5239 | 3912.1313 | 978.2597 | 0.00039903 | 71 | 24.673 | 4.1835 | 3.9121 | 0.97826 | 0.00039903
| 343.15 | 2500000 | 4182.8726 | 3917.2549 | 978.8322 | 0.0004045 | 70 | 24.673 | 4.1829 | 3.9173 | 0.97883 | 0.0004045
| 342.15 | 2500000 | 4182.2407 | 3922.375 | 979.3992 | 0.00041009 | 69 | 24.673 | 4.1822 | 3.9224 | 0.9794 | 0.00041009
| 341.15 | 2500000 | 4181.6289 | 3927.491 | 979.9609 | 0.00041582 | 68 | 24.673 | 4.1816 | 3.9275 | 0.97996 | 0.00041582
| 340.15 | 2500000 | 4181.0371 | 3932.6025 | 980.5171 | 0.00042169 | 67 | 24.673 | 4.181 | 3.9326 | 0.98052 | 0.00042169
| 339.15 | 2500000 | 4180.4648 | 3937.7085 | 981.0677 | 0.00042769 | 66 | 24.673 | 4.1805 | 3.9377 | 0.98107 | 0.00042769
| 338.15 | 2500000 | 4179.9131 | 3942.8086 | 981.6129 | 0.00043384 | 65 | 24.673 | 4.1799 | 3.9428 | 0.98161 | 0.00043384
| 337.15 | 2500000 | 4179.3809 | 3947.9019 | 982.1525 | 0.00044014 | 64 | 24.673 | 4.1794 | 3.9479 | 0.98215 | 0.00044014
| 336.15 | 2500000 | 4178.8691 | 3952.9875 | 982.6863 | 0.00044659 | 63 | 24.673 | 4.1789 | 3.953 | 0.98269 | 0.00044659
| 335.15 | 2500000 | 4178.377 | 3958.0652 | 983.2145 | 0.00045321 | 62 | 24.673 | 4.1784 | 3.9581 | 0.98321 | 0.00045321
| 334.15 | 2500000 | 4177.9048 | 3963.1335 | 983.737 | 0.00045999 | 61 | 24.673 | 4.1779 | 3.9631 | 0.98374 | 0.00045999
| 333.15 | 2500000 | 4177.4531 | 3968.1919 | 984.2537 | 0.00046694 | 60 | 24.673 | 4.1775 | 3.9682 | 0.98425 | 0.00046694
| 332.15 | 2500000 | 4177.021 | 3973.2395 | 984.7644 | 0.00047407 | 59 | 24.673 | 4.177 | 3.9732 | 0.98476 | 0.00047407
| 331.15 | 2500000 | 4176.6089 | 3978.2756 | 985.2693 | 0.00048138 | 58 | 24.673 | 4.1766 | 3.9783 | 0.98527 | 0.00048138
| 330.15 | 2500000 | 4176.2173 | 3983.2988 | 985.7682 | 0.00048888 | 57 | 24.673 | 4.1762 | 3.9833 | 0.98577 | 0.00048888
| 329.15 | 2500000 | 4175.8457 | 3988.3086 | 986.261 | 0.00049657 | 56 | 24.673 | 4.1758 | 3.9883 | 0.98626 | 0.00049657
| 328.15 | 2500000 | 4175.4941 | 3993.304 | 986.7479 | 0.00050447 | 55 | 24.673 | 4.1755 | 3.9933 | 0.98675 | 0.00050447
| 327.15 | 2500000 | 4175.1626 | 3998.2834 | 987.2285 | 0.00051258 | 54 | 24.673 | 4.1752 | 3.9983 | 0.98723 | 0.00051258
| 326.15 | 2500000 | 4174.8516 | 4003.2466 | 987.7029 | 0.0005209 | 53 | 24.673 | 4.1749 | 4.0032 | 0.9877 | 0.0005209
| 325.15 | 2500000 | 4174.5605 | 4008.1919 | 988.171 | 0.00052945 | 52 | 24.673 | 4.1746 | 4.0082 | 0.98817 | 0.00052945
| 324.15 | 2500000 | 4174.29 | 4013.1184 | 988.6328 | 0.00053824 | 51 | 24.673 | 4.1743 | 4.0131 | 0.98863 | 0.00053824
| 323.15 | 2500000 | 4174.04 | 4018.0249 | 989.0881 | 0.00054727 | 50 | 24.673 | 4.174 | 4.018 | 0.98909 | 0.00054727
| 322.15 | 2500000 | 4173.8101 | 4022.9102 | 989.537 | 0.00055655 | 49 | 24.673 | 4.1738 | 4.0229 | 0.98954 | 0.00055655
| 321.15 | 2500000 | 4173.6011 | 4027.7732 | 989.9793 | 0.00056609 | 48 | 24.673 | 4.1736 | 4.0278 | 0.98998 | 0.00056609
| 320.15 | 2500000 | 4173.4126 | 4032.6125 | 990.4149 | 0.00057591 | 47 | 24.673 | 4.1734 | 4.0326 | 0.99041 | 0.00057591
| 319.15 | 2500000 | 4173.2446 | 4037.427 | 990.8439 | 0.000586 | 46 | 24.673 | 4.1732 | 4.0374 | 0.99084 | 0.000586
| 318.15 | 2500000 | 4173.0977 | 4042.2151 | 991.2659 | 0.00059639 | 45 | 24.673 | 4.1731 | 4.0422 | 0.99127 | 0.00059639
| 317.15 | 2500000 | 4172.9717 | 4046.9758 | 991.6812 | 0.00060709 | 44 | 24.673 | 4.173 | 4.047 | 0.99168 | 0.00060709
| 316.15 | 2500000 | 4172.8672 | 4051.7075 | 992.0894 | 0.0006181 | 43 | 24.673 | 4.1729 | 4.0517 | 0.99209 | 0.0006181
| 315.15 | 2500000 | 4172.7837 | 4056.4087 | 992.4905 | 0.00062944 | 42 | 24.673 | 4.1728 | 4.0564 | 0.99249 | 0.00062944
| 314.15 | 2500000 | 4172.7217 | 4061.0781 | 992.8846 | 0.00064113 | 41 | 24.673 | 4.1727 | 4.0611 | 0.99288 | 0.00064113
| 313.15 | 2500000 | 4172.6816 | 4065.7141 | 993.2713 | 0.00065317 | 40 | 24.673 | 4.1727 | 4.0657 | 0.99327 | 0.00065317
| 312.15 | 2500000 | 4172.6636 | 4070.3154 | 993.6507 | 0.00066559 | 39 | 24.673 | 4.1727 | 4.0703 | 0.99365 | 0.00066559
| 311.15 | 2500000 | 4172.668 | 4074.8801 | 994.0226 | 0.0006784 | 38 | 24.673 | 4.1727 | 4.0749 | 0.99402 | 0.0006784
| 310.15 | 2500000 | 4172.6953 | 4079.407 | 994.387 | 0.00069161 | 37 | 24.673 | 4.1727 | 4.0794 | 0.99439 | 0.00069161
| 309.15 | 2500000 | 4172.7456 | 4083.8943 | 994.7437 | 0.00070525 | 36 | 24.673 | 4.1727 | 4.0839 | 0.99474 | 0.00070525
| 308.15 | 2500000 | 4172.8198 | 4088.3403 | 995.0926 | 0.00071933 | 35 | 24.673 | 4.1728 | 4.0883 | 0.99509 | 0.00071933
| 307.15 | 2500000 | 4172.918 | 4092.7437 | 995.4336 | 0.00073388 | 34 | 24.673 | 4.1729 | 4.0927 | 0.99543 | 0.00073388
| 306.15 | 2500000 | 4173.041 | 4097.1021 | 995.7666 | 0.00074891 | 33 | 24.673 | 4.173 | 4.0971 | 0.99577 | 0.00074891
| 305.15 | 2500000 | 4173.1895 | 4101.4146 | 996.0914 | 0.00076444 | 32 | 24.673 | 4.1732 | 4.1014 | 0.99609 | 0.00076444
| 304.15 | 2500000 | 4173.3647 | 4105.6792 | 996.408 | 0.00078051 | 31 | 24.673 | 4.1734 | 4.1057 | 0.99641 | 0.00078051
| 303.15 | 2500000 | 4173.5669 | 4109.894 | 996.7161 | 0.00079713 | 30 | 24.673 | 4.1736 | 4.1099 | 0.99672 | 0.00079713
| 302.15 | 2500000 | 4173.7974 | 4114.0571 | 997.0157 | 0.00081433 | 29 | 24.673 | 4.1738 | 4.1141 | 0.99702 | 0.00081433
| 301.15 | 2500000 | 4174.0576 | 4118.1675 | 997.3066 | 0.00083214 | 28 | 24.673 | 4.1741 | 4.1182 | 0.99731 | 0.00083214
| 300.15 | 2500000 | 4174.3481 | 4122.2227 | 997.5886 | 0.00085059 | 27 | 24.673 | 4.1743 | 4.1222 | 0.99759 | 0.00085059
| 299.15 | 2500000 | 4174.6714 | 4126.2217 | 997.8616 | 0.00086971 | 26 | 24.673 | 4.1747 | 4.1262 | 0.99786 | 0.00086971
| 298.15 | 2500000 | 4175.0278 | 4130.1616 | 998.1254 | 0.00088953 | 25 | 24.673 | 4.175 | 4.1302 | 0.99813 | 0.00088953
| 297.15 | 2500000 | 4175.4204 | 4134.042 | 998.3799 | 0.0009101 | 24 | 24.673 | 4.1754 | 4.134 | 0.99838 | 0.0009101
| 296.15 | 2500000 | 4175.8511 | 4137.8604 | 998.6249 | 0.00093145 | 23 | 24.673 | 4.1759 | 4.1379 | 0.99862 | 0.00093145
| 295.15 | 2500000 | 4176.3213 | 4141.6152 | 998.8601 | 0.00095362 | 22 | 24.673 | 4.1763 | 4.1416 | 0.99886 | 0.00095362
| 294.15 | 2500000 | 4176.8345 | 4145.3052 | 999.0854 | 0.00097665 | 21 | 24.673 | 4.1768 | 4.1453 | 0.99909 | 0.00097665
| 293.15 | 2500000 | 4177.3936 | 4148.9282 | 999.3007 | 0.0010006 | 20 | 24.673 | 4.1774 | 4.1489 | 0.9993 | 0.0010006
| 292.15 | 2500000 | 4178.0015 | 4152.4829 | 999.5056 | 0.0010255 | 19 | 24.673 | 4.178 | 4.1525 | 0.99951 | 0.0010255
| 291.15 | 2500000 | 4178.6626 | 4155.9683 | 999.6999 | 0.0010514 | 18 | 24.673 | 4.1787 | 4.156 | 0.9997 | 0.0010514
| 290.15 | 2500000 | 4179.3799 | 4159.3823 | 999.8835 | 0.0010784 | 17 | 24.673 | 4.1794 | 4.1594 | 0.99988 | 0.0010784
| 289.15 | 2500000 | 4180.1587 | 4162.7236 | 1000.056 | 0.0011066 | 16 | 24.673 | 4.1802 | 4.1627 | 1.0001 | 0.0011066
| 288.15 | 2500000 | 4181.0039 | 4165.9912 | 1000.2173 | 0.0011359 | 15 | 24.673 | 4.181 | 4.166 | 1.0002 | 0.0011359
| 287.15 | 2500000 | 4181.9214 | 4169.1841 | 1000.3671 | 0.0011665 | 14 | 24.673 | 4.1819 | 4.1692 | 1.0004 | 0.0011665
| 286.15 | 2500000 | 4182.917 | 4172.3008 | 1000.5049 | 0.0011985 | 13 | 24.673 | 4.1829 | 4.1723 | 1.0005 | 0.0011985
| 285.15 | 2500000 | 4183.9985 | 4175.3408 | 1000.6307 | 0.0012318 | 12 | 24.673 | 4.184 | 4.1753 | 1.0006 | 0.0012318
| 284.15 | 2500000 | 4185.1733 | 4178.3032 | 1000.7441 | 0.0012668 | 11 | 24.673 | 4.1852 | 4.1783 | 1.0007 | 0.0012668
| 283.15 | 2500000 | 4186.4497 | 4181.1875 | 1000.8446 | 0.0013033 | 10 | 24.673 | 4.1864 | 4.1812 | 1.0008 | 0.0013033
| 282.15 | 2500000 | 4187.8384 | 4183.9927 | 1000.9321 | 0.0013415 | 9 | 24.673 | 4.1878 | 4.184 | 1.0009 | 0.0013415
| 281.15 | 2500000 | 4189.3496 | 4186.7192 | 1001.006 | 0.0013816 | 8 | 24.673 | 4.1893 | 4.1867 | 1.001 | 0.0013816
| 280.15 | 2500000 | 4190.9946 | 4189.3672 | 1001.0662 | 0.0014237 | 7 | 24.673 | 4.191 | 4.1894 | 1.0011 | 0.0014237
| 279.15 | 2500000 | 4192.7876 | 4191.936 | 1001.112 | 0.0014678 | 6 | 24.673 | 4.1928 | 4.1919 | 1.0011 | 0.0014678
| 278.15 | 2500000 | 4194.7432 | 4194.4263 | 1001.1431 | 0.0015142 | 5 | 24.673 | 4.1947 | 4.1944 | 1.0011 | 0.0015142
| 277.15 | 2500000 | 4196.877 | 4196.8389 | 1001.1591 | 0.0015629 | 4 | 24.673 | 4.1969 | 4.1968 | 1.0012 | 0.0015629
| 276.15 | 2500000 | 4199.207 | 4199.1743 | 1001.1594 | 0.0016143 | 3 | 24.673 | 4.1992 | 4.1992 | 1.0012 | 0.0016143
| 275.15 | 2500000 | 4201.7539 | 4201.4346 | 1001.1436 | 0.0016683 | 2 | 24.673 | 4.2018 | 4.2014 | 1.0011 | 0.0016683
| 274.15 | 2500000 | 4204.5391 | 4203.6201 | 1001.1111 | 0.0017254 | 0.99999 | 24.673 | 4.2045 | 4.2036 | 1.0011 | 0.0017254
| 273.15 | 2500000 | 4207.5874 | 4205.7329 | 1001.0612 | 0.0017856 | -6.1035e-06 | 24.673 | 4.2076 | 4.2057 | 1.0011 | 0.0017856
| 473.15 | 2400000 | 4489.0723 | 3316.3555 | 865.3117 | 0.00013453 | 200 | 23.6861 | 4.4891 | 3.3164 | 0.86531 | 0.00013453
| 472.15 | 2400000 | 4483.9365 | 3320.1362 | 866.4963 | 0.00013525 | 199 | 23.6861 | 4.4839 | 3.3201 | 0.8665 | 0.00013525
| 471.15 | 2400000 | 4478.876 | 3323.9346 | 867.675 | 0.00013598 | 198 | 23.6861 | 4.4789 | 3.3239 | 0.86767 | 0.00013598
| 470.15 | 2400000 | 4473.8901 | 3327.7502 | 868.8478 | 0.00013671 | 197 | 23.6861 | 4.4739 | 3.3278 | 0.86885 | 0.00013671
| 469.15 | 2400000 | 4468.9766 | 3331.5833 | 870.015 | 0.00013745 | 196 | 23.6861 | 4.469 | 3.3316 | 0.87001 | 0.00013745
| 468.15 | 2400000 | 4464.1348 | 3335.4336 | 871.1763 | 0.0001382 | 195 | 23.6861 | 4.4641 | 3.3354 | 0.87118 | 0.0001382
| 467.15 | 2400000 | 4459.3633 | 3339.301 | 872.332 | 0.00013896 | 194 | 23.6861 | 4.4594 | 3.3393 | 0.87233 | 0.00013896
| 466.15 | 2400000 | 4454.6606 | 3343.1853 | 873.482 | 0.00013972 | 193 | 23.6861 | 4.4547 | 3.3432 | 0.87348 | 0.00013972
| 465.15 | 2400000 | 4450.0259 | 3347.0864 | 874.6264 | 0.0001405 | 192 | 23.6861 | 4.45 | 3.3471 | 0.87463 | 0.0001405
| 464.15 | 2400000 | 4445.458 | 3351.0044 | 875.7653 | 0.00014128 | 191 | 23.6861 | 4.4455 | 3.351 | 0.87577 | 0.00014128
| 463.15 | 2400000 | 4440.9556 | 3354.939 | 876.8987 | 0.00014207 | 190 | 23.6861 | 4.441 | 3.3549 | 0.8769 | 0.00014207
| 462.15 | 2400000 | 4436.5176 | 3358.8901 | 878.0266 | 0.00014287 | 189 | 23.6861 | 4.4365 | 3.3589 | 0.87803 | 0.00014287
| 461.15 | 2400000 | 4432.1426 | 3362.8574 | 879.149 | 0.00014368 | 188 | 23.6861 | 4.4321 | 3.3629 | 0.87915 | 0.00014368
| 460.15 | 2400000 | 4427.8301 | 3366.8413 | 880.2662 | 0.0001445 | 187 | 23.6861 | 4.4278 | 3.3668 | 0.88027 | 0.0001445
| 459.15 | 2400000 | 4423.5786 | 3370.8411 | 881.3779 | 0.00014532 | 186 | 23.6861 | 4.4236 | 3.3708 | 0.88138 | 0.00014532
| 458.15 | 2400000 | 4419.3877 | 3374.8569 | 882.4844 | 0.00014616 | 185 | 23.6861 | 4.4194 | 3.3749 | 0.88248 | 0.00014616
| 457.15 | 2400000 | 4415.2554 | 3378.8889 | 883.5855 | 0.000147 | 184 | 23.6861 | 4.4153 | 3.3789 | 0.88359 | 0.000147
| 456.15 | 2400000 | 4411.1816 | 3382.9365 | 884.6815 | 0.00014786 | 183 | 23.6861 | 4.4112 | 3.3829 | 0.88468 | 0.00014786
| 455.15 | 2400000 | 4407.165 | 3386.9998 | 885.7722 | 0.00014872 | 182 | 23.6861 | 4.4072 | 3.387 | 0.88577 | 0.00014872
| 454.15 | 2400000 | 4403.2051 | 3391.0786 | 886.8577 | 0.0001496 | 181 | 23.6861 | 4.4032 | 3.3911 | 0.88686 | 0.0001496
| 453.15 | 2400000 | 4399.3003 | 3395.1731 | 887.9381 | 0.00015049 | 180 | 23.6861 | 4.3993 | 3.3952 | 0.88794 | 0.00015049
| 452.15 | 2400000 | 4395.4497 | 3399.2827 | 889.0134 | 0.00015138 | 179 | 23.6861 | 4.3954 | 3.3993 | 0.88901 | 0.00015138
| 451.15 | 2400000 | 4391.6528 | 3403.4077 | 890.0836 | 0.00015229 | 178 | 23.6861 | 4.3917 | 3.4034 | 0.89008 | 0.00015229
| 450.15 | 2400000 | 4387.9092 | 3407.5479 | 891.1489 | 0.00015321 | 177 | 23.6861 | 4.3879 | 3.4075 | 0.89115 | 0.00015321
| 449.15 | 2400000 | 4384.2168 | 3411.7029 | 892.209 | 0.00015414 | 176 | 23.6861 | 4.3842 | 3.4117 | 0.89221 | 0.00015414
| 448.15 | 2400000 | 4380.5762 | 3415.8728 | 893.2642 | 0.00015508 | 175 | 23.6861 | 4.3806 | 3.4159 | 0.89326 | 0.00015508
| 447.15 | 2400000 | 4376.9854 | 3420.0576 | 894.3145 | 0.00015603 | 174 | 23.6861 | 4.377 | 3.4201 | 0.89431 | 0.00015603
| 446.15 | 2400000 | 4373.4443 | 3424.2573 | 895.3598 | 0.00015699 | 173 | 23.6861 | 4.3734 | 3.4243 | 0.89536 | 0.00015699
| 445.15 | 2400000 | 4369.9517 | 3428.4714 | 896.4002 | 0.00015797 | 172 | 23.6861 | 4.37 | 3.4285 | 0.8964 | 0.00015797
| 444.15 | 2400000 | 4366.5073 | 3432.7 | 897.4358 | 0.00015895 | 171 | 23.6861 | 4.3665 | 3.4327 | 0.89744 | 0.00015895
| 443.15 | 2400000 | 4363.1104 | 3436.9429 | 898.4665 | 0.00015995 | 170 | 23.6861 | 4.3631 | 3.4369 | 0.89847 | 0.00015995
| 442.15 | 2400000 | 4359.7593 | 3441.2002 | 899.4924 | 0.00016097 | 169 | 23.6861 | 4.3598 | 3.4412 | 0.89949 | 0.00016097
| 441.15 | 2400000 | 4356.4546 | 3445.4717 | 900.5134 | 0.00016199 | 168 | 23.6861 | 4.3565 | 3.4455 | 0.90051 | 0.00016199
| 440.15 | 2400000 | 4353.1948 | 3449.7571 | 901.5297 | 0.00016303 | 167 | 23.6861 | 4.3532 | 3.4498 | 0.90153 | 0.00016303
| 439.15 | 2400000 | 4349.9795 | 3454.0566 | 902.5413 | 0.00016408 | 166 | 23.6861 | 4.35 | 3.4541 | 0.90254 | 0.00016408
| 438.15 | 2400000 | 4346.8076 | 3458.3699 | 903.5482 | 0.00016515 | 165 | 23.6861 | 4.3468 | 3.4584 | 0.90355 | 0.00016515
| 437.15 | 2400000 | 4343.6792 | 3462.697 | 904.5503 | 0.00016623 | 164 | 23.6861 | 4.3437 | 3.4627 | 0.90455 | 0.00016623
| 436.15 | 2400000 | 4340.5933 | 3467.0378 | 905.5477 | 0.00016732 | 163 | 23.6861 | 4.3406 | 3.467 | 0.90555 | 0.00016732
| 435.15 | 2400000 | 4337.5488 | 3471.3923 | 906.5405 | 0.00016843 | 162 | 23.6861 | 4.3375 | 3.4714 | 0.90654 | 0.00016843
| 434.15 | 2400000 | 4334.5459 | 3475.76 | 907.5286 | 0.00016955 | 161 | 23.6861 | 4.3345 | 3.4758 | 0.90753 | 0.00016955
| 433.15 | 2400000 | 4331.5835 | 3480.1414 | 908.5121 | 0.00017069 | 160 | 23.6861 | 4.3316 | 3.4801 | 0.90851 | 0.00017069
| 432.15 | 2400000 | 4328.6611 | 3484.5359 | 909.491 | 0.00017184 | 159 | 23.6861 | 4.3287 | 3.4845 | 0.90949 | 0.00017184
| 431.15 | 2400000 | 4325.7783 | 3488.9438 | 910.4653 | 0.00017301 | 158 | 23.6861 | 4.3258 | 3.4889 | 0.91047 | 0.00017301
| 430.15 | 2400000 | 4322.9341 | 3493.3647 | 911.4351 | 0.00017419 | 157 | 23.6861 | 4.3229 | 3.4934 | 0.91144 | 0.00017419
| 429.15 | 2400000 | 4320.1284 | 3497.7986 | 912.4002 | 0.00017539 | 156 | 23.6861 | 4.3201 | 3.4978 | 0.9124 | 0.00017539
| 428.15 | 2400000 | 4317.3604 | 3502.2456 | 913.3608 | 0.00017661 | 155 | 23.6861 | 4.3174 | 3.5022 | 0.91336 | 0.00017661
| 427.15 | 2400000 | 4314.6294 | 3506.7053 | 914.317 | 0.00017784 | 154 | 23.6861 | 4.3146 | 3.5067 | 0.91432 | 0.00017784
| 426.15 | 2400000 | 4311.9355 | 3511.1777 | 915.2686 | 0.00017909 | 153 | 23.6861 | 4.3119 | 3.5112 | 0.91527 | 0.00017909
| 425.15 | 2400000 | 4309.2773 | 3515.6631 | 916.2156 | 0.00018036 | 152 | 23.6861 | 4.3093 | 3.5157 | 0.91622 | 0.00018036
| 424.15 | 2400000 | 4306.6553 | 3520.1609 | 917.1583 | 0.00018164 | 151 | 23.6861 | 4.3067 | 3.5202 | 0.91716 | 0.00018164
| 423.15 | 2400000 | 4304.0684 | 3524.6711 | 918.0964 | 0.00018295 | 150 | 23.6861 | 4.3041 | 3.5247 | 0.9181 | 0.00018295
| 422.15 | 2400000 | 4301.5161 | 3529.1938 | 919.0301 | 0.00018427 | 149 | 23.6861 | 4.3015 | 3.5292 | 0.91903 | 0.00018427
| 421.15 | 2400000 | 4298.9985 | 3533.729 | 919.9593 | 0.00018561 | 148 | 23.6861 | 4.299 | 3.5337 | 0.91996 | 0.00018561
| 420.15 | 2400000 | 4296.5142 | 3538.2764 | 920.8841 | 0.00018697 | 147 | 23.6861 | 4.2965 | 3.5383 | 0.92088 | 0.00018697
| 419.15 | 2400000 | 4294.0635 | 3542.8359 | 921.8045 | 0.00018835 | 146 | 23.6861 | 4.2941 | 3.5428 | 0.9218 | 0.00018835
| 418.15 | 2400000 | 4291.6455 | 3547.4075 | 922.7205 | 0.00018975 | 145 | 23.6861 | 4.2916 | 3.5474 | 0.92272 | 0.00018975
| 417.15 | 2400000 | 4289.2598 | 3551.9912 | 923.632 | 0.00019117 | 144 | 23.6861 | 4.2893 | 3.552 | 0.92363 | 0.00019117
| 416.15 | 2400000 | 4286.9067 | 3556.5869 | 924.5391 | 0.00019261 | 143 | 23.6861 | 4.2869 | 3.5566 | 0.92454 | 0.00019261
| 415.15 | 2400000 | 4284.585 | 3561.1943 | 925.4419 | 0.00019407 | 142 | 23.6861 | 4.2846 | 3.5612 | 0.92544 | 0.00019407
| 414.15 | 2400000 | 4282.2944 | 3565.8137 | 926.3403 | 0.00019556 | 141 | 23.6861 | 4.2823 | 3.5658 | 0.92634 | 0.00019556
| 413.15 | 2400000 | 4280.0347 | 3570.4446 | 927.2343 | 0.00019706 | 140 | 23.6861 | 4.28 | 3.5704 | 0.92723 | 0.00019706
| 412.15 | 2400000 | 4277.8057 | 3575.0872 | 928.124 | 0.00019859 | 139 | 23.6861 | 4.2778 | 3.5751 | 0.92812 | 0.00019859
| 411.15 | 2400000 | 4275.6064 | 3579.7415 | 929.0093 | 0.00020014 | 138 | 23.6861 | 4.2756 | 3.5797 | 0.92901 | 0.00020014
| 410.15 | 2400000 | 4273.437 | 3584.4072 | 929.8903 | 0.00020172 | 137 | 23.6861 | 4.2734 | 3.5844 | 0.92989 | 0.00020172
| 409.15 | 2400000 | 4271.2969 | 3589.0842 | 930.7668 | 0.00020332 | 136 | 23.6861 | 4.2713 | 3.5891 | 0.93077 | 0.00020332
| 408.15 | 2400000 | 4269.1855 | 3593.7727 | 931.6391 | 0.00020494 | 135 | 23.6861 | 4.2692 | 3.5938 | 0.93164 | 0.00020494
| 407.15 | 2400000 | 4267.103 | 3598.4722 | 932.507 | 0.00020659 | 134 | 23.6861 | 4.2671 | 3.5985 | 0.93251 | 0.00020659
| 406.15 | 2400000 | 4265.0488 | 3603.1831 | 933.3706 | 0.00020826 | 133 | 23.6861 | 4.265 | 3.6032 | 0.93337 | 0.00020826
| 405.15 | 2400000 | 4263.0225 | 3607.905 | 934.2299 | 0.00020996 | 132 | 23.6861 | 4.263 | 3.6079 | 0.93423 | 0.00020996
| 404.15 | 2400000 | 4261.0239 | 3612.6379 | 935.0848 | 0.00021169 | 131 | 23.6861 | 4.261 | 3.6126 | 0.93508 | 0.00021169
| 403.15 | 2400000 | 4259.0527 | 3617.3818 | 935.9354 | 0.00021345 | 130 | 23.6861 | 4.2591 | 3.6174 | 0.93594 | 0.00021345
| 402.15 | 2400000 | 4257.1089 | 3622.1365 | 936.7816 | 0.00021523 | 129 | 23.6861 | 4.2571 | 3.6221 | 0.93678 | 0.00021523
| 401.15 | 2400000 | 4255.1914 | 3626.9021 | 937.6235 | 0.00021704 | 128 | 23.6861 | 4.2552 | 3.6269 | 0.93762 | 0.00021704
| 400.15 | 2400000 | 4253.3003 | 3631.6782 | 938.4612 | 0.00021888 | 127 | 23.6861 | 4.2533 | 3.6317 | 0.93846 | 0.00021888
| 399.15 | 2400000 | 4251.4355 | 3636.4651 | 939.2944 | 0.00022075 | 126 | 23.6861 | 4.2514 | 3.6365 | 0.93929 | 0.00022075
| 398.15 | 2400000 | 4249.5962 | 3641.2625 | 940.1234 | 0.00022265 | 125 | 23.6861 | 4.2496 | 3.6413 | 0.94012 | 0.00022265
| 397.15 | 2400000 | 4247.7832 | 3646.0703 | 940.9481 | 0.00022458 | 124 | 23.6861 | 4.2478 | 3.6461 | 0.94095 | 0.00022458
| 396.15 | 2400000 | 4245.9951 | 3650.8884 | 941.7684 | 0.00022654 | 123 | 23.6861 | 4.246 | 3.6509 | 0.94177 | 0.00022654
| 395.15 | 2400000 | 4244.2324 | 3655.717 | 942.5844 | 0.00022854 | 122 | 23.6861 | 4.2442 | 3.6557 | 0.94258 | 0.00022854
| 394.15 | 2400000 | 4242.4941 | 3660.5557 | 943.396 | 0.00023057 | 121 | 23.6861 | 4.2425 | 3.6606 | 0.9434 | 0.00023057
| 393.15 | 2400000 | 4240.7808 | 3665.4043 | 944.2033 | 0.00023263 | 120 | 23.6861 | 4.2408 | 3.6654 | 0.9442 | 0.00023263
| 392.15 | 2400000 | 4239.0918 | 3670.2632 | 945.0063 | 0.00023473 | 119 | 23.6861 | 4.2391 | 3.6703 | 0.94501 | 0.00023473
| 391.15 | 2400000 | 4237.4272 | 3675.1318 | 945.8049 | 0.00023686 | 118 | 23.6861 | 4.2374 | 3.6751 | 0.9458 | 0.00023686
| 390.15 | 2400000 | 4235.7861 | 3680.0103 | 946.5992 | 0.00023903 | 117 | 23.6861 | 4.2358 | 3.68 | 0.9466 | 0.00023903
| 389.15 | 2400000 | 4234.1694 | 3684.8987 | 947.3891 | 0.00024123 | 116 | 23.6861 | 4.2342 | 3.6849 | 0.94739 | 0.00024123
| 388.15 | 2400000 | 4232.5757 | 3689.7964 | 948.1746 | 0.00024348 | 115 | 23.6861 | 4.2326 | 3.6898 | 0.94817 | 0.00024348
| 387.15 | 2400000 | 4231.0054 | 3694.7039 | 948.9558 | 0.00024576 | 114 | 23.6861 | 4.231 | 3.6947 | 0.94896 | 0.00024576
| 386.15 | 2400000 | 4229.4585 | 3699.6206 | 949.7326 | 0.00024808 | 113 | 23.6861 | 4.2295 | 3.6996 | 0.94973 | 0.00024808
| 385.15 | 2400000 | 4227.9341 | 3704.5466 | 950.505 | 0.00025045 | 112 | 23.6861 | 4.2279 | 3.7045 | 0.95051 | 0.00025045
| 384.15 | 2400000 | 4226.4331 | 3709.4819 | 951.2731 | 0.00025285 | 111 | 23.6861 | 4.2264 | 3.7095 | 0.95127 | 0.00025285
| 383.15 | 2400000 | 4224.9541 | 3714.4263 | 952.0367 | 0.0002553 | 110 | 23.6861 | 4.225 | 3.7144 | 0.95204 | 0.0002553
| 382.15 | 2400000 | 4223.498 | 3719.3794 | 952.7959 | 0.00025779 | 109 | 23.6861 | 4.2235 | 3.7194 | 0.9528 | 0.00025779
| 381.15 | 2400000 | 4222.064 | 3724.3416 | 953.5507 | 0.00026033 | 108 | 23.6861 | 4.2221 | 3.7243 | 0.95355 | 0.00026033
| 380.15 | 2400000 | 4220.6523 | 3729.3123 | 954.301 | 0.00026291 | 107 | 23.6861 | 4.2207 | 3.7293 | 0.9543 | 0.00026291
| 379.15 | 2400000 | 4219.2627 | 3734.2915 | 955.0469 | 0.00026554 | 106 | 23.6861 | 4.2193 | 3.7343 | 0.95505 | 0.00026554
| 378.15 | 2400000 | 4217.8945 | 3739.2793 | 955.7884 | 0.00026821 | 105 | 23.6861 | 4.2179 | 3.7393 | 0.95579 | 0.00026821
| 377.15 | 2400000 | 4216.5483 | 3744.2751 | 956.5254 | 0.00027094 | 104 | 23.6861 | 4.2165 | 3.7443 | 0.95653 | 0.00027094
| 376.15 | 2400000 | 4215.2236 | 3749.2793 | 957.2579 | 0.00027372 | 103 | 23.6861 | 4.2152 | 3.7493 | 0.95726 | 0.00027372
| 375.15 | 2400000 | 4213.9204 | 3754.2913 | 957.9859 | 0.00027654 | 102 | 23.6861 | 4.2139 | 3.7543 | 0.95799 | 0.00027654
| 374.15 | 2400000 | 4212.6387 | 3759.311 | 958.7094 | 0.00027942 | 101 | 23.6861 | 4.2126 | 3.7593 | 0.95871 | 0.00027942
| 373.15 | 2400000 | 4211.3784 | 3764.3384 | 959.4284 | 0.00028236 | 100 | 23.6861 | 4.2114 | 3.7643 | 0.95943 | 0.00028236
| 372.15 | 2400000 | 4210.1387 | 3769.373 | 960.1428 | 0.00028535 | 99 | 23.6861 | 4.2101 | 3.7694 | 0.96014 | 0.00028535
| 371.15 | 2400000 | 4208.9204 | 3774.415 | 960.8527 | 0.0002884 | 98 | 23.6861 | 4.2089 | 3.7744 | 0.96085 | 0.0002884
| 370.15 | 2400000 | 4207.7231 | 3779.4641 | 961.558 | 0.00029151 | 97 | 23.6861 | 4.2077 | 3.7795 | 0.96156 | 0.00029151
| 369.15 | 2400000 | 4206.5464 | 3784.52 | 962.2587 | 0.00029467 | 96 | 23.6861 | 4.2065 | 3.7845 | 0.96226 | 0.00029467
| 368.15 | 2400000 | 4205.3906 | 3789.5825 | 962.9548 | 0.0002979 | 95 | 23.6861 | 4.2054 | 3.7896 | 0.96295 | 0.0002979
| 367.15 | 2400000 | 4204.2554 | 3794.6516 | 963.6462 | 0.00030119 | 94 | 23.6861 | 4.2043 | 3.7947 | 0.96365 | 0.00030119
| 366.15 | 2400000 | 4203.1411 | 3799.7266 | 964.333 | 0.00030455 | 93 | 23.6861 | 4.2031 | 3.7997 | 0.96433 | 0.00030455
| 365.15 | 2400000 | 4202.0469 | 3804.8076 | 965.0151 | 0.00030797 | 92 | 23.6861 | 4.202 | 3.8048 | 0.96502 | 0.00030797
| 364.15 | 2400000 | 4200.9736 | 3809.8945 | 965.6926 | 0.00031146 | 91 | 23.6861 | 4.201 | 3.8099 | 0.96569 | 0.00031146
| 363.15 | 2400000 | 4199.9204 | 3814.9866 | 966.3654 | 0.00031503 | 90 | 23.6861 | 4.1999 | 3.815 | 0.96637 | 0.00031503
| 362.15 | 2400000 | 4198.8877 | 3820.084 | 967.0333 | 0.00031866 | 89 | 23.6861 | 4.1989 | 3.8201 | 0.96703 | 0.00031866
| 361.15 | 2400000 | 4197.875 | 3825.1863 | 967.6965 | 0.00032237 | 88 | 23.6861 | 4.1979 | 3.8252 | 0.9677 | 0.00032237
| 360.15 | 2400000 | 4196.8833 | 3830.293 | 968.355 | 0.00032615 | 87 | 23.6861 | 4.1969 | 3.8303 | 0.96835 | 0.00032615
| 359.15 | 2400000 | 4195.9111 | 3835.4041 | 969.0086 | 0.00033001 | 86 | 23.6861 | 4.1959 | 3.8354 | 0.96901 | 0.00033001
| 358.15 | 2400000 | 4194.9595 | 3840.519 | 969.6574 | 0.00033396 | 85 | 23.6861 | 4.195 | 3.8405 | 0.96966 | 0.00033396
| 357.15 | 2400000 | 4194.0278 | 3845.6377 | 970.3013 | 0.00033798 | 84 | 23.6861 | 4.194 | 3.8456 | 0.9703 | 0.00033798
| 356.15 | 2400000 | 4193.1162 | 3850.7598 | 970.9404 | 0.00034209 | 83 | 23.6861 | 4.1931 | 3.8508 | 0.97094 | 0.00034209
| 355.15 | 2400000 | 4192.2251 | 3855.8845 | 971.5745 | 0.00034629 | 82 | 23.6861 | 4.1922 | 3.8559 | 0.97157 | 0.00034629
| 354.15 | 2400000 | 4191.3535 | 3861.012 | 972.2036 | 0.00035058 | 81 | 23.6861 | 4.1914 | 3.861 | 0.9722 | 0.00035058
| 353.15 | 2400000 | 4190.5024 | 3866.1416 | 972.8278 | 0.00035496 | 80 | 23.6861 | 4.1905 | 3.8661 | 0.97283 | 0.00035496
| 352.15 | 2400000 | 4189.6709 | 3871.2729 | 973.447 | 0.00035943 | 79 | 23.6861 | 4.1897 | 3.8713 | 0.97345 | 0.00035943
| 351.15 | 2400000 | 4188.8599 | 3876.4055 | 974.0611 | 0.000364 | 78 | 23.6861 | 4.1889 | 3.8764 | 0.97406 | 0.000364
| 350.15 | 2400000 | 4188.0684 | 3881.5391 | 974.6702 | 0.00036868 | 77 | 23.6861 | 4.1881 | 3.8815 | 0.97467 | 0.00036868
| 349.15 | 2400000 | 4187.2974 | 3886.6731 | 975.2741 | 0.00037345 | 76 | 23.6861 | 4.1873 | 3.8867 | 0.97527 | 0.00037345
| 348.15 | 2400000 | 4186.5459 | 3891.8069 | 975.8729 | 0.00037834 | 75 | 23.6861 | 4.1865 | 3.8918 | 0.97587 | 0.00037834
| 347.15 | 2400000 | 4185.8145 | 3896.9402 | 976.4665 | 0.00038333 | 74 | 23.6861 | 4.1858 | 3.8969 | 0.97647 | 0.00038333
| 346.15 | 2400000 | 4185.103 | 3902.0725 | 977.0549 | 0.00038844 | 73 | 23.6861 | 4.1851 | 3.9021 | 0.97705 | 0.00038844
| 345.15 | 2400000 | 4184.4116 | 3907.2031 | 977.638 | 0.00039366 | 72 | 23.6861 | 4.1844 | 3.9072 | 0.97764 | 0.00039366
| 344.15 | 2400000 | 4183.7402 | 3912.3315 | 978.2159 | 0.00039901 | 71 | 23.6861 | 4.1837 | 3.9123 | 0.97822 | 0.00039901
| 343.15 | 2400000 | 4183.0889 | 3917.4573 | 978.7884 | 0.00040447 | 70 | 23.6861 | 4.1831 | 3.9175 | 0.97879 | 0.00040447
| 342.15 | 2400000 | 4182.457 | 3922.5796 | 979.3555 | 0.00041007 | 69 | 23.6861 | 4.1825 | 3.9226 | 0.97936 | 0.00041007
| 341.15 | 2400000 | 4181.8457 | 3927.6978 | 979.9172 | 0.0004158 | 68 | 23.6861 | 4.1818 | 3.9277 | 0.97992 | 0.0004158
| 340.15 | 2400000 | 4181.2539 | 3932.8115 | 980.4734 | 0.00042166 | 67 | 23.6861 | 4.1813 | 3.9328 | 0.98047 | 0.00042166
| 339.15 | 2400000 | 4180.6821 | 3937.9199 | 981.0242 | 0.00042767 | 66 | 23.6861 | 4.1807 | 3.9379 | 0.98102 | 0.00042767
| 338.15 | 2400000 | 4180.1309 | 3943.0225 | 981.5694 | 0.00043382 | 65 | 23.6861 | 4.1801 | 3.943 | 0.98157 | 0.00043382
| 337.15 | 2400000 | 4179.5991 | 3948.1179 | 982.1089 | 0.00044012 | 64 | 23.6861 | 4.1796 | 3.9481 | 0.98211 | 0.00044012
| 336.15 | 2400000 | 4179.0874 | 3953.2061 | 982.6429 | 0.00044657 | 63 | 23.6861 | 4.1791 | 3.9532 | 0.98264 | 0.00044657
| 335.15 | 2400000 | 4178.5957 | 3958.2861 | 983.1711 | 0.00045319 | 62 | 23.6861 | 4.1786 | 3.9583 | 0.98317 | 0.00045319
| 334.15 | 2400000 | 4178.1245 | 3963.3569 | 983.6936 | 0.00045997 | 61 | 23.6861 | 4.1781 | 3.9634 | 0.98369 | 0.00045997
| 333.15 | 2400000 | 4177.6729 | 3968.4177 | 984.2103 | 0.00046692 | 60 | 23.6861 | 4.1777 | 3.9684 | 0.98421 | 0.00046692
| 332.15 | 2400000 | 4177.2417 | 3973.468 | 984.7211 | 0.00047404 | 59 | 23.6861 | 4.1772 | 3.9735 | 0.98472 | 0.00047404
| 331.15 | 2400000 | 4176.8301 | 3978.5063 | 985.226 | 0.00048135 | 58 | 23.6861 | 4.1768 | 3.9785 | 0.98523 | 0.00048135
| 330.15 | 2400000 | 4176.439 | 3983.5325 | 985.7249 | 0.00048885 | 57 | 23.6861 | 4.1764 | 3.9835 | 0.98572 | 0.00048885
| 329.15 | 2400000 | 4176.0684 | 3988.5447 | 986.2178 | 0.00049655 | 56 | 23.6861 | 4.1761 | 3.9885 | 0.98622 | 0.00049655
| 328.15 | 2400000 | 4175.7173 | 3993.5425 | 986.7046 | 0.00050445 | 55 | 23.6861 | 4.1757 | 3.9935 | 0.9867 | 0.00050445
| 327.15 | 2400000 | 4175.3867 | 3998.5249 | 987.1852 | 0.00051256 | 54 | 23.6861 | 4.1754 | 3.9985 | 0.98719 | 0.00051256
| 326.15 | 2400000 | 4175.0767 | 4003.4905 | 987.6596 | 0.00052088 | 53 | 23.6861 | 4.1751 | 4.0035 | 0.98766 | 0.00052088
| 325.15 | 2400000 | 4174.7866 | 4008.4385 | 988.1277 | 0.00052944 | 52 | 23.6861 | 4.1748 | 4.0084 | 0.98813 | 0.00052944
| 324.15 | 2400000 | 4174.5171 | 4013.3677 | 988.5895 | 0.00053822 | 51 | 23.6861 | 4.1745 | 4.0134 | 0.98859 | 0.00053822
| 323.15 | 2400000 | 4174.2681 | 4018.2771 | 989.0449 | 0.00054725 | 50 | 23.6861 | 4.1743 | 4.0183 | 0.98904 | 0.00054725
| 322.15 | 2400000 | 4174.0396 | 4023.165 | 989.4937 | 0.00055653 | 49 | 23.6861 | 4.174 | 4.0232 | 0.98949 | 0.00055653
| 321.15 | 2400000 | 4173.8315 | 4028.031 | 989.936 | 0.00056608 | 48 | 23.6861 | 4.1738 | 4.028 | 0.98994 | 0.00056608
| 320.15 | 2400000 | 4173.6445 | 4032.873 | 990.3716 | 0.00057589 | 47 | 23.6861 | 4.1736 | 4.0329 | 0.99037 | 0.00057589
| 319.15 | 2400000 | 4173.478 | 4037.6904 | 990.8005 | 0.00058599 | 46 | 23.6861 | 4.1735 | 4.0377 | 0.9908 | 0.00058599
| 318.15 | 2400000 | 4173.3325 | 4042.4814 | 991.2226 | 0.00059638 | 45 | 23.6861 | 4.1733 | 4.0425 | 0.99122 | 0.00059638
| 317.15 | 2400000 | 4173.208 | 4047.2451 | 991.6378 | 0.00060707 | 44 | 23.6861 | 4.1732 | 4.0472 | 0.99164 | 0.00060707
| 316.15 | 2400000 | 4173.105 | 4051.9797 | 992.046 | 0.00061809 | 43 | 23.6861 | 4.1731 | 4.052 | 0.99205 | 0.00061809
| 315.15 | 2400000 | 4173.0229 | 4056.6838 | 992.4471 | 0.00062943 | 42 | 23.6861 | 4.173 | 4.0567 | 0.99245 | 0.00062943
| 314.15 | 2400000 | 4172.9629 | 4061.3564 | 992.8411 | 0.00064112 | 41 | 23.6861 | 4.173 | 4.0614 | 0.99284 | 0.00064112
| 313.15 | 2400000 | 4172.9243 | 4065.9956 | 993.2278 | 0.00065316 | 40 | 23.6861 | 4.1729 | 4.066 | 0.99323 | 0.00065316
| 312.15 | 2400000 | 4172.9082 | 4070.5999 | 993.6071 | 0.00066558 | 39 | 23.6861 | 4.1729 | 4.0706 | 0.99361 | 0.00066558
| 311.15 | 2400000 | 4172.915 | 4075.1677 | 993.979 | 0.00067839 | 38 | 23.6861 | 4.1729 | 4.0752 | 0.99398 | 0.00067839
| 310.15 | 2400000 | 4172.9443 | 4079.6978 | 994.3433 | 0.00069161 | 37 | 23.6861 | 4.1729 | 4.0797 | 0.99434 | 0.00069161
| 309.15 | 2400000 | 4172.9966 | 4084.1882 | 994.7 | 0.00070525 | 36 | 23.6861 | 4.173 | 4.0842 | 0.9947 | 0.00070525
| 308.15 | 2400000 | 4173.0732 | 4088.6377 | 995.0488 | 0.00071933 | 35 | 23.6861 | 4.1731 | 4.0886 | 0.99505 | 0.00071933
| 307.15 | 2400000 | 4173.1738 | 4093.0442 | 995.3897 | 0.00073388 | 34 | 23.6861 | 4.1732 | 4.093 | 0.99539 | 0.00073388
| 306.15 | 2400000 | 4173.2993 | 4097.4062 | 995.7226 | 0.00074891 | 33 | 23.6861 | 4.1733 | 4.0974 | 0.99572 | 0.00074891
| 305.15 | 2400000 | 4173.4507 | 4101.7217 | 996.0474 | 0.00076445 | 32 | 23.6861 | 4.1735 | 4.1017 | 0.99605 | 0.00076445
| 304.15 | 2400000 | 4173.6284 | 4105.9897 | 996.3638 | 0.00078051 | 31 | 23.6861 | 4.1736 | 4.106 | 0.99636 | 0.00078051
| 303.15 | 2400000 | 4173.834 | 4110.208 | 996.6719 | 0.00079713 | 30 | 23.6861 | 4.1738 | 4.1102 | 0.99667 | 0.00079713
| 302.15 | 2400000 | 4174.0674 | 4114.375 | 996.9713 | 0.00081434 | 29 | 23.6861 | 4.1741 | 4.1144 | 0.99697 | 0.00081434
| 301.15 | 2400000 | 4174.3306 | 4118.4888 | 997.2621 | 0.00083215 | 28 | 23.6861 | 4.1743 | 4.1185 | 0.99726 | 0.00083215
| 300.15 | 2400000 | 4174.625 | 4122.5479 | 997.544 | 0.0008506 | 27 | 23.6861 | 4.1746 | 4.1225 | 0.99754 | 0.0008506
| 299.15 | 2400000 | 4174.9512 | 4126.5503 | 997.8169 | 0.00086973 | 26 | 23.6861 | 4.175 | 4.1266 | 0.99782 | 0.00086973
| 298.15 | 2400000 | 4175.312 | 4130.4941 | 998.0806 | 0.00088955 | 25 | 23.6861 | 4.1753 | 4.1305 | 0.99808 | 0.00088955
| 297.15 | 2400000 | 4175.7085 | 4134.3784 | 998.335 | 0.00091013 | 24 | 23.6861 | 4.1757 | 4.1344 | 0.99833 | 0.00091013
| 296.15 | 2400000 | 4176.1431 | 4138.2007 | 998.5798 | 0.00093148 | 23 | 23.6861 | 4.1761 | 4.1382 | 0.99858 | 0.00093148
| 295.15 | 2400000 | 4176.6177 | 4141.9595 | 998.8149 | 0.00095365 | 22 | 23.6861 | 4.1766 | 4.142 | 0.99881 | 0.00095365
| 294.15 | 2400000 | 4177.1357 | 4145.6533 | 999.04 | 0.00097669 | 21 | 23.6861 | 4.1771 | 4.1457 | 0.99904 | 0.00097669
| 293.15 | 2400000 | 4177.6992 | 4149.2808 | 999.2551 | 0.0010006 | 20 | 23.6861 | 4.1777 | 4.1493 | 0.99926 | 0.0010006
| 292.15 | 2400000 | 4178.3125 | 4152.8398 | 999.4598 | 0.0010255 | 19 | 23.6861 | 4.1783 | 4.1528 | 0.99946 | 0.0010255
| 291.15 | 2400000 | 4178.9785 | 4156.3291 | 999.6541 | 0.0010515 | 18 | 23.6861 | 4.179 | 4.1563 | 0.99965 | 0.0010515
| 290.15 | 2400000 | 4179.7017 | 4159.7476 | 999.8375 | 0.0010785 | 17 | 23.6861 | 4.1797 | 4.1597 | 0.99984 | 0.0010785
| 289.15 | 2400000 | 4180.4863 | 4163.0933 | 1000.0098 | 0.0011066 | 16 | 23.6861 | 4.1805 | 4.1631 | 1 | 0.0011066
| 288.15 | 2400000 | 4181.3379 | 4166.3657 | 1000.1709 | 0.001136 | 15 | 23.6861 | 4.1813 | 4.1664 | 1.0002 | 0.001136
| 287.15 | 2400000 | 4182.2617 | 4169.563 | 1000.3204 | 0.0011666 | 14 | 23.6861 | 4.1823 | 4.1696 | 1.0003 | 0.0011666
| 286.15 | 2400000 | 4183.2646 | 4172.6851 | 1000.4581 | 0.0011985 | 13 | 23.6861 | 4.1833 | 4.1727 | 1.0005 | 0.0011985
| 285.15 | 2400000 | 4184.3535 | 4175.73 | 1000.5837 | 0.0012319 | 12 | 23.6861 | 4.1844 | 4.1757 | 1.0006 | 0.0012319
| 284.15 | 2400000 | 4185.5361 | 4178.6973 | 1000.6968 | 0.0012669 | 11 | 23.6861 | 4.1855 | 4.1787 | 1.0007 | 0.0012669
| 283.15 | 2400000 | 4186.8213 | 4181.5869 | 1000.7971 | 0.0013034 | 10 | 23.6861 | 4.1868 | 4.1816 | 1.0008 | 0.0013034
| 282.15 | 2400000 | 4188.2188 | 4184.3979 | 1000.8843 | 0.0013417 | 9 | 23.6861 | 4.1882 | 4.1844 | 1.0009 | 0.0013417
| 281.15 | 2400000 | 4189.7388 | 4187.1304 | 1000.958 | 0.0013818 | 8 | 23.6861 | 4.1897 | 4.1871 | 1.001 | 0.0013818
| 280.15 | 2400000 | 4191.394 | 4189.7837 | 1001.0178 | 0.0014238 | 7 | 23.6861 | 4.1914 | 4.1898 | 1.001 | 0.0014238
| 279.15 | 2400000 | 4193.1978 | 4192.3584 | 1001.0634 | 0.001468 | 6 | 23.6861 | 4.1932 | 4.1924 | 1.0011 | 0.001468
| 278.15 | 2400000 | 4195.1641 | 4194.8555 | 1001.0942 | 0.0015143 | 5 | 23.6861 | 4.1952 | 4.1949 | 1.0011 | 0.0015143
| 277.15 | 2400000 | 4197.3096 | 4197.2744 | 1001.1099 | 0.0015631 | 4 | 23.6861 | 4.1973 | 4.1973 | 1.0011 | 0.0015631
| 276.15 | 2400000 | 4199.6523 | 4199.6172 | 1001.1099 | 0.0016145 | 3 | 23.6861 | 4.1997 | 4.1996 | 1.0011 | 0.0016145
| 275.15 | 2400000 | 4202.2129 | 4201.8838 | 1001.0937 | 0.0016686 | 2 | 23.6861 | 4.2022 | 4.2019 | 1.0011 | 0.0016686
| 274.15 | 2400000 | 4205.0122 | 4204.0771 | 1001.0608 | 0.0017256 | 0.99999 | 23.6861 | 4.205 | 4.2041 | 1.0011 | 0.0017256
| 273.15 | 2400000 | 4208.0757 | 4206.1978 | 1001.0106 | 0.0017858 | -6.1035e-06 | 23.6861 | 4.2081 | 4.2062 | 1.001 | 0.0017858
| 473.15 | 2300000 | 4489.6533 | 3316.4319 | 865.2357 | 0.00013451 | 200 | 22.6992 | 4.4897 | 3.3164 | 0.86524 | 0.00013451
| 472.15 | 2300000 | 4484.5093 | 3320.2124 | 866.4208 | 0.00013523 | 199 | 22.6992 | 4.4845 | 3.3202 | 0.86642 | 0.00013523
| 471.15 | 2300000 | 4479.4409 | 3324.0107 | 867.6 | 0.00013595 | 198 | 22.6992 | 4.4794 | 3.324 | 0.8676 | 0.00013595
| 470.15 | 2300000 | 4474.4463 | 3327.8264 | 868.7734 | 0.00013669 | 197 | 22.6992 | 4.4744 | 3.3278 | 0.86877 | 0.00013669
| 469.15 | 2300000 | 4469.5254 | 3331.6597 | 869.941 | 0.00013743 | 196 | 22.6992 | 4.4695 | 3.3317 | 0.86994 | 0.00013743
| 468.15 | 2300000 | 4464.6758 | 3335.51 | 871.1029 | 0.00013818 | 195 | 22.6992 | 4.4647 | 3.3355 | 0.8711 | 0.00013818
| 467.15 | 2300000 | 4459.897 | 3339.3774 | 872.2591 | 0.00013893 | 194 | 22.6992 | 4.4599 | 3.3394 | 0.87226 | 0.00013893
| 466.15 | 2300000 | 4455.187 | 3343.2617 | 873.4096 | 0.0001397 | 193 | 22.6992 | 4.4552 | 3.3433 | 0.87341 | 0.0001397
| 465.15 | 2300000 | 4450.5449 | 3347.1631 | 874.5546 | 0.00014047 | 192 | 22.6992 | 4.4505 | 3.3472 | 0.87455 | 0.00014047
| 464.15 | 2300000 | 4445.9702 | 3351.0811 | 875.6939 | 0.00014125 | 191 | 22.6992 | 4.446 | 3.3511 | 0.87569 | 0.00014125
| 463.15 | 2300000 | 4441.4609 | 3355.0159 | 876.8278 | 0.00014205 | 190 | 22.6992 | 4.4415 | 3.355 | 0.87683 | 0.00014205
| 462.15 | 2300000 | 4437.0161 | 3358.967 | 877.9561 | 0.00014284 | 189 | 22.6992 | 4.437 | 3.359 | 0.87796 | 0.00014284
| 461.15 | 2300000 | 4432.6348 | 3362.9346 | 879.0791 | 0.00014365 | 188 | 22.6992 | 4.4326 | 3.3629 | 0.87908 | 0.00014365
| 460.15 | 2300000 | 4428.3154 | 3366.9185 | 880.1967 | 0.00014447 | 187 | 22.6992 | 4.4283 | 3.3669 | 0.8802 | 0.00014447
| 459.15 | 2300000 | 4424.0581 | 3370.9185 | 881.3088 | 0.0001453 | 186 | 22.6992 | 4.4241 | 3.3709 | 0.88131 | 0.0001453
| 458.15 | 2300000 | 4419.8604 | 3374.9346 | 882.4157 | 0.00014613 | 185 | 22.6992 | 4.4199 | 3.3749 | 0.88242 | 0.00014613
| 457.15 | 2300000 | 4415.7227 | 3378.9666 | 883.5173 | 0.00014698 | 184 | 22.6992 | 4.4157 | 3.379 | 0.88352 | 0.00014698
| 456.15 | 2300000 | 4411.6426 | 3383.0144 | 884.6136 | 0.00014783 | 183 | 22.6992 | 4.4116 | 3.383 | 0.88461 | 0.00014783
| 455.15 | 2300000 | 4407.6206 | 3387.0779 | 885.7048 | 0.0001487 | 182 | 22.6992 | 4.4076 | 3.3871 | 0.8857 | 0.0001487
| 454.15 | 2300000 | 4403.6543 | 3391.157 | 886.7908 | 0.00014958 | 181 | 22.6992 | 4.4037 | 3.3912 | 0.88679 | 0.00014958
| 453.15 | 2300000 | 4399.7441 | 3395.2515 | 887.8716 | 0.00015046 | 180 | 22.6992 | 4.3997 | 3.3953 | 0.88787 | 0.00015046
| 452.15 | 2300000 | 4395.8882 | 3399.3616 | 888.9473 | 0.00015136 | 179 | 22.6992 | 4.3959 | 3.3994 | 0.88895 | 0.00015136
| 451.15 | 2300000 | 4392.0864 | 3403.4868 | 890.0179 | 0.00015226 | 178 | 22.6992 | 4.3921 | 3.4035 | 0.89002 | 0.00015226
| 450.15 | 2300000 | 4388.3369 | 3407.6272 | 891.0836 | 0.00015318 | 177 | 22.6992 | 4.3883 | 3.4076 | 0.89108 | 0.00015318
| 449.15 | 2300000 | 4384.6396 | 3411.7825 | 892.1441 | 0.00015411 | 176 | 22.6992 | 4.3846 | 3.4118 | 0.89214 | 0.00015411
| 448.15 | 2300000 | 4380.9937 | 3415.9529 | 893.1997 | 0.00015505 | 175 | 22.6992 | 4.381 | 3.416 | 0.8932 | 0.00015505
| 447.15 | 2300000 | 4377.3984 | 3420.1379 | 894.2503 | 0.000156 | 174 | 22.6992 | 4.3774 | 3.4201 | 0.89425 | 0.000156
| 446.15 | 2300000 | 4373.8521 | 3424.3376 | 895.296 | 0.00015697 | 173 | 22.6992 | 4.3739 | 3.4243 | 0.8953 | 0.00015697
| 445.15 | 2300000 | 4370.355 | 3428.5522 | 896.3368 | 0.00015794 | 172 | 22.6992 | 4.3704 | 3.4286 | 0.89634 | 0.00015794
| 444.15 | 2300000 | 4366.9062 | 3432.781 | 897.3727 | 0.00015893 | 171 | 22.6992 | 4.3669 | 3.4328 | 0.89737 | 0.00015893
| 443.15 | 2300000 | 4363.5044 | 3437.0244 | 898.4038 | 0.00015993 | 170 | 22.6992 | 4.3635 | 3.437 | 0.8984 | 0.00015993
| 442.15 | 2300000 | 4360.1489 | 3441.282 | 899.43 | 0.00016094 | 169 | 22.6992 | 4.3601 | 3.4413 | 0.89943 | 0.00016094
| 441.15 | 2300000 | 4356.8398 | 3445.554 | 900.4515 | 0.00016197 | 168 | 22.6992 | 4.3568 | 3.4456 | 0.90045 | 0.00016197
| 440.15 | 2300000 | 4353.5757 | 3449.8398 | 901.4681 | 0.00016301 | 167 | 22.6992 | 4.3536 | 3.4498 | 0.90147 | 0.00016301
| 439.15 | 2300000 | 4350.356 | 3454.1396 | 902.48 | 0.00016406 | 166 | 22.6992 | 4.3504 | 3.4541 | 0.90248 | 0.00016406
| 438.15 | 2300000 | 4347.1807 | 3458.4534 | 903.4872 | 0.00016512 | 165 | 22.6992 | 4.3472 | 3.4585 | 0.90349 | 0.00016512
| 437.15 | 2300000 | 4344.0479 | 3462.781 | 904.4896 | 0.0001662 | 164 | 22.6992 | 4.344 | 3.4628 | 0.90449 | 0.0001662
| 436.15 | 2300000 | 4340.958 | 3467.1223 | 905.4874 | 0.00016729 | 163 | 22.6992 | 4.341 | 3.4671 | 0.90549 | 0.00016729
| 435.15 | 2300000 | 4337.9097 | 3471.4773 | 906.4805 | 0.0001684 | 162 | 22.6992 | 4.3379 | 3.4715 | 0.90648 | 0.0001684
| 434.15 | 2300000 | 4334.9028 | 3475.8455 | 907.4689 | 0.00016952 | 161 | 22.6992 | 4.3349 | 3.4758 | 0.90747 | 0.00016952
| 433.15 | 2300000 | 4331.9365 | 3480.2273 | 908.4528 | 0.00017066 | 160 | 22.6992 | 4.3319 | 3.4802 | 0.90845 | 0.00017066
| 432.15 | 2300000 | 4329.0107 | 3484.6226 | 909.4319 | 0.00017181 | 159 | 22.6992 | 4.329 | 3.4846 | 0.90943 | 0.00017181
| 431.15 | 2300000 | 4326.124 | 3489.0308 | 910.4066 | 0.00017298 | 158 | 22.6992 | 4.3261 | 3.489 | 0.91041 | 0.00017298
| 430.15 | 2300000 | 4323.2764 | 3493.4524 | 911.3766 | 0.00017417 | 157 | 22.6992 | 4.3233 | 3.4935 | 0.91138 | 0.00017417
| 429.15 | 2300000 | 4320.4673 | 3497.8867 | 912.3421 | 0.00017537 | 156 | 22.6992 | 4.3205 | 3.4979 | 0.91234 | 0.00017537
| 428.15 | 2300000 | 4317.6958 | 3502.3342 | 913.303 | 0.00017658 | 155 | 22.6992 | 4.3177 | 3.5023 | 0.9133 | 0.00017658
| 427.15 | 2300000 | 4314.9619 | 3506.7947 | 914.2594 | 0.00017782 | 154 | 22.6992 | 4.315 | 3.5068 | 0.91426 | 0.00017782
| 426.15 | 2300000 | 4312.2646 | 3511.2678 | 915.2113 | 0.00017907 | 153 | 22.6992 | 4.3123 | 3.5113 | 0.91521 | 0.00017907
| 425.15 | 2300000 | 4309.6035 | 3515.7537 | 916.1586 | 0.00018033 | 152 | 22.6992 | 4.3096 | 3.5158 | 0.91616 | 0.00018033
| 424.15 | 2300000 | 4306.978 | 3520.252 | 917.1016 | 0.00018162 | 151 | 22.6992 | 4.307 | 3.5203 | 0.9171 | 0.00018162
| 423.15 | 2300000 | 4304.3882 | 3524.7629 | 918.04 | 0.00018292 | 150 | 22.6992 | 4.3044 | 3.5248 | 0.91804 | 0.00018292
| 422.15 | 2300000 | 4301.833 | 3529.2864 | 918.9739 | 0.00018424 | 149 | 22.6992 | 4.3018 | 3.5293 | 0.91897 | 0.00018424
| 421.15 | 2300000 | 4299.312 | 3533.8223 | 919.9034 | 0.00018558 | 148 | 22.6992 | 4.2993 | 3.5338 | 0.9199 | 0.00018558
| 420.15 | 2300000 | 4296.8252 | 3538.3704 | 920.8285 | 0.00018694 | 147 | 22.6992 | 4.2968 | 3.5384 | 0.92083 | 0.00018694
| 419.15 | 2300000 | 4294.3716 | 3542.9304 | 921.7491 | 0.00018832 | 146 | 22.6992 | 4.2944 | 3.5429 | 0.92175 | 0.00018832
| 418.15 | 2300000 | 4291.9507 | 3547.5029 | 922.6653 | 0.00018972 | 145 | 22.6992 | 4.292 | 3.5475 | 0.92267 | 0.00018972
| 417.15 | 2300000 | 4289.5625 | 3552.0874 | 923.5771 | 0.00019114 | 144 | 22.6992 | 4.2896 | 3.5521 | 0.92358 | 0.00019114
| 416.15 | 2300000 | 4287.2065 | 3556.6836 | 924.4846 | 0.00019258 | 143 | 22.6992 | 4.2872 | 3.5567 | 0.92448 | 0.00019258
| 415.15 | 2300000 | 4284.8823 | 3561.292 | 925.3876 | 0.00019405 | 142 | 22.6992 | 4.2849 | 3.5613 | 0.92539 | 0.00019405
| 414.15 | 2300000 | 4282.5894 | 3565.9121 | 926.2862 | 0.00019553 | 141 | 22.6992 | 4.2826 | 3.5659 | 0.92629 | 0.00019553
| 413.15 | 2300000 | 4280.3271 | 3570.5439 | 927.1805 | 0.00019704 | 140 | 22.6992 | 4.2803 | 3.5705 | 0.92718 | 0.00019704
| 412.15 | 2300000 | 4278.0952 | 3575.1873 | 928.0704 | 0.00019857 | 139 | 22.6992 | 4.2781 | 3.5752 | 0.92807 | 0.00019857
| 411.15 | 2300000 | 4275.8936 | 3579.8423 | 928.9559 | 0.00020012 | 138 | 22.6992 | 4.2759 | 3.5798 | 0.92896 | 0.00020012
| 410.15 | 2300000 | 4273.7222 | 3584.5088 | 929.8371 | 0.00020169 | 137 | 22.6992 | 4.2737 | 3.5845 | 0.92984 | 0.00020169
| 409.15 | 2300000 | 4271.5796 | 3589.1868 | 930.7139 | 0.00020329 | 136 | 22.6992 | 4.2716 | 3.5892 | 0.93071 | 0.00020329
| 408.15 | 2300000 | 4269.4663 | 3593.8762 | 931.5864 | 0.00020492 | 135 | 22.6992 | 4.2695 | 3.5939 | 0.93159 | 0.00020492
| 407.15 | 2300000 | 4267.3813 | 3598.5767 | 932.4545 | 0.00020656 | 134 | 22.6992 | 4.2674 | 3.5986 | 0.93245 | 0.00020656
| 406.15 | 2300000 | 4265.3252 | 3603.2883 | 933.3183 | 0.00020824 | 133 | 22.6992 | 4.2653 | 3.6033 | 0.93332 | 0.00020824
| 405.15 | 2300000 | 4263.2969 | 3608.0112 | 934.1778 | 0.00020994 | 132 | 22.6992 | 4.2633 | 3.608 | 0.93418 | 0.00020994
| 404.15 | 2300000 | 4261.2959 | 3612.7451 | 935.0329 | 0.00021167 | 131 | 22.6992 | 4.2613 | 3.6127 | 0.93503 | 0.00021167
| 403.15 | 2300000 | 4259.3228 | 3617.49 | 935.8837 | 0.00021342 | 130 | 22.6992 | 4.2593 | 3.6175 | 0.93588 | 0.00021342
| 402.15 | 2300000 | 4257.3765 | 3622.2458 | 936.7302 | 0.0002152 | 129 | 22.6992 | 4.2574 | 3.6222 | 0.93673 | 0.0002152
| 401.15 | 2300000 | 4255.4575 | 3627.0122 | 937.5723 | 0.00021701 | 128 | 22.6992 | 4.2555 | 3.627 | 0.93757 | 0.00021701
| 400.15 | 2300000 | 4253.5645 | 3631.7896 | 938.4102 | 0.00021885 | 127 | 22.6992 | 4.2536 | 3.6318 | 0.93841 | 0.00021885
| 399.15 | 2300000 | 4251.6978 | 3636.5774 | 939.2437 | 0.00022072 | 126 | 22.6992 | 4.2517 | 3.6366 | 0.93924 | 0.00022072
| 398.15 | 2300000 | 4249.8569 | 3641.3757 | 940.0728 | 0.00022262 | 125 | 22.6992 | 4.2499 | 3.6414 | 0.94007 | 0.00022262
| 397.15 | 2300000 | 4248.042 | 3646.1848 | 940.8976 | 0.00022455 | 124 | 22.6992 | 4.248 | 3.6462 | 0.9409 | 0.00022455
| 396.15 | 2300000 | 4246.252 | 3651.0039 | 941.7181 | 0.00022652 | 123 | 22.6992 | 4.2463 | 3.651 | 0.94172 | 0.00022652
| 395.15 | 2300000 | 4244.4878 | 3655.8335 | 942.5343 | 0.00022851 | 122 | 22.6992 | 4.2445 | 3.6558 | 0.94253 | 0.00022851
| 394.15 | 2300000 | 4242.748 | 3660.6733 | 943.3461 | 0.00023054 | 121 | 22.6992 | 4.2427 | 3.6607 | 0.94335 | 0.00023054
| 393.15 | 2300000 | 4241.0332 | 3665.5232 | 944.1536 | 0.0002326 | 120 | 22.6992 | 4.241 | 3.6655 | 0.94415 | 0.0002326
| 392.15 | 2300000 | 4239.3423 | 3670.3833 | 944.9567 | 0.0002347 | 119 | 22.6992 | 4.2393 | 3.6704 | 0.94496 | 0.0002347
| 391.15 | 2300000 | 4237.6763 | 3675.2532 | 945.7556 | 0.00023683 | 118 | 22.6992 | 4.2377 | 3.6753 | 0.94576 | 0.00023683
| 390.15 | 2300000 | 4236.0337 | 3680.1328 | 946.55 | 0.000239 | 117 | 22.6992 | 4.236 | 3.6801 | 0.94655 | 0.000239
| 389.15 | 2300000 | 4234.415 | 3685.0222 | 947.3401 | 0.00024121 | 116 | 22.6992 | 4.2344 | 3.685 | 0.94734 | 0.00024121
| 388.15 | 2300000 | 4232.8203 | 3689.9214 | 948.1258 | 0.00024345 | 115 | 22.6992 | 4.2328 | 3.6899 | 0.94813 | 0.00024345
| 387.15 | 2300000 | 4231.2485 | 3694.8301 | 948.9072 | 0.00024573 | 114 | 22.6992 | 4.2312 | 3.6948 | 0.94891 | 0.00024573
| 386.15 | 2300000 | 4229.7002 | 3699.748 | 949.6841 | 0.00024806 | 113 | 22.6992 | 4.2297 | 3.6997 | 0.94968 | 0.00024806
| 385.15 | 2300000 | 4228.1748 | 3704.6755 | 950.4567 | 0.00025042 | 112 | 22.6992 | 4.2282 | 3.7047 | 0.95046 | 0.00025042
| 384.15 | 2300000 | 4226.6724 | 3709.6121 | 951.2249 | 0.00025282 | 111 | 22.6992 | 4.2267 | 3.7096 | 0.95122 | 0.00025282
| 383.15 | 2300000 | 4225.1924 | 3714.5576 | 951.9886 | 0.00025527 | 110 | 22.6992 | 4.2252 | 3.7146 | 0.95199 | 0.00025527
| 382.15 | 2300000 | 4223.7349 | 3719.5122 | 952.748 | 0.00025776 | 109 | 22.6992 | 4.2237 | 3.7195 | 0.95275 | 0.00025776
| 381.15 | 2300000 | 4222.2998 | 3724.4758 | 953.503 | 0.0002603 | 108 | 22.6992 | 4.2223 | 3.7245 | 0.9535 | 0.0002603
| 380.15 | 2300000 | 4220.8867 | 3729.448 | 954.2535 | 0.00026288 | 107 | 22.6992 | 4.2209 | 3.7294 | 0.95425 | 0.00026288
| 379.15 | 2300000 | 4219.4961 | 3734.4285 | 954.9995 | 0.00026551 | 106 | 22.6992 | 4.2195 | 3.7344 | 0.955 | 0.00026551
| 378.15 | 2300000 | 4218.127 | 3739.4177 | 955.7411 | 0.00026819 | 105 | 22.6992 | 4.2181 | 3.7394 | 0.95574 | 0.00026819
| 377.15 | 2300000 | 4216.7798 | 3744.415 | 956.4783 | 0.00027091 | 104 | 22.6992 | 4.2168 | 3.7444 | 0.95648 | 0.00027091
| 376.15 | 2300000 | 4215.4541 | 3749.4207 | 957.2109 | 0.00027369 | 103 | 22.6992 | 4.2155 | 3.7494 | 0.95721 | 0.00027369
| 375.15 | 2300000 | 4214.1499 | 3754.4341 | 957.9391 | 0.00027652 | 102 | 22.6992 | 4.2141 | 3.7544 | 0.95794 | 0.00027652
| 374.15 | 2300000 | 4212.8672 | 3759.4553 | 958.6627 | 0.0002794 | 101 | 22.6992 | 4.2129 | 3.7595 | 0.95866 | 0.0002794
| 373.15 | 2300000 | 4211.606 | 3764.4841 | 959.3818 | 0.00028233 | 100 | 22.6992 | 4.2116 | 3.7645 | 0.95938 | 0.00028233
| 372.15 | 2300000 | 4210.3657 | 3769.5205 | 960.0964 | 0.00028532 | 99 | 22.6992 | 4.2104 | 3.7695 | 0.9601 | 0.00028532
| 371.15 | 2300000 | 4209.1465 | 3774.5642 | 960.8063 | 0.00028837 | 98 | 22.6992 | 4.2091 | 3.7746 | 0.96081 | 0.00028837
| 370.15 | 2300000 | 4207.9482 | 3779.6147 | 961.5118 | 0.00029148 | 97 | 22.6992 | 4.2079 | 3.7796 | 0.96151 | 0.00029148
| 369.15 | 2300000 | 4206.7705 | 3784.6724 | 962.2126 | 0.00029465 | 96 | 22.6992 | 4.2068 | 3.7847 | 0.96221 | 0.00029465
| 368.15 | 2300000 | 4205.6143 | 3789.7366 | 962.9088 | 0.00029787 | 95 | 22.6992 | 4.2056 | 3.7897 | 0.96291 | 0.00029787
| 367.15 | 2300000 | 4204.4785 | 3794.8071 | 963.6004 | 0.00030117 | 94 | 22.6992 | 4.2045 | 3.7948 | 0.9636 | 0.00030117
| 366.15 | 2300000 | 4203.3633 | 3799.8838 | 964.2873 | 0.00030452 | 93 | 22.6992 | 4.2034 | 3.7999 | 0.96429 | 0.00030452
| 365.15 | 2300000 | 4202.2686 | 3804.9666 | 964.9695 | 0.00030795 | 92 | 22.6992 | 4.2023 | 3.805 | 0.96497 | 0.00030795
| 364.15 | 2300000 | 4201.1943 | 3810.0552 | 965.6471 | 0.00031144 | 91 | 22.6992 | 4.2012 | 3.8101 | 0.96565 | 0.00031144
| 363.15 | 2300000 | 4200.1406 | 3815.1492 | 966.3199 | 0.000315 | 90 | 22.6992 | 4.2001 | 3.8151 | 0.96632 | 0.000315
| 362.15 | 2300000 | 4199.1074 | 3820.2483 | 966.988 | 0.00031863 | 89 | 22.6992 | 4.1991 | 3.8202 | 0.96699 | 0.00031863
| 361.15 | 2300000 | 4198.0947 | 3825.3523 | 967.6514 | 0.00032234 | 88 | 22.6992 | 4.1981 | 3.8254 | 0.96765 | 0.00032234
| 360.15 | 2300000 | 4197.1021 | 3830.4609 | 968.3099 | 0.00032613 | 87 | 22.6992 | 4.1971 | 3.8305 | 0.96831 | 0.00032613
| 359.15 | 2300000 | 4196.1299 | 3835.5737 | 968.9636 | 0.00032999 | 86 | 22.6992 | 4.1961 | 3.8356 | 0.96896 | 0.00032999
| 358.15 | 2300000 | 4195.1777 | 3840.6907 | 969.6125 | 0.00033393 | 85 | 22.6992 | 4.1952 | 3.8407 | 0.96961 | 0.00033393
| 357.15 | 2300000 | 4194.2456 | 3845.8113 | 970.2565 | 0.00033796 | 84 | 22.6992 | 4.1942 | 3.8458 | 0.97026 | 0.00033796
| 356.15 | 2300000 | 4193.334 | 3850.9351 | 970.8956 | 0.00034207 | 83 | 22.6992 | 4.1933 | 3.8509 | 0.9709 | 0.00034207
| 355.15 | 2300000 | 4192.4424 | 3856.062 | 971.5298 | 0.00034626 | 82 | 22.6992 | 4.1924 | 3.8561 | 0.97153 | 0.00034626
| 354.15 | 2300000 | 4191.5708 | 3861.1914 | 972.1591 | 0.00035055 | 81 | 22.6992 | 4.1916 | 3.8612 | 0.97216 | 0.00035055
| 353.15 | 2300000 | 4190.7192 | 3866.3228 | 972.7833 | 0.00035493 | 80 | 22.6992 | 4.1907 | 3.8663 | 0.97278 | 0.00035493
| 352.15 | 2300000 | 4189.8877 | 3871.4561 | 973.4026 | 0.00035941 | 79 | 22.6992 | 4.1899 | 3.8715 | 0.9734 | 0.00035941
| 351.15 | 2300000 | 4189.0762 | 3876.5908 | 974.0168 | 0.00036398 | 78 | 22.6992 | 4.1891 | 3.8766 | 0.97402 | 0.00036398
| 350.15 | 2300000 | 4188.2847 | 3881.7263 | 974.6259 | 0.00036865 | 77 | 22.6992 | 4.1883 | 3.8817 | 0.97463 | 0.00036865
| 349.15 | 2300000 | 4187.5137 | 3886.8623 | 975.2299 | 0.00037343 | 76 | 22.6992 | 4.1875 | 3.8869 | 0.97523 | 0.00037343
| 348.15 | 2300000 | 4186.7622 | 3891.9983 | 975.8288 | 0.00037831 | 75 | 22.6992 | 4.1868 | 3.892 | 0.97583 | 0.00037831
| 347.15 | 2300000 | 4186.0308 | 3897.1338 | 976.4225 | 0.00038331 | 74 | 22.6992 | 4.186 | 3.8971 | 0.97642 | 0.00038331
| 346.15 | 2300000 | 4185.3193 | 3902.2683 | 977.0109 | 0.00038841 | 73 | 22.6992 | 4.1853 | 3.9023 | 0.97701 | 0.00038841
| 345.15 | 2300000 | 4184.6279 | 3907.4009 | 977.5941 | 0.00039364 | 72 | 22.6992 | 4.1846 | 3.9074 | 0.97759 | 0.00039364
| 344.15 | 2300000 | 4183.9565 | 3912.5317 | 978.172 | 0.00039898 | 71 | 22.6992 | 4.184 | 3.9125 | 0.97817 | 0.00039898
| 343.15 | 2300000 | 4183.3052 | 3917.6594 | 978.7446 | 0.00040445 | 70 | 22.6992 | 4.1833 | 3.9177 | 0.97874 | 0.00040445
| 342.15 | 2300000 | 4182.6738 | 3922.7842 | 979.3118 | 0.00041005 | 69 | 22.6992 | 4.1827 | 3.9228 | 0.97931 | 0.00041005
| 341.15 | 2300000 | 4182.0625 | 3927.9048 | 979.8735 | 0.00041577 | 68 | 22.6992 | 4.1821 | 3.9279 | 0.97987 | 0.00041577
| 340.15 | 2300000 | 4181.4712 | 3933.0208 | 980.4298 | 0.00042164 | 67 | 22.6992 | 4.1815 | 3.933 | 0.98043 | 0.00042164
| 339.15 | 2300000 | 4180.8999 | 3938.1313 | 980.9806 | 0.00042764 | 66 | 22.6992 | 4.1809 | 3.9381 | 0.98098 | 0.00042764
| 338.15 | 2300000 | 4180.3481 | 3943.2361 | 981.5258 | 0.00043379 | 65 | 22.6992 | 4.1803 | 3.9432 | 0.98153 | 0.00043379
| 337.15 | 2300000 | 4179.8169 | 3948.3342 | 982.0654 | 0.00044009 | 64 | 22.6992 | 4.1798 | 3.9483 | 0.98207 | 0.00044009
| 336.15 | 2300000 | 4179.3062 | 3953.4248 | 982.5994 | 0.00044655 | 63 | 22.6992 | 4.1793 | 3.9534 | 0.9826 | 0.00044655
| 335.15 | 2300000 | 4178.8149 | 3958.5071 | 983.1277 | 0.00045316 | 62 | 22.6992 | 4.1788 | 3.9585 | 0.98313 | 0.00045316
| 334.15 | 2300000 | 4178.3438 | 3963.5803 | 983.6502 | 0.00045994 | 61 | 22.6992 | 4.1783 | 3.9636 | 0.98365 | 0.00045994
| 333.15 | 2300000 | 4177.8931 | 3968.6438 | 984.1669 | 0.00046689 | 60 | 22.6992 | 4.1779 | 3.9686 | 0.98417 | 0.00046689
| 332.15 | 2300000 | 4177.4619 | 3973.6965 | 984.6777 | 0.00047402 | 59 | 22.6992 | 4.1775 | 3.9737 | 0.98468 | 0.00047402
| 331.15 | 2300000 | 4177.0518 | 3978.7375 | 985.1826 | 0.00048133 | 58 | 22.6992 | 4.1771 | 3.9787 | 0.98518 | 0.00048133
| 330.15 | 2300000 | 4176.6611 | 3983.7659 | 985.6816 | 0.00048883 | 57 | 22.6992 | 4.1767 | 3.9838 | 0.98568 | 0.00048883
| 329.15 | 2300000 | 4176.291 | 3988.781 | 986.1745 | 0.00049653 | 56 | 22.6992 | 4.1763 | 3.9888 | 0.98617 | 0.00049653
| 328.15 | 2300000 | 4175.9409 | 3993.7812 | 986.6613 | 0.00050443 | 55 | 22.6992 | 4.1759 | 3.9938 | 0.98666 | 0.00050443
| 327.15 | 2300000 | 4175.6113 | 3998.7664 | 987.1419 | 0.00051254 | 54 | 22.6992 | 4.1756 | 3.9988 | 0.98714 | 0.00051254
| 326.15 | 2300000 | 4175.3022 | 4003.7346 | 987.6163 | 0.00052086 | 53 | 22.6992 | 4.1753 | 4.0037 | 0.98762 | 0.00052086
| 325.15 | 2300000 | 4175.0132 | 4008.6853 | 988.0845 | 0.00052942 | 52 | 22.6992 | 4.175 | 4.0087 | 0.98808 | 0.00052942
| 324.15 | 2300000 | 4174.7446 | 4013.6172 | 988.5463 | 0.0005382 | 51 | 22.6992 | 4.1747 | 4.0136 | 0.98855 | 0.0005382
| 323.15 | 2300000 | 4174.4966 | 4018.5293 | 989.0016 | 0.00054723 | 50 | 22.6992 | 4.1745 | 4.0185 | 0.989 | 0.00054723
| 322.15 | 2300000 | 4174.269 | 4023.4202 | 989.4504 | 0.00055652 | 49 | 22.6992 | 4.1743 | 4.0234 | 0.98945 | 0.00055652
| 321.15 | 2300000 | 4174.0625 | 4028.2888 | 989.8927 | 0.00056606 | 48 | 22.6992 | 4.1741 | 4.0283 | 0.98989 | 0.00056606
| 320.15 | 2300000 | 4173.8765 | 4033.1338 | 990.3283 | 0.00057588 | 47 | 22.6992 | 4.1739 | 4.0331 | 0.99033 | 0.00057588
| 319.15 | 2300000 | 4173.7114 | 4037.9541 | 990.7571 | 0.00058597 | 46 | 22.6992 | 4.1737 | 4.038 | 0.99076 | 0.00058597
| 318.15 | 2300000 | 4173.5674 | 4042.748 | 991.1792 | 0.00059636 | 45 | 22.6992 | 4.1736 | 4.0427 | 0.99118 | 0.00059636
| 317.15 | 2300000 | 4173.4443 | 4047.5144 | 991.5944 | 0.00060706 | 44 | 22.6992 | 4.1734 | 4.0475 | 0.99159 | 0.00060706
| 316.15 | 2300000 | 4173.3428 | 4052.2522 | 992.0026 | 0.00061808 | 43 | 22.6992 | 4.1733 | 4.0523 | 0.992 | 0.00061808
| 315.15 | 2300000 | 4173.2627 | 4056.9592 | 992.4036 | 0.00062942 | 42 | 22.6992 | 4.1733 | 4.057 | 0.9924 | 0.00062942
| 314.15 | 2300000 | 4173.2041 | 4061.6348 | 992.7975 | 0.00064111 | 41 | 22.6992 | 4.1732 | 4.0616 | 0.9928 | 0.00064111
| 313.15 | 2300000 | 4173.1675 | 4066.2771 | 993.1842 | 0.00065316 | 40 | 22.6992 | 4.1732 | 4.0663 | 0.99318 | 0.00065316
| 312.15 | 2300000 | 4173.1533 | 4070.8845 | 993.5635 | 0.00066558 | 39 | 22.6992 | 4.1732 | 4.0709 | 0.99356 | 0.00066558
| 311.15 | 2300000 | 4173.1616 | 4075.4556 | 993.9353 | 0.00067839 | 38 | 22.6992 | 4.1732 | 4.0755 | 0.99394 | 0.00067839
| 310.15 | 2300000 | 4173.1934 | 4079.9888 | 994.2996 | 0.00069161 | 37 | 22.6992 | 4.1732 | 4.08 | 0.9943 | 0.00069161
| 309.15 | 2300000 | 4173.248 | 4084.4824 | 994.6561 | 0.00070525 | 36 | 22.6992 | 4.1732 | 4.0845 | 0.99466 | 0.00070525
| 308.15 | 2300000 | 4173.3267 | 4088.9351 | 995.0049 | 0.00071933 | 35 | 22.6992 | 4.1733 | 4.0889 | 0.995 | 0.00071933
| 307.15 | 2300000 | 4173.4297 | 4093.3447 | 995.3458 | 0.00073388 | 34 | 22.6992 | 4.1734 | 4.0933 | 0.99535 | 0.00073388
| 306.15 | 2300000 | 4173.5581 | 4097.71 | 995.6786 | 0.00074891 | 33 | 22.6992 | 4.1736 | 4.0977 | 0.99568 | 0.00074891
| 305.15 | 2300000 | 4173.7119 | 4102.0293 | 996.0033 | 0.00076445 | 32 | 22.6992 | 4.1737 | 4.102 | 0.996 | 0.00076445
| 304.15 | 2300000 | 4173.8926 | 4106.3008 | 996.3196 | 0.00078052 | 31 | 22.6992 | 4.1739 | 4.1063 | 0.99632 | 0.00078052
| 303.15 | 2300000 | 4174.1011 | 4110.5225 | 996.6276 | 0.00079714 | 30 | 22.6992 | 4.1741 | 4.1105 | 0.99663 | 0.00079714
| 302.15 | 2300000 | 4174.3374 | 4114.6929 | 996.9269 | 0.00081435 | 29 | 22.6992 | 4.1743 | 4.1147 | 0.99693 | 0.00081435
| 301.15 | 2300000 | 4174.604 | 4118.8101 | 997.2177 | 0.00083216 | 28 | 22.6992 | 4.1746 | 4.1188 | 0.99722 | 0.00083216
| 300.15 | 2300000 | 4174.9014 | 4122.873 | 997.4995 | 0.00085062 | 27 | 22.6992 | 4.1749 | 4.1229 | 0.9975 | 0.00085062
| 299.15 | 2300000 | 4175.2314 | 4126.8789 | 997.7722 | 0.00086974 | 26 | 22.6992 | 4.1752 | 4.1269 | 0.99777 | 0.00086974
| 298.15 | 2300000 | 4175.5962 | 4130.8267 | 998.0358 | 0.00088958 | 25 | 22.6992 | 4.1756 | 4.1308 | 0.99804 | 0.00088958
| 297.15 | 2300000 | 4175.9966 | 4134.7144 | 998.29 | 0.00091015 | 24 | 22.6992 | 4.176 | 4.1347 | 0.99829 | 0.00091015
| 296.15 | 2300000 | 4176.4351 | 4138.541 | 998.5347 | 0.00093151 | 23 | 22.6992 | 4.1764 | 4.1385 | 0.99853 | 0.00093151
| 295.15 | 2300000 | 4176.9146 | 4142.3037 | 998.7697 | 0.00095368 | 22 | 22.6992 | 4.1769 | 4.1423 | 0.99877 | 0.00095368
| 294.15 | 2300000 | 4177.437 | 4146.0015 | 998.9947 | 0.00097672 | 21 | 22.6992 | 4.1774 | 4.146 | 0.99899 | 0.00097672
| 293.15 | 2300000 | 4178.0054 | 4149.6328 | 999.2096 | 0.0010007 | 20 | 22.6992 | 4.178 | 4.1496 | 0.99921 | 0.0010007
| 292.15 | 2300000 | 4178.6235 | 4153.1963 | 999.4142 | 0.0010256 | 19 | 22.6992 | 4.1786 | 4.1532 | 0.99941 | 0.0010256
| 291.15 | 2300000 | 4179.2949 | 4156.6899 | 999.6082 | 0.0010515 | 18 | 22.6992 | 4.1793 | 4.1567 | 0.99961 | 0.0010515
| 290.15 | 2300000 | 4180.0239 | 4160.1128 | 999.7914 | 0.0010785 | 17 | 22.6992 | 4.18 | 4.1601 | 0.99979 | 0.0010785
| 289.15 | 2300000 | 4180.8145 | 4163.4634 | 999.9636 | 0.0011067 | 16 | 22.6992 | 4.1808 | 4.1635 | 0.99996 | 0.0011067
| 288.15 | 2300000 | 4181.6724 | 4166.7402 | 1000.1245 | 0.001136 | 15 | 22.6992 | 4.1817 | 4.1667 | 1.0001 | 0.001136
| 287.15 | 2300000 | 4182.603 | 4169.9424 | 1000.2738 | 0.0011666 | 14 | 22.6992 | 4.1826 | 4.1699 | 1.0003 | 0.0011666
| 286.15 | 2300000 | 4183.6128 | 4173.0693 | 1000.4113 | 0.0011986 | 13 | 22.6992 | 4.1836 | 4.1731 | 1.0004 | 0.0011986
| 285.15 | 2300000 | 4184.709 | 4176.1191 | 1000.5366 | 0.001232 | 12 | 22.6992 | 4.1847 | 4.1761 | 1.0005 | 0.001232
| 284.15 | 2300000 | 4185.8994 | 4179.0918 | 1000.6495 | 0.001267 | 11 | 22.6992 | 4.1859 | 4.1791 | 1.0006 | 0.001267
| 283.15 | 2300000 | 4187.1929 | 4181.9868 | 1000.7495 | 0.0013035 | 10 | 22.6992 | 4.1872 | 4.182 | 1.0007 | 0.0013035
| 282.15 | 2300000 | 4188.5991 | 4184.8032 | 1000.8365 | 0.0013418 | 9 | 22.6992 | 4.1886 | 4.1848 | 1.0008 | 0.0013418
| 281.15 | 2300000 | 4190.1284 | 4187.541 | 1000.9099 | 0.0013819 | 8 | 22.6992 | 4.1901 | 4.1875 | 1.0009 | 0.0013819
| 280.15 | 2300000 | 4191.7939 | 4190.2007 | 1000.9695 | 0.001424 | 7 | 22.6992 | 4.1918 | 4.1902 | 1.001 | 0.001424
| 279.15 | 2300000 | 4193.6079 | 4192.7817 | 1001.0148 | 0.0014681 | 6 | 22.6992 | 4.1936 | 4.1928 | 1.001 | 0.0014681
| 278.15 | 2300000 | 4195.5854 | 4195.2847 | 1001.0453 | 0.0015145 | 5 | 22.6992 | 4.1956 | 4.1953 | 1.001 | 0.0015145
| 277.15 | 2300000 | 4197.7427 | 4197.7104 | 1001.0607 | 0.0015633 | 4 | 22.6992 | 4.1977 | 4.1977 | 1.0011 | 0.0015633
| 276.15 | 2300000 | 4200.0981 | 4200.0596 | 1001.0603 | 0.0016147 | 3 | 22.6992 | 4.2001 | 4.2001 | 1.0011 | 0.0016147
| 275.15 | 2300000 | 4202.6719 | 4202.334 | 1001.0438 | 0.0016688 | 2 | 22.6992 | 4.2027 | 4.2023 | 1.001 | 0.0016688
| 274.15 | 2300000 | 4205.4858 | 4204.5347 | 1001.0106 | 0.0017258 | 0.99999 | 22.6992 | 4.2055 | 4.2045 | 1.001 | 0.0017258
| 273.15 | 2300000 | 4208.5645 | 4206.6631 | 1000.96 | 0.0017861 | -6.1035e-06 | 22.6992 | 4.2086 | 4.2067 | 1.001 | 0.0017861
| 473.15 | 2200000 | 4490.2354 | 3316.5083 | 865.1596 | 0.00013448 | 200 | 21.7122 | 4.4902 | 3.3165 | 0.86516 | 0.00013448
| 472.15 | 2200000 | 4485.0825 | 3320.2888 | 866.3453 | 0.0001352 | 199 | 21.7122 | 4.4851 | 3.3203 | 0.86635 | 0.0001352
| 471.15 | 2200000 | 4480.0059 | 3324.0872 | 867.5251 | 0.00013593 | 198 | 21.7122 | 4.48 | 3.3241 | 0.86753 | 0.00013593
| 470.15 | 2200000 | 4475.0039 | 3327.9028 | 868.699 | 0.00013666 | 197 | 21.7122 | 4.475 | 3.3279 | 0.8687 | 0.00013666
| 469.15 | 2200000 | 4470.0747 | 3331.7361 | 869.8671 | 0.0001374 | 196 | 21.7122 | 4.4701 | 3.3317 | 0.86987 | 0.0001374
| 468.15 | 2200000 | 4465.2178 | 3335.5864 | 871.0295 | 0.00013815 | 195 | 21.7122 | 4.4652 | 3.3356 | 0.87103 | 0.00013815
| 467.15 | 2200000 | 4460.4312 | 3339.4539 | 872.1862 | 0.00013891 | 194 | 21.7122 | 4.4604 | 3.3395 | 0.87219 | 0.00013891
| 466.15 | 2200000 | 4455.7139 | 3343.3384 | 873.3372 | 0.00013967 | 193 | 21.7122 | 4.4557 | 3.3433 | 0.87334 | 0.00013967
| 465.15 | 2200000 | 4451.0649 | 3347.2397 | 874.4826 | 0.00014045 | 192 | 21.7122 | 4.4511 | 3.3472 | 0.87448 | 0.00014045
| 464.15 | 2200000 | 4446.4829 | 3351.158 | 875.6225 | 0.00014123 | 191 | 21.7122 | 4.4465 | 3.3512 | 0.87562 | 0.00014123
| 463.15 | 2200000 | 4441.9668 | 3355.0928 | 876.7568 | 0.00014202 | 190 | 21.7122 | 4.442 | 3.3551 | 0.87676 | 0.00014202
| 462.15 | 2200000 | 4437.5151 | 3359.0439 | 877.8857 | 0.00014282 | 189 | 21.7122 | 4.4375 | 3.359 | 0.87789 | 0.00014282
| 461.15 | 2200000 | 4433.127 | 3363.0117 | 879.009 | 0.00014363 | 188 | 21.7122 | 4.4331 | 3.363 | 0.87901 | 0.00014363
| 460.15 | 2200000 | 4428.8018 | 3366.9956 | 880.1271 | 0.00014445 | 187 | 21.7122 | 4.4288 | 3.367 | 0.88013 | 0.00014445
| 459.15 | 2200000 | 4424.5376 | 3370.9958 | 881.2397 | 0.00014527 | 186 | 21.7122 | 4.4245 | 3.371 | 0.88124 | 0.00014527
| 458.15 | 2200000 | 4420.334 | 3375.0122 | 882.347 | 0.00014611 | 185 | 21.7122 | 4.4203 | 3.375 | 0.88235 | 0.00014611
| 457.15 | 2200000 | 4416.1899 | 3379.0442 | 883.4491 | 0.00014695 | 184 | 21.7122 | 4.4162 | 3.379 | 0.88345 | 0.00014695
| 456.15 | 2200000 | 4412.1045 | 3383.0923 | 884.5458 | 0.00014781 | 183 | 21.7122 | 4.4121 | 3.3831 | 0.88455 | 0.00014781
| 455.15 | 2200000 | 4408.0762 | 3387.156 | 885.6374 | 0.00014867 | 182 | 21.7122 | 4.4081 | 3.3872 | 0.88564 | 0.00014867
| 454.15 | 2200000 | 4404.1045 | 3391.2354 | 886.7238 | 0.00014955 | 181 | 21.7122 | 4.4041 | 3.3912 | 0.88672 | 0.00014955
| 453.15 | 2200000 | 4400.1885 | 3395.3301 | 887.8051 | 0.00015044 | 180 | 21.7122 | 4.4002 | 3.3953 | 0.88781 | 0.00015044
| 452.15 | 2200000 | 4396.3271 | 3399.4404 | 888.8812 | 0.00015133 | 179 | 21.7122 | 4.3963 | 3.3994 | 0.88888 | 0.00015133
| 451.15 | 2200000 | 4392.52 | 3403.5659 | 889.9522 | 0.00015224 | 178 | 21.7122 | 4.3925 | 3.4036 | 0.88995 | 0.00015224
| 450.15 | 2200000 | 4388.7656 | 3407.7065 | 891.0182 | 0.00015316 | 177 | 21.7122 | 4.3888 | 3.4077 | 0.89102 | 0.00015316
| 449.15 | 2200000 | 4385.063 | 3411.8621 | 892.0792 | 0.00015409 | 176 | 21.7122 | 4.3851 | 3.4119 | 0.89208 | 0.00015409
| 448.15 | 2200000 | 4381.4121 | 3416.0327 | 893.1351 | 0.00015503 | 175 | 21.7122 | 4.3814 | 3.416 | 0.89314 | 0.00015503
| 447.15 | 2200000 | 4377.8115 | 3420.218 | 894.1861 | 0.00015598 | 174 | 21.7122 | 4.3778 | 3.4202 | 0.89419 | 0.00015598
| 446.15 | 2200000 | 4374.2607 | 3424.4182 | 895.2322 | 0.00015694 | 173 | 21.7122 | 4.3743 | 3.4244 | 0.89523 | 0.00015694
| 445.15 | 2200000 | 4370.7588 | 3428.6331 | 896.2734 | 0.00015792 | 172 | 21.7122 | 4.3708 | 3.4286 | 0.89627 | 0.00015792
| 444.15 | 2200000 | 4367.3052 | 3432.8623 | 897.3096 | 0.0001589 | 171 | 21.7122 | 4.3673 | 3.4329 | 0.89731 | 0.0001589
| 443.15 | 2200000 | 4363.8989 | 3437.106 | 898.3411 | 0.0001599 | 170 | 21.7122 | 4.3639 | 3.4371 | 0.89834 | 0.0001599
| 442.15 | 2200000 | 4360.5391 | 3441.364 | 899.3677 | 0.00016092 | 169 | 21.7122 | 4.3605 | 3.4414 | 0.89937 | 0.00016092
| 441.15 | 2200000 | 4357.2256 | 3445.6362 | 900.3895 | 0.00016194 | 168 | 21.7122 | 4.3572 | 3.4456 | 0.90039 | 0.00016194
| 440.15 | 2200000 | 4353.957 | 3449.9226 | 901.4064 | 0.00016298 | 167 | 21.7122 | 4.354 | 3.4499 | 0.90141 | 0.00016298
| 439.15 | 2200000 | 4350.7334 | 3454.2229 | 902.4187 | 0.00016403 | 166 | 21.7122 | 4.3507 | 3.4542 | 0.90242 | 0.00016403
| 438.15 | 2200000 | 4347.5537 | 3458.5371 | 903.4262 | 0.0001651 | 165 | 21.7122 | 4.3476 | 3.4585 | 0.90343 | 0.0001651
| 437.15 | 2200000 | 4344.417 | 3462.865 | 904.429 | 0.00016618 | 164 | 21.7122 | 4.3444 | 3.4629 | 0.90443 | 0.00016618
| 436.15 | 2200000 | 4341.3228 | 3467.2068 | 905.4271 | 0.00016727 | 163 | 21.7122 | 4.3413 | 3.4672 | 0.90543 | 0.00016727
| 435.15 | 2200000 | 4338.271 | 3471.5623 | 906.4205 | 0.00016838 | 162 | 21.7122 | 4.3383 | 3.4716 | 0.90642 | 0.00016838
| 434.15 | 2200000 | 4335.2603 | 3475.9312 | 907.4092 | 0.0001695 | 161 | 21.7122 | 4.3353 | 3.4759 | 0.90741 | 0.0001695
| 433.15 | 2200000 | 4332.2905 | 3480.3132 | 908.3934 | 0.00017064 | 160 | 21.7122 | 4.3323 | 3.4803 | 0.90839 | 0.00017064
| 432.15 | 2200000 | 4329.3608 | 3484.709 | 909.3729 | 0.00017179 | 159 | 21.7122 | 4.3294 | 3.4847 | 0.90937 | 0.00017179
| 431.15 | 2200000 | 4326.4707 | 3489.1179 | 910.3478 | 0.00017296 | 158 | 21.7122 | 4.3265 | 3.4891 | 0.91035 | 0.00017296
| 430.15 | 2200000 | 4323.6191 | 3493.5398 | 911.3182 | 0.00017414 | 157 | 21.7122 | 4.3236 | 3.4935 | 0.91132 | 0.00017414
| 429.15 | 2200000 | 4320.8066 | 3497.9749 | 912.2839 | 0.00017534 | 156 | 21.7122 | 4.3208 | 3.498 | 0.91228 | 0.00017534
| 428.15 | 2200000 | 4318.0317 | 3502.4231 | 913.2451 | 0.00017656 | 155 | 21.7122 | 4.318 | 3.5024 | 0.91325 | 0.00017656
| 427.15 | 2200000 | 4315.2944 | 3506.884 | 914.2018 | 0.00017779 | 154 | 21.7122 | 4.3153 | 3.5069 | 0.9142 | 0.00017779
| 426.15 | 2200000 | 4312.5938 | 3511.3577 | 915.154 | 0.00017904 | 153 | 21.7122 | 4.3126 | 3.5114 | 0.91515 | 0.00017904
| 425.15 | 2200000 | 4309.9297 | 3515.8442 | 916.1016 | 0.00018031 | 152 | 21.7122 | 4.3099 | 3.5158 | 0.9161 | 0.00018031
| 424.15 | 2200000 | 4307.3013 | 3520.3433 | 917.0448 | 0.00018159 | 151 | 21.7122 | 4.3073 | 3.5203 | 0.91704 | 0.00018159
| 423.15 | 2200000 | 4304.708 | 3524.8547 | 917.9835 | 0.0001829 | 150 | 21.7122 | 4.3047 | 3.5249 | 0.91798 | 0.0001829
| 422.15 | 2200000 | 4302.1499 | 3529.3789 | 918.9177 | 0.00018422 | 149 | 21.7122 | 4.3021 | 3.5294 | 0.91892 | 0.00018422
| 421.15 | 2200000 | 4299.626 | 3533.9153 | 919.8475 | 0.00018556 | 148 | 21.7122 | 4.2996 | 3.5339 | 0.91985 | 0.00018556
| 420.15 | 2200000 | 4297.1362 | 3538.4641 | 920.7728 | 0.00018692 | 147 | 21.7122 | 4.2971 | 3.5385 | 0.92077 | 0.00018692
| 419.15 | 2200000 | 4294.6797 | 3543.0251 | 921.6937 | 0.0001883 | 146 | 21.7122 | 4.2947 | 3.543 | 0.92169 | 0.0001883
| 418.15 | 2200000 | 4292.2563 | 3547.5981 | 922.6102 | 0.0001897 | 145 | 21.7122 | 4.2923 | 3.5476 | 0.92261 | 0.0001897
| 417.15 | 2200000 | 4289.8657 | 3552.1833 | 923.5223 | 0.00019112 | 144 | 21.7122 | 4.2899 | 3.5522 | 0.92352 | 0.00019112
| 416.15 | 2200000 | 4287.5068 | 3556.7805 | 924.4299 | 0.00019256 | 143 | 21.7122 | 4.2875 | 3.5568 | 0.92443 | 0.00019256
| 415.15 | 2200000 | 4285.1797 | 3561.3896 | 925.3332 | 0.00019402 | 142 | 21.7122 | 4.2852 | 3.5614 | 0.92533 | 0.00019402
| 414.15 | 2200000 | 4282.8843 | 3566.0105 | 926.2321 | 0.00019551 | 141 | 21.7122 | 4.2829 | 3.566 | 0.92623 | 0.00019551
| 413.15 | 2200000 | 4280.6196 | 3570.6431 | 927.1266 | 0.00019701 | 140 | 21.7122 | 4.2806 | 3.5706 | 0.92713 | 0.00019701
| 412.15 | 2200000 | 4278.3853 | 3575.2874 | 928.0167 | 0.00019854 | 139 | 21.7122 | 4.2784 | 3.5753 | 0.92802 | 0.00019854
| 411.15 | 2200000 | 4276.1816 | 3579.9434 | 928.9025 | 0.00020009 | 138 | 21.7122 | 4.2762 | 3.5799 | 0.9289 | 0.00020009
| 410.15 | 2200000 | 4274.0073 | 3584.6106 | 929.7839 | 0.00020167 | 137 | 21.7122 | 4.274 | 3.5846 | 0.92978 | 0.00020167
| 409.15 | 2200000 | 4271.8628 | 3589.2896 | 930.6609 | 0.00020327 | 136 | 21.7122 | 4.2719 | 3.5893 | 0.93066 | 0.00020327
| 408.15 | 2200000 | 4269.7471 | 3593.9797 | 931.5336 | 0.00020489 | 135 | 21.7122 | 4.2697 | 3.594 | 0.93153 | 0.00020489
| 407.15 | 2200000 | 4267.6602 | 3598.6812 | 932.402 | 0.00020654 | 134 | 21.7122 | 4.2677 | 3.5987 | 0.9324 | 0.00020654
| 406.15 | 2200000 | 4265.6016 | 3603.3938 | 933.266 | 0.00020821 | 133 | 21.7122 | 4.2656 | 3.6034 | 0.93327 | 0.00020821
| 405.15 | 2200000 | 4263.5708 | 3608.1177 | 934.1257 | 0.00020991 | 132 | 21.7122 | 4.2636 | 3.6081 | 0.93413 | 0.00020991
| 404.15 | 2200000 | 4261.5684 | 3612.8525 | 934.981 | 0.00021164 | 131 | 21.7122 | 4.2616 | 3.6129 | 0.93498 | 0.00021164
| 403.15 | 2200000 | 4259.5933 | 3617.5981 | 935.832 | 0.00021339 | 130 | 21.7122 | 4.2596 | 3.6176 | 0.93583 | 0.00021339
| 402.15 | 2200000 | 4257.645 | 3622.355 | 936.6787 | 0.00021518 | 129 | 21.7122 | 4.2576 | 3.6224 | 0.93668 | 0.00021518
| 401.15 | 2200000 | 4255.7236 | 3627.1226 | 937.5211 | 0.00021699 | 128 | 21.7122 | 4.2557 | 3.6271 | 0.93752 | 0.00021699
| 400.15 | 2200000 | 4253.8286 | 3631.9009 | 938.3591 | 0.00021883 | 127 | 21.7122 | 4.2538 | 3.6319 | 0.93836 | 0.00021883
| 399.15 | 2200000 | 4251.96 | 3636.6897 | 939.1928 | 0.0002207 | 126 | 21.7122 | 4.252 | 3.6367 | 0.93919 | 0.0002207
| 398.15 | 2200000 | 4250.1177 | 3641.4893 | 940.0222 | 0.0002226 | 125 | 21.7122 | 4.2501 | 3.6415 | 0.94002 | 0.0002226
| 397.15 | 2200000 | 4248.3008 | 3646.2991 | 940.8472 | 0.00022453 | 124 | 21.7122 | 4.2483 | 3.6463 | 0.94085 | 0.00022453
| 396.15 | 2200000 | 4246.5093 | 3651.1196 | 941.6678 | 0.00022649 | 123 | 21.7122 | 4.2465 | 3.6511 | 0.94167 | 0.00022649
| 395.15 | 2200000 | 4244.7432 | 3655.9502 | 942.4842 | 0.00022849 | 122 | 21.7122 | 4.2447 | 3.656 | 0.94248 | 0.00022849
| 394.15 | 2200000 | 4243.002 | 3660.7913 | 943.2962 | 0.00023051 | 121 | 21.7122 | 4.243 | 3.6608 | 0.9433 | 0.00023051
| 393.15 | 2200000 | 4241.2852 | 3665.6423 | 944.1039 | 0.00023258 | 120 | 21.7122 | 4.2413 | 3.6656 | 0.9441 | 0.00023258
| 392.15 | 2200000 | 4239.5933 | 3670.5034 | 944.9072 | 0.00023467 | 119 | 21.7122 | 4.2396 | 3.6705 | 0.94491 | 0.00023467
| 391.15 | 2200000 | 4237.9253 | 3675.3745 | 945.7062 | 0.00023681 | 118 | 21.7122 | 4.2379 | 3.6754 | 0.94571 | 0.00023681
| 390.15 | 2200000 | 4236.2812 | 3680.2554 | 946.5008 | 0.00023898 | 117 | 21.7122 | 4.2363 | 3.6803 | 0.9465 | 0.00023898
| 389.15 | 2200000 | 4234.6616 | 3685.146 | 947.2911 | 0.00024118 | 116 | 21.7122 | 4.2347 | 3.6851 | 0.94729 | 0.00024118
| 388.15 | 2200000 | 4233.0649 | 3690.0464 | 948.077 | 0.00024342 | 115 | 21.7122 | 4.2331 | 3.69 | 0.94808 | 0.00024342
| 387.15 | 2200000 | 4231.4922 | 3694.9563 | 948.8585 | 0.00024571 | 114 | 21.7122 | 4.2315 | 3.695 | 0.94886 | 0.00024571
| 386.15 | 2200000 | 4229.9424 | 3699.8757 | 949.6356 | 0.00024803 | 113 | 21.7122 | 4.2299 | 3.6999 | 0.94964 | 0.00024803
| 385.15 | 2200000 | 4228.4155 | 3704.8042 | 950.4083 | 0.00025039 | 112 | 21.7122 | 4.2284 | 3.7048 | 0.95041 | 0.00025039
| 384.15 | 2200000 | 4226.9116 | 3709.7422 | 951.1767 | 0.0002528 | 111 | 21.7122 | 4.2269 | 3.7097 | 0.95118 | 0.0002528
| 383.15 | 2200000 | 4225.4307 | 3714.6892 | 951.9406 | 0.00025525 | 110 | 21.7122 | 4.2254 | 3.7147 | 0.95194 | 0.00025525
| 382.15 | 2200000 | 4223.9722 | 3719.645 | 952.7001 | 0.00025774 | 109 | 21.7122 | 4.224 | 3.7196 | 0.9527 | 0.00025774
| 381.15 | 2200000 | 4222.5356 | 3724.6099 | 953.4553 | 0.00026027 | 108 | 21.7122 | 4.2225 | 3.7246 | 0.95346 | 0.00026027
| 380.15 | 2200000 | 4221.1216 | 3729.5835 | 954.2059 | 0.00026285 | 107 | 21.7122 | 4.2211 | 3.7296 | 0.95421 | 0.00026285
| 379.15 | 2200000 | 4219.7295 | 3734.5657 | 954.9521 | 0.00026548 | 106 | 21.7122 | 4.2197 | 3.7346 | 0.95495 | 0.00026548
| 378.15 | 2200000 | 4218.3594 | 3739.5562 | 955.6938 | 0.00026816 | 105 | 21.7122 | 4.2184 | 3.7396 | 0.95569 | 0.00026816
| 377.15 | 2200000 | 4217.0112 | 3744.5549 | 956.4312 | 0.00027089 | 104 | 21.7122 | 4.217 | 3.7446 | 0.95643 | 0.00027089
| 376.15 | 2200000 | 4215.6846 | 3749.562 | 957.1639 | 0.00027366 | 103 | 21.7122 | 4.2157 | 3.7496 | 0.95716 | 0.00027366
| 375.15 | 2200000 | 4214.3794 | 3754.5769 | 957.8922 | 0.00027649 | 102 | 21.7122 | 4.2144 | 3.7546 | 0.95789 | 0.00027649
| 374.15 | 2200000 | 4213.0957 | 3759.5999 | 958.616 | 0.00027937 | 101 | 21.7122 | 4.2131 | 3.7596 | 0.95862 | 0.00027937
| 373.15 | 2200000 | 4211.8335 | 3764.6301 | 959.3352 | 0.00028231 | 100 | 21.7122 | 4.2118 | 3.7646 | 0.95934 | 0.00028231
| 372.15 | 2200000 | 4210.5923 | 3769.668 | 960.0499 | 0.0002853 | 99 | 21.7122 | 4.2106 | 3.7697 | 0.96005 | 0.0002853
| 371.15 | 2200000 | 4209.3726 | 3774.7131 | 960.76 | 0.00028835 | 98 | 21.7122 | 4.2094 | 3.7747 | 0.96076 | 0.00028835
| 370.15 | 2200000 | 4208.1733 | 3779.7656 | 961.4656 | 0.00029145 | 97 | 21.7122 | 4.2082 | 3.7798 | 0.96147 | 0.00029145
| 369.15 | 2200000 | 4206.9951 | 3784.8247 | 962.1665 | 0.00029462 | 96 | 21.7122 | 4.207 | 3.7848 | 0.96217 | 0.00029462
| 368.15 | 2200000 | 4205.8379 | 3789.8904 | 962.8628 | 0.00029785 | 95 | 21.7122 | 4.2058 | 3.7899 | 0.96286 | 0.00029785
| 367.15 | 2200000 | 4204.7012 | 3794.9626 | 963.5545 | 0.00030114 | 94 | 21.7122 | 4.2047 | 3.795 | 0.96355 | 0.00030114
| 366.15 | 2200000 | 4203.5854 | 3800.0413 | 964.2416 | 0.0003045 | 93 | 21.7122 | 4.2036 | 3.8 | 0.96424 | 0.0003045
| 365.15 | 2200000 | 4202.4902 | 3805.1257 | 964.9239 | 0.00030792 | 92 | 21.7122 | 4.2025 | 3.8051 | 0.96492 | 0.00030792
| 364.15 | 2200000 | 4201.4155 | 3810.2158 | 965.6016 | 0.00031141 | 91 | 21.7122 | 4.2014 | 3.8102 | 0.9656 | 0.00031141
| 363.15 | 2200000 | 4200.3613 | 3815.3115 | 966.2745 | 0.00031497 | 90 | 21.7122 | 4.2004 | 3.8153 | 0.96627 | 0.00031497
| 362.15 | 2200000 | 4199.3276 | 3820.4124 | 966.9427 | 0.00031861 | 89 | 21.7122 | 4.1993 | 3.8204 | 0.96694 | 0.00031861
| 361.15 | 2200000 | 4198.3145 | 3825.5183 | 967.6061 | 0.00032231 | 88 | 21.7122 | 4.1983 | 3.8255 | 0.96761 | 0.00032231
| 360.15 | 2200000 | 4197.3213 | 3830.6287 | 968.2648 | 0.0003261 | 87 | 21.7122 | 4.1973 | 3.8306 | 0.96826 | 0.0003261
| 359.15 | 2200000 | 4196.3486 | 3835.7434 | 968.9186 | 0.00032996 | 86 | 21.7122 | 4.1963 | 3.8357 | 0.96892 | 0.00032996
| 358.15 | 2200000 | 4195.396 | 3840.8623 | 969.5676 | 0.0003339 | 85 | 21.7122 | 4.1954 | 3.8409 | 0.96957 | 0.0003339
| 357.15 | 2200000 | 4194.4639 | 3845.9846 | 970.2117 | 0.00033793 | 84 | 21.7122 | 4.1945 | 3.846 | 0.97021 | 0.00033793
| 356.15 | 2200000 | 4193.5518 | 3851.1106 | 970.8509 | 0.00034204 | 83 | 21.7122 | 4.1936 | 3.8511 | 0.97085 | 0.00034204
| 355.15 | 2200000 | 4192.6597 | 3856.2393 | 971.4852 | 0.00034624 | 82 | 21.7122 | 4.1927 | 3.8562 | 0.97149 | 0.00034624
| 354.15 | 2200000 | 4191.7876 | 3861.3706 | 972.1145 | 0.00035052 | 81 | 21.7122 | 4.1918 | 3.8614 | 0.97211 | 0.00035052
| 353.15 | 2200000 | 4190.936 | 3866.5042 | 972.7389 | 0.0003549 | 80 | 21.7122 | 4.1909 | 3.8665 | 0.97274 | 0.0003549
| 352.15 | 2200000 | 4190.1045 | 3871.6394 | 973.3582 | 0.00035938 | 79 | 21.7122 | 4.1901 | 3.8716 | 0.97336 | 0.00035938
| 351.15 | 2200000 | 4189.293 | 3876.7761 | 973.9725 | 0.00036395 | 78 | 21.7122 | 4.1893 | 3.8768 | 0.97397 | 0.00036395
| 350.15 | 2200000 | 4188.501 | 3881.9138 | 974.5817 | 0.00036863 | 77 | 21.7122 | 4.1885 | 3.8819 | 0.97458 | 0.00036863
| 349.15 | 2200000 | 4187.73 | 3887.0518 | 975.1857 | 0.0003734 | 76 | 21.7122 | 4.1877 | 3.8871 | 0.97519 | 0.0003734
| 348.15 | 2200000 | 4186.9785 | 3892.1899 | 975.7847 | 0.00037829 | 75 | 21.7122 | 4.187 | 3.8922 | 0.97578 | 0.00037829
| 347.15 | 2200000 | 4186.2471 | 3897.3274 | 976.3784 | 0.00038328 | 74 | 21.7122 | 4.1862 | 3.8973 | 0.97638 | 0.00038328
| 346.15 | 2200000 | 4185.5356 | 3902.4641 | 976.967 | 0.00038839 | 73 | 21.7122 | 4.1855 | 3.9025 | 0.97697 | 0.00038839
| 345.15 | 2200000 | 4184.8442 | 3907.5989 | 977.5502 | 0.00039361 | 72 | 21.7122 | 4.1848 | 3.9076 | 0.97755 | 0.00039361
| 344.15 | 2200000 | 4184.1729 | 3912.7319 | 978.1282 | 0.00039896 | 71 | 21.7122 | 4.1842 | 3.9127 | 0.97813 | 0.00039896
| 343.15 | 2200000 | 4183.5215 | 3917.8621 | 978.7008 | 0.00040442 | 70 | 21.7122 | 4.1835 | 3.9179 | 0.9787 | 0.00040442
| 342.15 | 2200000 | 4182.8906 | 3922.9888 | 979.268 | 0.00041002 | 69 | 21.7122 | 4.1829 | 3.923 | 0.97927 | 0.00041002
| 341.15 | 2200000 | 4182.2793 | 3928.1116 | 979.8298 | 0.00041575 | 68 | 21.7122 | 4.1823 | 3.9281 | 0.97983 | 0.00041575
| 340.15 | 2200000 | 4181.688 | 3933.23 | 980.3862 | 0.00042161 | 67 | 21.7122 | 4.1817 | 3.9332 | 0.98039 | 0.00042161
| 339.15 | 2200000 | 4181.1172 | 3938.343 | 980.937 | 0.00042762 | 66 | 21.7122 | 4.1811 | 3.9383 | 0.98094 | 0.00042762
| 338.15 | 2200000 | 4180.5664 | 3943.4502 | 981.4822 | 0.00043377 | 65 | 21.7122 | 4.1806 | 3.9435 | 0.98148 | 0.00043377
| 337.15 | 2200000 | 4180.0352 | 3948.5505 | 982.0219 | 0.00044007 | 64 | 21.7122 | 4.18 | 3.9486 | 0.98202 | 0.00044007
| 336.15 | 2200000 | 4179.5244 | 3953.6436 | 982.5559 | 0.00044652 | 63 | 21.7122 | 4.1795 | 3.9536 | 0.98256 | 0.00044652
| 335.15 | 2200000 | 4179.0337 | 3958.7283 | 983.0842 | 0.00045314 | 62 | 21.7122 | 4.179 | 3.9587 | 0.98308 | 0.00045314
| 334.15 | 2200000 | 4178.5635 | 3963.804 | 983.6068 | 0.00045992 | 61 | 21.7122 | 4.1786 | 3.9638 | 0.98361 | 0.00045992
| 333.15 | 2200000 | 4178.1133 | 3968.8699 | 984.1235 | 0.00046687 | 60 | 21.7122 | 4.1781 | 3.9689 | 0.98412 | 0.00046687
| 332.15 | 2200000 | 4177.6831 | 3973.925 | 984.6343 | 0.000474 | 59 | 21.7122 | 4.1777 | 3.9739 | 0.98463 | 0.000474
| 331.15 | 2200000 | 4177.2729 | 3978.9685 | 985.1393 | 0.00048131 | 58 | 21.7122 | 4.1773 | 3.979 | 0.98514 | 0.00048131
| 330.15 | 2200000 | 4176.8833 | 3983.9995 | 985.6382 | 0.00048881 | 57 | 21.7122 | 4.1769 | 3.984 | 0.98564 | 0.00048881
| 329.15 | 2200000 | 4176.5137 | 3989.0171 | 986.1312 | 0.00049651 | 56 | 21.7122 | 4.1765 | 3.989 | 0.98613 | 0.00049651
| 328.15 | 2200000 | 4176.1646 | 3994.0203 | 986.618 | 0.00050441 | 55 | 21.7122 | 4.1762 | 3.994 | 0.98662 | 0.00050441
| 327.15 | 2200000 | 4175.8359 | 3999.0078 | 987.0986 | 0.00051252 | 54 | 21.7122 | 4.1758 | 3.999 | 0.9871 | 0.00051252
| 326.15 | 2200000 | 4175.5273 | 4003.9788 | 987.5731 | 0.00052085 | 53 | 21.7122 | 4.1755 | 4.004 | 0.98757 | 0.00052085
| 325.15 | 2200000 | 4175.2397 | 4008.9321 | 988.0412 | 0.0005294 | 52 | 21.7122 | 4.1752 | 4.0089 | 0.98804 | 0.0005294
| 324.15 | 2200000 | 4174.9722 | 4013.8669 | 988.5029 | 0.00053819 | 51 | 21.7122 | 4.175 | 4.0139 | 0.9885 | 0.00053819
| 323.15 | 2200000 | 4174.7251 | 4018.7817 | 988.9583 | 0.00054722 | 50 | 21.7122 | 4.1747 | 4.0188 | 0.98896 | 0.00054722
| 322.15 | 2200000 | 4174.499 | 4023.6753 | 989.4071 | 0.0005565 | 49 | 21.7122 | 4.1745 | 4.0237 | 0.98941 | 0.0005565
| 321.15 | 2200000 | 4174.2935 | 4028.5469 | 989.8494 | 0.00056604 | 48 | 21.7122 | 4.1743 | 4.0285 | 0.98985 | 0.00056604
| 320.15 | 2200000 | 4174.1089 | 4033.3948 | 990.285 | 0.00057586 | 47 | 21.7122 | 4.1741 | 4.0334 | 0.99028 | 0.00057586
| 319.15 | 2200000 | 4173.9448 | 4038.2178 | 990.7138 | 0.00058596 | 46 | 21.7122 | 4.1739 | 4.0382 | 0.99071 | 0.00058596
| 318.15 | 2200000 | 4173.8022 | 4043.0146 | 991.1358 | 0.00059635 | 45 | 21.7122 | 4.1738 | 4.043 | 0.99114 | 0.00059635
| 317.15 | 2200000 | 4173.6807 | 4047.7842 | 991.551 | 0.00060705 | 44 | 21.7122 | 4.1737 | 4.0478 | 0.99155 | 0.00060705
| 316.15 | 2200000 | 4173.5806 | 4052.5247 | 991.9591 | 0.00061806 | 43 | 21.7122 | 4.1736 | 4.0525 | 0.99196 | 0.00061806
| 315.15 | 2200000 | 4173.5024 | 4057.2349 | 992.3602 | 0.00062941 | 42 | 21.7122 | 4.1735 | 4.0572 | 0.99236 | 0.00062941
| 314.15 | 2200000 | 4173.4453 | 4061.9133 | 992.754 | 0.0006411 | 41 | 21.7122 | 4.1734 | 4.0619 | 0.99275 | 0.0006411
| 313.15 | 2200000 | 4173.4111 | 4066.5586 | 993.1406 | 0.00065315 | 40 | 21.7122 | 4.1734 | 4.0666 | 0.99314 | 0.00065315
| 312.15 | 2200000 | 4173.3984 | 4071.1692 | 993.5199 | 0.00066557 | 39 | 21.7122 | 4.1734 | 4.0712 | 0.99352 | 0.00066557
| 311.15 | 2200000 | 4173.4092 | 4075.7434 | 993.8917 | 0.00067838 | 38 | 21.7122 | 4.1734 | 4.0757 | 0.99389 | 0.00067838
| 310.15 | 2200000 | 4173.4424 | 4080.2798 | 994.2559 | 0.0006916 | 37 | 21.7122 | 4.1734 | 4.0803 | 0.99426 | 0.0006916
| 309.15 | 2200000 | 4173.4995 | 4084.7769 | 994.6124 | 0.00070524 | 36 | 21.7122 | 4.1735 | 4.0848 | 0.99461 | 0.00070524
| 308.15 | 2200000 | 4173.5806 | 4089.2327 | 994.9611 | 0.00071933 | 35 | 21.7122 | 4.1736 | 4.0892 | 0.99496 | 0.00071933
| 307.15 | 2200000 | 4173.686 | 4093.6458 | 995.3018 | 0.00073388 | 34 | 21.7122 | 4.1737 | 4.0936 | 0.9953 | 0.00073388
| 306.15 | 2200000 | 4173.8169 | 4098.0142 | 995.6346 | 0.00074891 | 33 | 21.7122 | 4.1738 | 4.098 | 0.99563 | 0.00074891
| 305.15 | 2200000 | 4173.9736 | 4102.3369 | 995.9592 | 0.00076446 | 32 | 21.7122 | 4.174 | 4.1023 | 0.99596 | 0.00076446
| 304.15 | 2200000 | 4174.1567 | 4106.6118 | 996.2755 | 0.00078053 | 31 | 21.7122 | 4.1742 | 4.1066 | 0.99628 | 0.00078053
| 303.15 | 2200000 | 4174.3682 | 4110.8369 | 996.5833 | 0.00079715 | 30 | 21.7122 | 4.1744 | 4.1108 | 0.99658 | 0.00079715
| 302.15 | 2200000 | 4174.6079 | 4115.0107 | 996.8826 | 0.00081436 | 29 | 21.7122 | 4.1746 | 4.115 | 0.99688 | 0.00081436
| 301.15 | 2200000 | 4174.8774 | 4119.1318 | 997.1732 | 0.00083218 | 28 | 21.7122 | 4.1749 | 4.1191 | 0.99717 | 0.00083218
| 300.15 | 2200000 | 4175.1787 | 4123.1982 | 997.4548 | 0.00085063 | 27 | 21.7122 | 4.1752 | 4.1232 | 0.99745 | 0.00085063
| 299.15 | 2200000 | 4175.5122 | 4127.208 | 997.7275 | 0.00086976 | 26 | 21.7122 | 4.1755 | 4.1272 | 0.99773 | 0.00086976
| 298.15 | 2200000 | 4175.8804 | 4131.1597 | 997.991 | 0.0008896 | 25 | 21.7122 | 4.1759 | 4.1312 | 0.99799 | 0.0008896
| 297.15 | 2200000 | 4176.2847 | 4135.0513 | 998.2451 | 0.00091018 | 24 | 21.7122 | 4.1763 | 4.1351 | 0.99825 | 0.00091018
| 296.15 | 2200000 | 4176.7275 | 4138.8813 | 998.4896 | 0.00093154 | 23 | 21.7122 | 4.1767 | 4.1389 | 0.99849 | 0.00093154
| 295.15 | 2200000 | 4177.2109 | 4142.6479 | 998.7244 | 0.00095372 | 22 | 21.7122 | 4.1772 | 4.1426 | 0.99872 | 0.00095372
| 294.15 | 2200000 | 4177.7383 | 4146.3501 | 998.9493 | 0.00097676 | 21 | 21.7122 | 4.1777 | 4.1464 | 0.99895 | 0.00097676
| 293.15 | 2200000 | 4178.3115 | 4149.9858 | 999.1641 | 0.0010007 | 20 | 21.7122 | 4.1783 | 4.15 | 0.99916 | 0.0010007
| 292.15 | 2200000 | 4178.9351 | 4153.5532 | 999.3685 | 0.0010256 | 19 | 21.7122 | 4.1789 | 4.1536 | 0.99937 | 0.0010256
| 291.15 | 2200000 | 4179.6118 | 4157.0513 | 999.5623 | 0.0010516 | 18 | 21.7122 | 4.1796 | 4.1571 | 0.99956 | 0.0010516
| 290.15 | 2200000 | 4180.3462 | 4160.4785 | 999.7454 | 0.0010786 | 17 | 21.7122 | 4.1803 | 4.1605 | 0.99975 | 0.0010786
| 289.15 | 2200000 | 4181.1426 | 4163.8335 | 999.9173 | 0.0011067 | 16 | 21.7122 | 4.1811 | 4.1638 | 0.99992 | 0.0011067
| 288.15 | 2200000 | 4182.0068 | 4167.1152 | 1000.078 | 0.0011361 | 15 | 21.7122 | 4.182 | 4.1671 | 1.0001 | 0.0011361
| 287.15 | 2200000 | 4182.9443 | 4170.3223 | 1000.2271 | 0.0011667 | 14 | 21.7122 | 4.1829 | 4.1703 | 1.0002 | 0.0011667
| 286.15 | 2200000 | 4183.9609 | 4173.4536 | 1000.3644 | 0.0011987 | 13 | 21.7122 | 4.184 | 4.1735 | 1.0004 | 0.0011987
| 285.15 | 2200000 | 4185.0649 | 4176.5088 | 1000.4895 | 0.0012321 | 12 | 21.7122 | 4.1851 | 4.1765 | 1.0005 | 0.0012321
| 284.15 | 2200000 | 4186.2632 | 4179.4863 | 1000.6021 | 0.0012671 | 11 | 21.7122 | 4.1863 | 4.1795 | 1.0006 | 0.0012671
| 283.15 | 2200000 | 4187.5649 | 4182.3867 | 1000.702 | 0.0013036 | 10 | 21.7122 | 4.1876 | 4.1824 | 1.0007 | 0.0013036
| 282.15 | 2200000 | 4188.9795 | 4185.2085 | 1000.7887 | 0.0013419 | 9 | 21.7122 | 4.189 | 4.1852 | 1.0008 | 0.0013419
| 281.15 | 2200000 | 4190.5186 | 4187.9526 | 1000.8619 | 0.001382 | 8 | 21.7122 | 4.1905 | 4.188 | 1.0009 | 0.001382
| 280.15 | 2200000 | 4192.1938 | 4190.6177 | 1000.9211 | 0.0014241 | 7 | 21.7122 | 4.1922 | 4.1906 | 1.0009 | 0.0014241
| 279.15 | 2200000 | 4194.0181 | 4193.2051 | 1000.9661 | 0.0014683 | 6 | 21.7122 | 4.194 | 4.1932 | 1.001 | 0.0014683
| 278.15 | 2200000 | 4196.0068 | 4195.7144 | 1000.9964 | 0.0015147 | 5 | 21.7122 | 4.196 | 4.1957 | 1.001 | 0.0015147
| 277.15 | 2200000 | 4198.1763 | 4198.1465 | 1001.0114 | 0.0015635 | 4 | 21.7122 | 4.1982 | 4.1981 | 1.001 | 0.0015635
| 276.15 | 2200000 | 4200.5444 | 4200.5029 | 1001.0107 | 0.0016148 | 3 | 21.7122 | 4.2005 | 4.2005 | 1.001 | 0.0016148
| 275.15 | 2200000 | 4203.1318 | 4202.7842 | 1000.9939 | 0.001669 | 2 | 21.7122 | 4.2031 | 4.2028 | 1.001 | 0.001669
| 274.15 | 2200000 | 4205.96 | 4204.9922 | 1000.9603 | 0.001726 | 0.99999 | 21.7122 | 4.206 | 4.205 | 1.001 | 0.001726
| 273.15 | 2200000 | 4209.0537 | 4207.1284 | 1000.9094 | 0.0017863 | -6.1035e-06 | 21.7122 | 4.2091 | 4.2071 | 1.0009 | 0.0017863
| 473.15 | 2100000 | 4490.8179 | 3316.5847 | 865.0835 | 0.00013446 | 200 | 20.7253 | 4.4908 | 3.3166 | 0.86508 | 0.00013446
| 472.15 | 2100000 | 4485.6572 | 3320.3652 | 866.2697 | 0.00013518 | 199 | 20.7253 | 4.4857 | 3.3204 | 0.86627 | 0.00013518
| 471.15 | 2100000 | 4480.5723 | 3324.1636 | 867.45 | 0.0001359 | 198 | 20.7253 | 4.4806 | 3.3242 | 0.86745 | 0.0001359
| 470.15 | 2100000 | 4475.562 | 3327.9795 | 868.6245 | 0.00013664 | 197 | 20.7253 | 4.4756 | 3.328 | 0.86862 | 0.00013664
| 469.15 | 2100000 | 4470.625 | 3331.8125 | 869.7932 | 0.00013738 | 196 | 20.7253 | 4.4706 | 3.3318 | 0.86979 | 0.00013738
| 468.15 | 2100000 | 4465.7603 | 3335.6628 | 870.9561 | 0.00013813 | 195 | 20.7253 | 4.4658 | 3.3357 | 0.87096 | 0.00013813
| 467.15 | 2100000 | 4460.9663 | 3339.5305 | 872.1132 | 0.00013888 | 194 | 20.7253 | 4.461 | 3.3395 | 0.87211 | 0.00013888
| 466.15 | 2100000 | 4456.2417 | 3343.415 | 873.2648 | 0.00013965 | 193 | 20.7253 | 4.4562 | 3.3434 | 0.87326 | 0.00013965
| 465.15 | 2100000 | 4451.5854 | 3347.3164 | 874.4106 | 0.00014042 | 192 | 20.7253 | 4.4516 | 3.3473 | 0.87441 | 0.00014042
| 464.15 | 2100000 | 4446.9961 | 3351.2346 | 875.551 | 0.0001412 | 191 | 20.7253 | 4.447 | 3.3512 | 0.87555 | 0.0001412
| 463.15 | 2100000 | 4442.4731 | 3355.1697 | 876.6858 | 0.000142 | 190 | 20.7253 | 4.4425 | 3.3552 | 0.87669 | 0.000142
| 462.15 | 2100000 | 4438.0146 | 3359.1211 | 877.8151 | 0.00014279 | 189 | 20.7253 | 4.438 | 3.3591 | 0.87782 | 0.00014279
| 461.15 | 2100000 | 4433.6201 | 3363.0889 | 878.939 | 0.0001436 | 188 | 20.7253 | 4.4336 | 3.3631 | 0.87894 | 0.0001436
| 460.15 | 2100000 | 4429.2886 | 3367.073 | 880.0574 | 0.00014442 | 187 | 20.7253 | 4.4293 | 3.3671 | 0.88006 | 0.00014442
| 459.15 | 2100000 | 4425.0181 | 3371.0732 | 881.1705 | 0.00014525 | 186 | 20.7253 | 4.425 | 3.3711 | 0.88117 | 0.00014525
| 458.15 | 2100000 | 4420.8086 | 3375.0898 | 882.2783 | 0.00014608 | 185 | 20.7253 | 4.4208 | 3.3751 | 0.88228 | 0.00014608
| 457.15 | 2100000 | 4416.6582 | 3379.1221 | 883.3808 | 0.00014693 | 184 | 20.7253 | 4.4167 | 3.3791 | 0.88338 | 0.00014693
| 456.15 | 2100000 | 4412.5664 | 3383.1704 | 884.478 | 0.00014778 | 183 | 20.7253 | 4.4126 | 3.3832 | 0.88448 | 0.00014778
| 455.15 | 2100000 | 4408.5327 | 3387.2341 | 885.57 | 0.00014865 | 182 | 20.7253 | 4.4085 | 3.3872 | 0.88557 | 0.00014865
| 454.15 | 2100000 | 4404.5552 | 3391.3137 | 886.6568 | 0.00014953 | 181 | 20.7253 | 4.4046 | 3.3913 | 0.88666 | 0.00014953
| 453.15 | 2100000 | 4400.6338 | 3395.4087 | 887.7385 | 0.00015041 | 180 | 20.7253 | 4.4006 | 3.3954 | 0.88774 | 0.00015041
| 452.15 | 2100000 | 4396.7671 | 3399.5193 | 888.815 | 0.00015131 | 179 | 20.7253 | 4.3968 | 3.3995 | 0.88882 | 0.00015131
| 451.15 | 2100000 | 4392.9541 | 3403.645 | 889.8864 | 0.00015221 | 178 | 20.7253 | 4.393 | 3.4036 | 0.88989 | 0.00015221
| 450.15 | 2100000 | 4389.1943 | 3407.7859 | 890.9528 | 0.00015313 | 177 | 20.7253 | 4.3892 | 3.4078 | 0.89095 | 0.00015313
| 449.15 | 2100000 | 4385.4868 | 3411.9419 | 892.0142 | 0.00015406 | 176 | 20.7253 | 4.3855 | 3.4119 | 0.89201 | 0.00015406
| 448.15 | 2100000 | 4381.8311 | 3416.1128 | 893.0705 | 0.000155 | 175 | 20.7253 | 4.3818 | 3.4161 | 0.89307 | 0.000155
| 447.15 | 2100000 | 4378.2256 | 3420.2983 | 894.1219 | 0.00015595 | 174 | 20.7253 | 4.3782 | 3.4203 | 0.89412 | 0.00015595
| 446.15 | 2100000 | 4374.6694 | 3424.4988 | 895.1683 | 0.00015692 | 173 | 20.7253 | 4.3747 | 3.4245 | 0.89517 | 0.00015692
| 445.15 | 2100000 | 4371.1631 | 3428.7141 | 896.2099 | 0.00015789 | 172 | 20.7253 | 4.3712 | 3.4287 | 0.89621 | 0.00015789
| 444.15 | 2100000 | 4367.7046 | 3432.9436 | 897.2465 | 0.00015888 | 171 | 20.7253 | 4.3677 | 3.4329 | 0.89725 | 0.00015888
| 443.15 | 2100000 | 4364.2939 | 3437.1877 | 898.2783 | 0.00015988 | 170 | 20.7253 | 4.3643 | 3.4372 | 0.89828 | 0.00015988
| 442.15 | 2100000 | 4360.9297 | 3441.446 | 899.3052 | 0.00016089 | 169 | 20.7253 | 4.3609 | 3.4414 | 0.89931 | 0.00016089
| 441.15 | 2100000 | 4357.6118 | 3445.7188 | 900.3274 | 0.00016192 | 168 | 20.7253 | 4.3576 | 3.4457 | 0.90033 | 0.00016192
| 440.15 | 2100000 | 4354.3389 | 3450.0054 | 901.3447 | 0.00016296 | 167 | 20.7253 | 4.3543 | 3.45 | 0.90134 | 0.00016296
| 439.15 | 2100000 | 4351.1108 | 3454.3062 | 902.3573 | 0.00016401 | 166 | 20.7253 | 4.3511 | 3.4543 | 0.90236 | 0.00016401
| 438.15 | 2100000 | 4347.9268 | 3458.6208 | 903.3652 | 0.00016507 | 165 | 20.7253 | 4.3479 | 3.4586 | 0.90337 | 0.00016507
| 437.15 | 2100000 | 4344.7861 | 3462.9492 | 904.3683 | 0.00016615 | 164 | 20.7253 | 4.3448 | 3.4629 | 0.90437 | 0.00016615
| 436.15 | 2100000 | 4341.6885 | 3467.2915 | 905.3667 | 0.00016724 | 163 | 20.7253 | 4.3417 | 3.4673 | 0.90537 | 0.00016724
| 435.15 | 2100000 | 4338.6323 | 3471.6472 | 906.3605 | 0.00016835 | 162 | 20.7253 | 4.3386 | 3.4716 | 0.90636 | 0.00016835
| 434.15 | 2100000 | 4335.6177 | 3476.0166 | 907.3495 | 0.00016947 | 161 | 20.7253 | 4.3356 | 3.476 | 0.90735 | 0.00016947
| 433.15 | 2100000 | 4332.644 | 3480.3994 | 908.334 | 0.00017061 | 160 | 20.7253 | 4.3326 | 3.4804 | 0.90833 | 0.00017061
| 432.15 | 2100000 | 4329.7109 | 3484.7957 | 909.3138 | 0.00017176 | 159 | 20.7253 | 4.3297 | 3.4848 | 0.90931 | 0.00017176
| 431.15 | 2100000 | 4326.8174 | 3489.2048 | 910.2891 | 0.00017293 | 158 | 20.7253 | 4.3268 | 3.4892 | 0.91029 | 0.00017293
| 430.15 | 2100000 | 4323.9624 | 3493.6274 | 911.2596 | 0.00017412 | 157 | 20.7253 | 4.324 | 3.4936 | 0.91126 | 0.00017412
| 429.15 | 2100000 | 4321.1465 | 3498.0632 | 912.2257 | 0.00017532 | 156 | 20.7253 | 4.3211 | 3.4981 | 0.91223 | 0.00017532
| 428.15 | 2100000 | 4318.3682 | 3502.5117 | 913.1873 | 0.00017653 | 155 | 20.7253 | 4.3184 | 3.5025 | 0.91319 | 0.00017653
| 427.15 | 2100000 | 4315.6274 | 3506.9734 | 914.1442 | 0.00017776 | 154 | 20.7253 | 4.3156 | 3.507 | 0.91414 | 0.00017776
| 426.15 | 2100000 | 4312.9238 | 3511.4478 | 915.0967 | 0.00017901 | 153 | 20.7253 | 4.3129 | 3.5114 | 0.9151 | 0.00017901
| 425.15 | 2100000 | 4310.2563 | 3515.9348 | 916.0446 | 0.00018028 | 152 | 20.7253 | 4.3103 | 3.5159 | 0.91604 | 0.00018028
| 424.15 | 2100000 | 4307.6245 | 3520.4346 | 916.988 | 0.00018157 | 151 | 20.7253 | 4.3076 | 3.5204 | 0.91699 | 0.00018157
| 423.15 | 2100000 | 4305.0283 | 3524.9468 | 917.927 | 0.00018287 | 150 | 20.7253 | 4.305 | 3.5249 | 0.91793 | 0.00018287
| 422.15 | 2100000 | 4302.4673 | 3529.4714 | 918.8615 | 0.00018419 | 149 | 20.7253 | 4.3025 | 3.5295 | 0.91886 | 0.00018419
| 421.15 | 2100000 | 4299.9404 | 3534.0085 | 919.7916 | 0.00018553 | 148 | 20.7253 | 4.2999 | 3.534 | 0.91979 | 0.00018553
| 420.15 | 2100000 | 4297.4478 | 3538.5581 | 920.7172 | 0.00018689 | 147 | 20.7253 | 4.2974 | 3.5386 | 0.92072 | 0.00018689
| 419.15 | 2100000 | 4294.9883 | 3543.1199 | 921.6383 | 0.00018827 | 146 | 20.7253 | 4.295 | 3.5431 | 0.92164 | 0.00018827
| 418.15 | 2100000 | 4292.562 | 3547.6936 | 922.5551 | 0.00018967 | 145 | 20.7253 | 4.2926 | 3.5477 | 0.92256 | 0.00018967
| 417.15 | 2100000 | 4290.1685 | 3552.2795 | 923.4673 | 0.00019109 | 144 | 20.7253 | 4.2902 | 3.5523 | 0.92347 | 0.00019109
| 416.15 | 2100000 | 4287.8071 | 3556.8774 | 924.3752 | 0.00019253 | 143 | 20.7253 | 4.2878 | 3.5569 | 0.92438 | 0.00019253
| 415.15 | 2100000 | 4285.4775 | 3561.4873 | 925.2788 | 0.000194 | 142 | 20.7253 | 4.2855 | 3.5615 | 0.92528 | 0.000194
| 414.15 | 2100000 | 4283.1797 | 3566.1089 | 926.1779 | 0.00019548 | 141 | 20.7253 | 4.2832 | 3.5661 | 0.92618 | 0.00019548
| 413.15 | 2100000 | 4280.9121 | 3570.7424 | 927.0726 | 0.00019699 | 140 | 20.7253 | 4.2809 | 3.5707 | 0.92707 | 0.00019699
| 412.15 | 2100000 | 4278.6758 | 3575.3875 | 927.963 | 0.00019851 | 139 | 20.7253 | 4.2787 | 3.5754 | 0.92796 | 0.00019851
| 411.15 | 2100000 | 4276.4692 | 3580.0442 | 928.8491 | 0.00020007 | 138 | 20.7253 | 4.2765 | 3.58 | 0.92885 | 0.00020007
| 410.15 | 2100000 | 4274.293 | 3584.7124 | 929.7307 | 0.00020164 | 137 | 20.7253 | 4.2743 | 3.5847 | 0.92973 | 0.00020164
| 409.15 | 2100000 | 4272.146 | 3589.3921 | 930.608 | 0.00020324 | 136 | 20.7253 | 4.2721 | 3.5894 | 0.93061 | 0.00020324
| 408.15 | 2100000 | 4270.0278 | 3594.0833 | 931.4809 | 0.00020486 | 135 | 20.7253 | 4.27 | 3.5941 | 0.93148 | 0.00020486
| 407.15 | 2100000 | 4267.939 | 3598.7856 | 932.3495 | 0.00020651 | 134 | 20.7253 | 4.2679 | 3.5988 | 0.93235 | 0.00020651
| 406.15 | 2100000 | 4265.8779 | 3603.4993 | 933.2137 | 0.00020819 | 133 | 20.7253 | 4.2659 | 3.6035 | 0.93321 | 0.00020819
| 405.15 | 2100000 | 4263.8457 | 3608.2239 | 934.0736 | 0.00020989 | 132 | 20.7253 | 4.2638 | 3.6082 | 0.93407 | 0.00020989
| 404.15 | 2100000 | 4261.8408 | 3612.9597 | 934.9291 | 0.00021161 | 131 | 20.7253 | 4.2618 | 3.613 | 0.93493 | 0.00021161
| 403.15 | 2100000 | 4259.8633 | 3617.7065 | 935.7804 | 0.00021337 | 130 | 20.7253 | 4.2599 | 3.6177 | 0.93578 | 0.00021337
| 402.15 | 2100000 | 4257.9131 | 3622.4644 | 936.6273 | 0.00021515 | 129 | 20.7253 | 4.2579 | 3.6225 | 0.93663 | 0.00021515
| 401.15 | 2100000 | 4255.9902 | 3627.2327 | 937.4698 | 0.00021696 | 128 | 20.7253 | 4.256 | 3.6272 | 0.93747 | 0.00021696
| 400.15 | 2100000 | 4254.0933 | 3632.012 | 938.308 | 0.0002188 | 127 | 20.7253 | 4.2541 | 3.632 | 0.93831 | 0.0002188
| 399.15 | 2100000 | 4252.2231 | 3636.802 | 939.1419 | 0.00022067 | 126 | 20.7253 | 4.2522 | 3.6368 | 0.93914 | 0.00022067
| 398.15 | 2100000 | 4250.3784 | 3641.6025 | 939.9715 | 0.00022257 | 125 | 20.7253 | 4.2504 | 3.6416 | 0.93997 | 0.00022257
| 397.15 | 2100000 | 4248.5601 | 3646.4136 | 940.7967 | 0.0002245 | 124 | 20.7253 | 4.2486 | 3.6464 | 0.9408 | 0.0002245
| 396.15 | 2100000 | 4246.7666 | 3651.2351 | 941.6176 | 0.00022646 | 123 | 20.7253 | 4.2468 | 3.6512 | 0.94162 | 0.00022646
| 395.15 | 2100000 | 4244.999 | 3656.0669 | 942.4341 | 0.00022846 | 122 | 20.7253 | 4.245 | 3.6561 | 0.94243 | 0.00022846
| 394.15 | 2100000 | 4243.2559 | 3660.9089 | 943.2463 | 0.00023049 | 121 | 20.7253 | 4.2433 | 3.6609 | 0.94325 | 0.00023049
| 393.15 | 2100000 | 4241.5376 | 3665.7612 | 944.0542 | 0.00023255 | 120 | 20.7253 | 4.2415 | 3.6658 | 0.94405 | 0.00023255
| 392.15 | 2100000 | 4239.8442 | 3670.6235 | 944.8577 | 0.00023465 | 119 | 20.7253 | 4.2398 | 3.6706 | 0.94486 | 0.00023465
| 391.15 | 2100000 | 4238.1748 | 3675.4958 | 945.6569 | 0.00023678 | 118 | 20.7253 | 4.2382 | 3.6755 | 0.94566 | 0.00023678
| 390.15 | 2100000 | 4236.5293 | 3680.3779 | 946.4516 | 0.00023895 | 117 | 20.7253 | 4.2365 | 3.6804 | 0.94645 | 0.00023895
| 389.15 | 2100000 | 4234.9077 | 3685.2698 | 947.2421 | 0.00024115 | 116 | 20.7253 | 4.2349 | 3.6853 | 0.94724 | 0.00024115
| 388.15 | 2100000 | 4233.3101 | 3690.1714 | 948.0281 | 0.0002434 | 115 | 20.7253 | 4.2333 | 3.6902 | 0.94803 | 0.0002434
| 387.15 | 2100000 | 4231.7358 | 3695.0825 | 948.8098 | 0.00024568 | 114 | 20.7253 | 4.2317 | 3.6951 | 0.94881 | 0.00024568
| 386.15 | 2100000 | 4230.1846 | 3700.0032 | 949.5871 | 0.000248 | 113 | 20.7253 | 4.2302 | 3.7 | 0.94959 | 0.000248
| 385.15 | 2100000 | 4228.6562 | 3704.9331 | 950.36 | 0.00025037 | 112 | 20.7253 | 4.2287 | 3.7049 | 0.95036 | 0.00025037
| 384.15 | 2100000 | 4227.1514 | 3709.8723 | 951.1285 | 0.00025277 | 111 | 20.7253 | 4.2272 | 3.7099 | 0.95113 | 0.00025277
| 383.15 | 2100000 | 4225.6689 | 3714.8206 | 951.8926 | 0.00025522 | 110 | 20.7253 | 4.2257 | 3.7148 | 0.95189 | 0.00025522
| 382.15 | 2100000 | 4224.209 | 3719.7781 | 952.6523 | 0.00025771 | 109 | 20.7253 | 4.2242 | 3.7198 | 0.95265 | 0.00025771
| 381.15 | 2100000 | 4222.7715 | 3724.7441 | 953.4075 | 0.00026025 | 108 | 20.7253 | 4.2228 | 3.7247 | 0.95341 | 0.00026025
| 380.15 | 2100000 | 4221.3564 | 3729.7192 | 954.1583 | 0.00026283 | 107 | 20.7253 | 4.2214 | 3.7297 | 0.95416 | 0.00026283
| 379.15 | 2100000 | 4219.9634 | 3734.7026 | 954.9047 | 0.00026546 | 106 | 20.7253 | 4.22 | 3.7347 | 0.9549 | 0.00026546
| 378.15 | 2100000 | 4218.5923 | 3739.6946 | 955.6465 | 0.00026813 | 105 | 20.7253 | 4.2186 | 3.7397 | 0.95565 | 0.00026813
| 377.15 | 2100000 | 4217.2427 | 3744.6951 | 956.384 | 0.00027086 | 104 | 20.7253 | 4.2172 | 3.7447 | 0.95638 | 0.00027086
| 376.15 | 2100000 | 4215.915 | 3749.7034 | 957.1169 | 0.00027364 | 103 | 20.7253 | 4.2159 | 3.7497 | 0.95712 | 0.00027364
| 375.15 | 2100000 | 4214.6094 | 3754.72 | 957.8453 | 0.00027646 | 102 | 20.7253 | 4.2146 | 3.7547 | 0.95785 | 0.00027646
| 374.15 | 2100000 | 4213.3247 | 3759.7441 | 958.5692 | 0.00027934 | 101 | 20.7253 | 4.2133 | 3.7597 | 0.95857 | 0.00027934
| 373.15 | 2100000 | 4212.0615 | 3764.7761 | 959.2886 | 0.00028228 | 100 | 20.7253 | 4.2121 | 3.7648 | 0.95929 | 0.00028228
| 372.15 | 2100000 | 4210.8193 | 3769.8157 | 960.0034 | 0.00028527 | 99 | 20.7253 | 4.2108 | 3.7698 | 0.96 | 0.00028527
| 371.15 | 2100000 | 4209.5986 | 3774.8623 | 960.7136 | 0.00028832 | 98 | 20.7253 | 4.2096 | 3.7749 | 0.96071 | 0.00028832
| 370.15 | 2100000 | 4208.3989 | 3779.9163 | 961.4193 | 0.00029143 | 97 | 20.7253 | 4.2084 | 3.7799 | 0.96142 | 0.00029143
| 369.15 | 2100000 | 4207.2197 | 3784.9771 | 962.1204 | 0.00029459 | 96 | 20.7253 | 4.2072 | 3.785 | 0.96212 | 0.00029459
| 368.15 | 2100000 | 4206.062 | 3790.0444 | 962.8168 | 0.00029782 | 95 | 20.7253 | 4.2061 | 3.79 | 0.96282 | 0.00029782
| 367.15 | 2100000 | 4204.9248 | 3795.1184 | 963.5087 | 0.00030111 | 94 | 20.7253 | 4.2049 | 3.7951 | 0.96351 | 0.00030111
| 366.15 | 2100000 | 4203.8081 | 3800.1985 | 964.1958 | 0.00030447 | 93 | 20.7253 | 4.2038 | 3.8002 | 0.9642 | 0.00030447
| 365.15 | 2100000 | 4202.7124 | 3805.2847 | 964.8783 | 0.00030789 | 92 | 20.7253 | 4.2027 | 3.8053 | 0.96488 | 0.00030789
| 364.15 | 2100000 | 4201.6372 | 3810.3767 | 965.556 | 0.00031138 | 91 | 20.7253 | 4.2016 | 3.8104 | 0.96556 | 0.00031138
| 363.15 | 2100000 | 4200.582 | 3815.4741 | 966.2291 | 0.00031495 | 90 | 20.7253 | 4.2006 | 3.8155 | 0.96623 | 0.00031495
| 362.15 | 2100000 | 4199.5479 | 3820.5769 | 966.8974 | 0.00031858 | 89 | 20.7253 | 4.1995 | 3.8206 | 0.9669 | 0.00031858
| 361.15 | 2100000 | 4198.5342 | 3825.6843 | 967.5609 | 0.00032229 | 88 | 20.7253 | 4.1985 | 3.8257 | 0.96756 | 0.00032229
| 360.15 | 2100000 | 4197.5405 | 3830.7966 | 968.2197 | 0.00032607 | 87 | 20.7253 | 4.1975 | 3.8308 | 0.96822 | 0.00032607
| 359.15 | 2100000 | 4196.5674 | 3835.9133 | 968.8736 | 0.00032993 | 86 | 20.7253 | 4.1966 | 3.8359 | 0.96887 | 0.00032993
| 358.15 | 2100000 | 4195.6143 | 3841.0339 | 969.5226 | 0.00033388 | 85 | 20.7253 | 4.1956 | 3.841 | 0.96952 | 0.00033388
| 357.15 | 2100000 | 4194.6816 | 3846.1582 | 970.1669 | 0.0003379 | 84 | 20.7253 | 4.1947 | 3.8462 | 0.97017 | 0.0003379
| 356.15 | 2100000 | 4193.769 | 3851.2859 | 970.8062 | 0.00034201 | 83 | 20.7253 | 4.1938 | 3.8513 | 0.97081 | 0.00034201
| 355.15 | 2100000 | 4192.877 | 3856.4167 | 971.4406 | 0.00034621 | 82 | 20.7253 | 4.1929 | 3.8564 | 0.97144 | 0.00034621
| 354.15 | 2100000 | 4192.0049 | 3861.55 | 972.0699 | 0.0003505 | 81 | 20.7253 | 4.192 | 3.8616 | 0.97207 | 0.0003505
| 353.15 | 2100000 | 4191.1528 | 3866.6855 | 972.6944 | 0.00035488 | 80 | 20.7253 | 4.1912 | 3.8667 | 0.97269 | 0.00035488
| 352.15 | 2100000 | 4190.3213 | 3871.8228 | 973.3138 | 0.00035935 | 79 | 20.7253 | 4.1903 | 3.8718 | 0.97331 | 0.00035935
| 351.15 | 2100000 | 4189.5093 | 3876.9614 | 973.9282 | 0.00036393 | 78 | 20.7253 | 4.1895 | 3.877 | 0.97393 | 0.00036393
| 350.15 | 2100000 | 4188.7178 | 3882.1013 | 974.5374 | 0.0003686 | 77 | 20.7253 | 4.1887 | 3.8821 | 0.97454 | 0.0003686
| 349.15 | 2100000 | 4187.9463 | 3887.2415 | 975.1415 | 0.00037338 | 76 | 20.7253 | 4.1879 | 3.8872 | 0.97514 | 0.00037338
| 348.15 | 2100000 | 4187.1948 | 3892.3816 | 975.7406 | 0.00037826 | 75 | 20.7253 | 4.1872 | 3.8924 | 0.97574 | 0.00037826
| 347.15 | 2100000 | 4186.4634 | 3897.5212 | 976.3344 | 0.00038325 | 74 | 20.7253 | 4.1865 | 3.8975 | 0.97633 | 0.00038325
| 346.15 | 2100000 | 4185.752 | 3902.6599 | 976.923 | 0.00038836 | 73 | 20.7253 | 4.1858 | 3.9027 | 0.97692 | 0.00038836
| 345.15 | 2100000 | 4185.0605 | 3907.7971 | 977.5063 | 0.00039359 | 72 | 20.7253 | 4.1851 | 3.9078 | 0.97751 | 0.00039359
| 344.15 | 2100000 | 4184.3896 | 3912.9321 | 978.0843 | 0.00039893 | 71 | 20.7253 | 4.1844 | 3.9129 | 0.97808 | 0.00039893
| 343.15 | 2100000 | 4183.7383 | 3918.0645 | 978.657 | 0.0004044 | 70 | 20.7253 | 4.1837 | 3.9181 | 0.97866 | 0.0004044
| 342.15 | 2100000 | 4183.1074 | 3923.1936 | 979.2242 | 0.00041 | 69 | 20.7253 | 4.1831 | 3.9232 | 0.97922 | 0.00041
| 341.15 | 2100000 | 4182.4966 | 3928.3186 | 979.7861 | 0.00041572 | 68 | 20.7253 | 4.1825 | 3.9283 | 0.97979 | 0.00041572
| 340.15 | 2100000 | 4181.9058 | 3933.4392 | 980.3425 | 0.00042159 | 67 | 20.7253 | 4.1819 | 3.9334 | 0.98034 | 0.00042159
| 339.15 | 2100000 | 4181.335 | 3938.5547 | 980.8934 | 0.00042759 | 66 | 20.7253 | 4.1813 | 3.9386 | 0.98089 | 0.00042759
| 338.15 | 2100000 | 4180.7842 | 3943.6641 | 981.4387 | 0.00043374 | 65 | 20.7253 | 4.1808 | 3.9437 | 0.98144 | 0.00043374
| 337.15 | 2100000 | 4180.2534 | 3948.7668 | 981.9784 | 0.00044005 | 64 | 20.7253 | 4.1803 | 3.9488 | 0.98198 | 0.00044005
| 336.15 | 2100000 | 4179.7432 | 3953.8623 | 982.5125 | 0.0004465 | 63 | 20.7253 | 4.1797 | 3.9539 | 0.98251 | 0.0004465
| 335.15 | 2100000 | 4179.2529 | 3958.9495 | 983.0408 | 0.00045312 | 62 | 20.7253 | 4.1793 | 3.9589 | 0.98304 | 0.00045312
| 334.15 | 2100000 | 4178.7832 | 3964.0276 | 983.5634 | 0.0004599 | 61 | 20.7253 | 4.1788 | 3.964 | 0.98356 | 0.0004599
| 333.15 | 2100000 | 4178.3335 | 3969.0959 | 984.0801 | 0.00046685 | 60 | 20.7253 | 4.1783 | 3.9691 | 0.98408 | 0.00046685
| 332.15 | 2100000 | 4177.9038 | 3974.1538 | 984.5909 | 0.00047398 | 59 | 20.7253 | 4.1779 | 3.9742 | 0.98459 | 0.00047398
| 331.15 | 2100000 | 4177.4946 | 3979.1997 | 985.0959 | 0.00048129 | 58 | 20.7253 | 4.1775 | 3.9792 | 0.9851 | 0.00048129
| 330.15 | 2100000 | 4177.1055 | 3984.2334 | 985.5949 | 0.00048879 | 57 | 20.7253 | 4.1771 | 3.9842 | 0.98559 | 0.00048879
| 329.15 | 2100000 | 4176.7368 | 3989.2534 | 986.0878 | 0.00049649 | 56 | 20.7253 | 4.1767 | 3.9893 | 0.98609 | 0.00049649
| 328.15 | 2100000 | 4176.3887 | 3994.2593 | 986.5746 | 0.00050439 | 55 | 20.7253 | 4.1764 | 3.9943 | 0.98657 | 0.00050439
| 327.15 | 2100000 | 4176.0605 | 3999.2495 | 987.0553 | 0.0005125 | 54 | 20.7253 | 4.1761 | 3.9992 | 0.98706 | 0.0005125
| 326.15 | 2100000 | 4175.7529 | 4004.2231 | 987.5297 | 0.00052083 | 53 | 20.7253 | 4.1758 | 4.0042 | 0.98753 | 0.00052083
| 325.15 | 2100000 | 4175.4663 | 4009.1792 | 987.9979 | 0.00052938 | 52 | 20.7253 | 4.1755 | 4.0092 | 0.988 | 0.00052938
| 324.15 | 2100000 | 4175.1997 | 4014.1167 | 988.4597 | 0.00053817 | 51 | 20.7253 | 4.1752 | 4.0141 | 0.98846 | 0.00053817
| 323.15 | 2100000 | 4174.9541 | 4019.0342 | 988.915 | 0.0005472 | 50 | 20.7253 | 4.175 | 4.019 | 0.98891 | 0.0005472
| 322.15 | 2100000 | 4174.729 | 4023.9307 | 989.3638 | 0.00055648 | 49 | 20.7253 | 4.1747 | 4.0239 | 0.98936 | 0.00055648
| 321.15 | 2100000 | 4174.5244 | 4028.8049 | 989.806 | 0.00056603 | 48 | 20.7253 | 4.1745 | 4.0288 | 0.98981 | 0.00056603
| 320.15 | 2100000 | 4174.3413 | 4033.6555 | 990.2416 | 0.00057584 | 47 | 20.7253 | 4.1743 | 4.0337 | 0.99024 | 0.00057584
| 319.15 | 2100000 | 4174.1787 | 4038.4814 | 990.6704 | 0.00058594 | 46 | 20.7253 | 4.1742 | 4.0385 | 0.99067 | 0.00058594
| 318.15 | 2100000 | 4174.0376 | 4043.2815 | 991.0924 | 0.00059634 | 45 | 20.7253 | 4.174 | 4.0433 | 0.99109 | 0.00059634
| 317.15 | 2100000 | 4173.9175 | 4048.0537 | 991.5075 | 0.00060704 | 44 | 20.7253 | 4.1739 | 4.0481 | 0.99151 | 0.00060704
| 316.15 | 2100000 | 4173.8188 | 4052.7974 | 991.9156 | 0.00061805 | 43 | 20.7253 | 4.1738 | 4.0528 | 0.99192 | 0.00061805
| 315.15 | 2100000 | 4173.7422 | 4057.5105 | 992.3167 | 0.0006294 | 42 | 20.7253 | 4.1737 | 4.0575 | 0.99232 | 0.0006294
| 314.15 | 2100000 | 4173.687 | 4062.1921 | 992.7105 | 0.00064109 | 41 | 20.7253 | 4.1737 | 4.0622 | 0.99271 | 0.00064109
| 313.15 | 2100000 | 4173.6543 | 4066.8403 | 993.097 | 0.00065314 | 40 | 20.7253 | 4.1737 | 4.0668 | 0.9931 | 0.00065314
| 312.15 | 2100000 | 4173.644 | 4071.4541 | 993.4763 | 0.00066556 | 39 | 20.7253 | 4.1736 | 4.0715 | 0.99348 | 0.00066556
| 311.15 | 2100000 | 4173.6562 | 4076.0315 | 993.848 | 0.00067838 | 38 | 20.7253 | 4.1737 | 4.076 | 0.99385 | 0.00067838
| 310.15 | 2100000 | 4173.6919 | 4080.571 | 994.2121 | 0.0006916 | 37 | 20.7253 | 4.1737 | 4.0806 | 0.99421 | 0.0006916
| 309.15 | 2100000 | 4173.751 | 4085.0713 | 994.5685 | 0.00070524 | 36 | 20.7253 | 4.1738 | 4.0851 | 0.99457 | 0.00070524
| 308.15 | 2100000 | 4173.8345 | 4089.5303 | 994.9172 | 0.00071933 | 35 | 20.7253 | 4.1738 | 4.0895 | 0.99492 | 0.00071933
| 307.15 | 2100000 | 4173.9424 | 4093.9468 | 995.2579 | 0.00073388 | 34 | 20.7253 | 4.1739 | 4.0939 | 0.99526 | 0.00073388
| 306.15 | 2100000 | 4174.0757 | 4098.3188 | 995.5906 | 0.00074892 | 33 | 20.7253 | 4.1741 | 4.0983 | 0.99559 | 0.00074892
| 305.15 | 2100000 | 4174.2354 | 4102.6445 | 995.915 | 0.00076446 | 32 | 20.7253 | 4.1742 | 4.1026 | 0.99592 | 0.00076446
| 304.15 | 2100000 | 4174.4214 | 4106.9229 | 996.2313 | 0.00078053 | 31 | 20.7253 | 4.1744 | 4.1069 | 0.99623 | 0.00078053
| 303.15 | 2100000 | 4174.6353 | 4111.1514 | 996.539 | 0.00079716 | 30 | 20.7253 | 4.1746 | 4.1112 | 0.99654 | 0.00079716
| 302.15 | 2100000 | 4174.8784 | 4115.3291 | 996.8382 | 0.00081437 | 29 | 20.7253 | 4.1749 | 4.1153 | 0.99684 | 0.00081437
| 301.15 | 2100000 | 4175.1514 | 4119.4536 | 997.1287 | 0.00083219 | 28 | 20.7253 | 4.1752 | 4.1195 | 0.99713 | 0.00083219
| 300.15 | 2100000 | 4175.4556 | 4123.5234 | 997.4102 | 0.00085065 | 27 | 20.7253 | 4.1755 | 4.1235 | 0.99741 | 0.00085065
| 299.15 | 2100000 | 4175.793 | 4127.5371 | 997.6828 | 0.00086978 | 26 | 20.7253 | 4.1758 | 4.1275 | 0.99768 | 0.00086978
| 298.15 | 2100000 | 4176.165 | 4131.4927 | 997.9461 | 0.00088962 | 25 | 20.7253 | 4.1762 | 4.1315 | 0.99795 | 0.00088962
| 297.15 | 2100000 | 4176.5732 | 4135.3882 | 998.2001 | 0.0009102 | 24 | 20.7253 | 4.1766 | 4.1354 | 0.9982 | 0.0009102
| 296.15 | 2100000 | 4177.02 | 4139.2222 | 998.4445 | 0.00093156 | 23 | 20.7253 | 4.177 | 4.1392 | 0.99844 | 0.00093156
| 295.15 | 2100000 | 4177.5083 | 4142.9927 | 998.6791 | 0.00095375 | 22 | 20.7253 | 4.1775 | 4.143 | 0.99868 | 0.00095375
| 294.15 | 2100000 | 4178.0396 | 4146.6987 | 998.9039 | 0.0009768 | 21 | 20.7253 | 4.178 | 4.1467 | 0.9989 | 0.0009768
| 293.15 | 2100000 | 4178.6182 | 4150.3384 | 999.1185 | 0.0010008 | 20 | 20.7253 | 4.1786 | 4.1503 | 0.99912 | 0.0010008
| 292.15 | 2100000 | 4179.2466 | 4153.9102 | 999.3228 | 0.0010257 | 19 | 20.7253 | 4.1792 | 4.1539 | 0.99932 | 0.0010257
| 291.15 | 2100000 | 4179.9287 | 4157.4126 | 999.5164 | 0.0010516 | 18 | 20.7253 | 4.1799 | 4.1574 | 0.99952 | 0.0010516
| 290.15 | 2100000 | 4180.6689 | 4160.8442 | 999.6993 | 0.0010786 | 17 | 20.7253 | 4.1807 | 4.1608 | 0.9997 | 0.0010786
| 289.15 | 2100000 | 4181.4712 | 4164.2041 | 999.8711 | 0.0011068 | 16 | 20.7253 | 4.1815 | 4.1642 | 0.99987 | 0.0011068
| 288.15 | 2100000 | 4182.3418 | 4167.4902 | 1000.0316 | 0.0011362 | 15 | 20.7253 | 4.1823 | 4.1675 | 1 | 0.0011362
| 287.15 | 2100000 | 4183.2856 | 4170.7021 | 1000.1805 | 0.0011668 | 14 | 20.7253 | 4.1833 | 4.1707 | 1.0002 | 0.0011668
| 286.15 | 2100000 | 4184.3096 | 4173.8384 | 1000.3175 | 0.0011988 | 13 | 20.7253 | 4.1843 | 4.1738 | 1.0003 | 0.0011988
| 285.15 | 2100000 | 4185.4209 | 4176.8984 | 1000.4424 | 0.0012322 | 12 | 20.7253 | 4.1854 | 4.1769 | 1.0004 | 0.0012322
| 284.15 | 2100000 | 4186.627 | 4179.8813 | 1000.5548 | 0.0012671 | 11 | 20.7253 | 4.1866 | 4.1799 | 1.0006 | 0.0012671
| 283.15 | 2100000 | 4187.937 | 4182.7871 | 1000.6544 | 0.0013037 | 10 | 20.7253 | 4.1879 | 4.1828 | 1.0007 | 0.0013037
| 282.15 | 2100000 | 4189.3608 | 4185.6147 | 1000.7408 | 0.001342 | 9 | 20.7253 | 4.1894 | 4.1856 | 1.0007 | 0.001342
| 281.15 | 2100000 | 4190.9092 | 4188.3638 | 1000.8138 | 0.0013821 | 8 | 20.7253 | 4.1909 | 4.1884 | 1.0008 | 0.0013821
| 280.15 | 2100000 | 4192.5942 | 4191.0352 | 1000.8728 | 0.0014242 | 7 | 20.7253 | 4.1926 | 4.191 | 1.0009 | 0.0014242
| 279.15 | 2100000 | 4194.4292 | 4193.6284 | 1000.9175 | 0.0014684 | 6 | 20.7253 | 4.1944 | 4.1936 | 1.0009 | 0.0014684
| 278.15 | 2100000 | 4196.4292 | 4196.144 | 1000.9474 | 0.0015148 | 5 | 20.7253 | 4.1964 | 4.1961 | 1.0009 | 0.0015148
| 277.15 | 2100000 | 4198.6104 | 4198.583 | 1000.9622 | 0.0015637 | 4 | 20.7253 | 4.1986 | 4.1986 | 1.001 | 0.0015637
| 276.15 | 2100000 | 4200.9912 | 4200.9463 | 1000.9612 | 0.001615 | 3 | 20.7253 | 4.201 | 4.2009 | 1.001 | 0.001615
| 275.15 | 2100000 | 4203.5918 | 4203.2349 | 1000.944 | 0.0016692 | 2 | 20.7253 | 4.2036 | 4.2032 | 1.0009 | 0.0016692
| 274.15 | 2100000 | 4206.4341 | 4205.4502 | 1000.91 | 0.0017263 | 0.99999 | 20.7253 | 4.2064 | 4.2055 | 1.0009 | 0.0017263
| 273.15 | 2100000 | 4209.5435 | 4207.5942 | 1000.8588 | 0.0017865 | -6.1035e-06 | 20.7253 | 4.2095 | 4.2076 | 1.0009 | 0.0017865
| 473.15 | 2000000 | 4491.4014 | 3316.6611 | 865.0073 | 0.00013443 | 200 | 19.7384 | 4.4914 | 3.3167 | 0.86501 | 0.00013443
| 472.15 | 2000000 | 4486.2319 | 3320.4419 | 866.1941 | 0.00013515 | 199 | 19.7384 | 4.4862 | 3.3204 | 0.86619 | 0.00013515
| 471.15 | 2000000 | 4481.1392 | 3324.2402 | 867.3749 | 0.00013588 | 198 | 19.7384 | 4.4811 | 3.3242 | 0.86737 | 0.00013588
| 470.15 | 2000000 | 4476.1206 | 3328.0559 | 868.5499 | 0.00013661 | 197 | 19.7384 | 4.4761 | 3.3281 | 0.86855 | 0.00013661
| 469.15 | 2000000 | 4471.1763 | 3331.8892 | 869.7191 | 0.00013735 | 196 | 19.7384 | 4.4712 | 3.3319 | 0.86972 | 0.00013735
| 468.15 | 2000000 | 4466.3037 | 3335.7395 | 870.8825 | 0.0001381 | 195 | 19.7384 | 4.4663 | 3.3357 | 0.87088 | 0.0001381
| 467.15 | 2000000 | 4461.502 | 3339.6072 | 872.0402 | 0.00013886 | 194 | 19.7384 | 4.4615 | 3.3396 | 0.87204 | 0.00013886
| 466.15 | 2000000 | 4456.77 | 3343.4919 | 873.1923 | 0.00013962 | 193 | 19.7384 | 4.4568 | 3.3435 | 0.87319 | 0.00013962
| 465.15 | 2000000 | 4452.1064 | 3347.3933 | 874.3386 | 0.0001404 | 192 | 19.7384 | 4.4521 | 3.3474 | 0.87434 | 0.0001404
| 464.15 | 2000000 | 4447.5103 | 3351.3118 | 875.4795 | 0.00014118 | 191 | 19.7384 | 4.4475 | 3.3513 | 0.87548 | 0.00014118
| 463.15 | 2000000 | 4442.9805 | 3355.2466 | 876.6147 | 0.00014197 | 190 | 19.7384 | 4.443 | 3.3552 | 0.87661 | 0.00014197
| 462.15 | 2000000 | 4438.5151 | 3359.1982 | 877.7446 | 0.00014277 | 189 | 19.7384 | 4.4385 | 3.3592 | 0.87774 | 0.00014277
| 461.15 | 2000000 | 4434.1143 | 3363.1663 | 878.8689 | 0.00014358 | 188 | 19.7384 | 4.4341 | 3.3632 | 0.87887 | 0.00014358
| 460.15 | 2000000 | 4429.7759 | 3367.1504 | 879.9878 | 0.0001444 | 187 | 19.7384 | 4.4298 | 3.3672 | 0.87999 | 0.0001444
| 459.15 | 2000000 | 4425.499 | 3371.1509 | 881.1013 | 0.00014522 | 186 | 19.7384 | 4.4255 | 3.3712 | 0.8811 | 0.00014522
| 458.15 | 2000000 | 4421.2832 | 3375.1675 | 882.2095 | 0.00014606 | 185 | 19.7384 | 4.4213 | 3.3752 | 0.88221 | 0.00014606
| 457.15 | 2000000 | 4417.127 | 3379.2 | 883.3124 | 0.0001469 | 184 | 19.7384 | 4.4171 | 3.3792 | 0.88331 | 0.0001469
| 456.15 | 2000000 | 4413.0293 | 3383.2483 | 884.4101 | 0.00014776 | 183 | 19.7384 | 4.413 | 3.3832 | 0.88441 | 0.00014776
| 455.15 | 2000000 | 4408.9893 | 3387.3125 | 885.5025 | 0.00014862 | 182 | 19.7384 | 4.409 | 3.3873 | 0.8855 | 0.00014862
| 454.15 | 2000000 | 4405.0063 | 3391.3923 | 886.5898 | 0.0001495 | 181 | 19.7384 | 4.405 | 3.3914 | 0.88659 | 0.0001495
| 453.15 | 2000000 | 4401.0791 | 3395.4875 | 887.6718 | 0.00015039 | 180 | 19.7384 | 4.4011 | 3.3955 | 0.88767 | 0.00015039
| 452.15 | 2000000 | 4397.207 | 3399.5981 | 888.7488 | 0.00015128 | 179 | 19.7384 | 4.3972 | 3.3996 | 0.88875 | 0.00015128
| 451.15 | 2000000 | 4393.3887 | 3403.7241 | 889.8206 | 0.00015219 | 178 | 19.7384 | 4.3934 | 3.4037 | 0.88982 | 0.00015219
| 450.15 | 2000000 | 4389.624 | 3407.8652 | 890.8874 | 0.00015311 | 177 | 19.7384 | 4.3896 | 3.4079 | 0.89089 | 0.00015311
| 449.15 | 2000000 | 4385.9111 | 3412.0215 | 891.9492 | 0.00015404 | 176 | 19.7384 | 4.3859 | 3.412 | 0.89195 | 0.00015404
| 448.15 | 2000000 | 4382.25 | 3416.1926 | 893.0059 | 0.00015498 | 175 | 19.7384 | 4.3822 | 3.4162 | 0.89301 | 0.00015498
| 447.15 | 2000000 | 4378.6396 | 3420.3787 | 894.0576 | 0.00015593 | 174 | 19.7384 | 4.3786 | 3.4204 | 0.89406 | 0.00015593
| 446.15 | 2000000 | 4375.0791 | 3424.5796 | 895.1045 | 0.00015689 | 173 | 19.7384 | 4.3751 | 3.4246 | 0.8951 | 0.00015689
| 445.15 | 2000000 | 4371.5679 | 3428.7949 | 896.1464 | 0.00015787 | 172 | 19.7384 | 4.3716 | 3.4288 | 0.89615 | 0.00015787
| 444.15 | 2000000 | 4368.1045 | 3433.0249 | 897.1833 | 0.00015885 | 171 | 19.7384 | 4.3681 | 3.433 | 0.89718 | 0.00015885
| 443.15 | 2000000 | 4364.689 | 3437.2693 | 898.2155 | 0.00015985 | 170 | 19.7384 | 4.3647 | 3.4373 | 0.89822 | 0.00015985
| 442.15 | 2000000 | 4361.3203 | 3441.5281 | 899.2429 | 0.00016087 | 169 | 19.7384 | 4.3613 | 3.4415 | 0.89924 | 0.00016087
| 441.15 | 2000000 | 4357.998 | 3445.801 | 900.2653 | 0.00016189 | 168 | 19.7384 | 4.358 | 3.4458 | 0.90027 | 0.00016189
| 440.15 | 2000000 | 4354.7212 | 3450.0881 | 901.283 | 0.00016293 | 167 | 19.7384 | 4.3547 | 3.4501 | 0.90128 | 0.00016293
| 439.15 | 2000000 | 4351.4888 | 3454.3894 | 902.296 | 0.00016398 | 166 | 19.7384 | 4.3515 | 3.4544 | 0.9023 | 0.00016398
| 438.15 | 2000000 | 4348.3008 | 3458.7043 | 903.3041 | 0.00016505 | 165 | 19.7384 | 4.3483 | 3.4587 | 0.9033 | 0.00016505
| 437.15 | 2000000 | 4345.1558 | 3463.0334 | 904.3076 | 0.00016613 | 164 | 19.7384 | 4.3452 | 3.463 | 0.90431 | 0.00016613
| 436.15 | 2000000 | 4342.0542 | 3467.376 | 905.3063 | 0.00016722 | 163 | 19.7384 | 4.3421 | 3.4674 | 0.90531 | 0.00016722
| 435.15 | 2000000 | 4338.9941 | 3471.7324 | 906.3004 | 0.00016833 | 162 | 19.7384 | 4.339 | 3.4717 | 0.9063 | 0.00016833
| 434.15 | 2000000 | 4335.9761 | 3476.1021 | 907.2898 | 0.00016945 | 161 | 19.7384 | 4.336 | 3.4761 | 0.90729 | 0.00016945
| 433.15 | 2000000 | 4332.9985 | 3480.4854 | 908.2745 | 0.00017059 | 160 | 19.7384 | 4.333 | 3.4805 | 0.90827 | 0.00017059
| 432.15 | 2000000 | 4330.0615 | 3484.8821 | 909.2547 | 0.00017174 | 159 | 19.7384 | 4.3301 | 3.4849 | 0.90925 | 0.00017174
| 431.15 | 2000000 | 4327.1641 | 3489.292 | 910.2302 | 0.00017291 | 158 | 19.7384 | 4.3272 | 3.4893 | 0.91023 | 0.00017291
| 430.15 | 2000000 | 4324.3062 | 3493.7151 | 911.2012 | 0.00017409 | 157 | 19.7384 | 4.3243 | 3.4937 | 0.9112 | 0.00017409
| 429.15 | 2000000 | 4321.4863 | 3498.1514 | 912.1675 | 0.00017529 | 156 | 19.7384 | 4.3215 | 3.4982 | 0.91217 | 0.00017529
| 428.15 | 2000000 | 4318.7046 | 3502.6006 | 913.1293 | 0.00017651 | 155 | 19.7384 | 4.3187 | 3.5026 | 0.91313 | 0.00017651
| 427.15 | 2000000 | 4315.9609 | 3507.0627 | 914.0866 | 0.00017774 | 154 | 19.7384 | 4.316 | 3.5071 | 0.91409 | 0.00017774
| 426.15 | 2000000 | 4313.2534 | 3511.5376 | 915.0393 | 0.00017899 | 153 | 19.7384 | 4.3133 | 3.5115 | 0.91504 | 0.00017899
| 425.15 | 2000000 | 4310.583 | 3516.0254 | 915.9875 | 0.00018026 | 152 | 19.7384 | 4.3106 | 3.516 | 0.91599 | 0.00018026
| 424.15 | 2000000 | 4307.9482 | 3520.5256 | 916.9313 | 0.00018154 | 151 | 19.7384 | 4.3079 | 3.5205 | 0.91693 | 0.00018154
| 423.15 | 2000000 | 4305.3491 | 3525.0386 | 917.8705 | 0.00018285 | 150 | 19.7384 | 4.3053 | 3.525 | 0.91787 | 0.00018285
| 422.15 | 2000000 | 4302.7852 | 3529.564 | 918.8053 | 0.00018417 | 149 | 19.7384 | 4.3028 | 3.5296 | 0.91881 | 0.00018417
| 421.15 | 2000000 | 4300.2554 | 3534.1018 | 919.7356 | 0.00018551 | 148 | 19.7384 | 4.3003 | 3.5341 | 0.91974 | 0.00018551
| 420.15 | 2000000 | 4297.7593 | 3538.6521 | 920.6614 | 0.00018687 | 147 | 19.7384 | 4.2978 | 3.5387 | 0.92066 | 0.00018687
| 419.15 | 2000000 | 4295.2974 | 3543.2144 | 921.5829 | 0.00018825 | 146 | 19.7384 | 4.2953 | 3.5432 | 0.92158 | 0.00018825
| 418.15 | 2000000 | 4292.8682 | 3547.7891 | 922.4999 | 0.00018965 | 145 | 19.7384 | 4.2929 | 3.5478 | 0.9225 | 0.00018965
| 417.15 | 2000000 | 4290.4722 | 3552.3757 | 923.4124 | 0.00019107 | 144 | 19.7384 | 4.2905 | 3.5524 | 0.92341 | 0.00019107
| 416.15 | 2000000 | 4288.1079 | 3556.9744 | 924.3206 | 0.00019251 | 143 | 19.7384 | 4.2881 | 3.557 | 0.92432 | 0.00019251
| 415.15 | 2000000 | 4285.7759 | 3561.585 | 925.2244 | 0.00019397 | 142 | 19.7384 | 4.2858 | 3.5616 | 0.92522 | 0.00019397
| 414.15 | 2000000 | 4283.4751 | 3566.2075 | 926.1237 | 0.00019545 | 141 | 19.7384 | 4.2835 | 3.5662 | 0.92612 | 0.00019545
| 413.15 | 2000000 | 4281.2056 | 3570.8418 | 927.0187 | 0.00019696 | 140 | 19.7384 | 4.2812 | 3.5708 | 0.92702 | 0.00019696
| 412.15 | 2000000 | 4278.9663 | 3575.4875 | 927.9093 | 0.00019849 | 139 | 19.7384 | 4.279 | 3.5755 | 0.92791 | 0.00019849
| 411.15 | 2000000 | 4276.7573 | 3580.1453 | 928.7956 | 0.00020004 | 138 | 19.7384 | 4.2768 | 3.5801 | 0.9288 | 0.00020004
| 410.15 | 2000000 | 4274.5786 | 3584.8142 | 929.6774 | 0.00020162 | 137 | 19.7384 | 4.2746 | 3.5848 | 0.92968 | 0.00020162
| 409.15 | 2000000 | 4272.4292 | 3589.4949 | 930.5549 | 0.00020321 | 136 | 19.7384 | 4.2724 | 3.5895 | 0.93055 | 0.00020321
| 408.15 | 2000000 | 4270.3091 | 3594.1868 | 931.4281 | 0.00020484 | 135 | 19.7384 | 4.2703 | 3.5942 | 0.93143 | 0.00020484
| 407.15 | 2000000 | 4268.2178 | 3598.8901 | 932.2969 | 0.00020649 | 134 | 19.7384 | 4.2682 | 3.5989 | 0.9323 | 0.00020649
| 406.15 | 2000000 | 4266.1548 | 3603.6045 | 933.1614 | 0.00020816 | 133 | 19.7384 | 4.2662 | 3.6036 | 0.93316 | 0.00020816
| 405.15 | 2000000 | 4264.1201 | 3608.3303 | 934.0215 | 0.00020986 | 132 | 19.7384 | 4.2641 | 3.6083 | 0.93402 | 0.00020986
| 404.15 | 2000000 | 4262.1133 | 3613.0671 | 934.8773 | 0.00021159 | 131 | 19.7384 | 4.2621 | 3.6131 | 0.93488 | 0.00021159
| 403.15 | 2000000 | 4260.1338 | 3617.8147 | 935.7287 | 0.00021334 | 130 | 19.7384 | 4.2601 | 3.6178 | 0.93573 | 0.00021334
| 402.15 | 2000000 | 4258.1821 | 3622.5735 | 936.5758 | 0.00021513 | 129 | 19.7384 | 4.2582 | 3.6226 | 0.93658 | 0.00021513
| 401.15 | 2000000 | 4256.2568 | 3627.343 | 937.4185 | 0.00021694 | 128 | 19.7384 | 4.2563 | 3.6273 | 0.93742 | 0.00021694
| 400.15 | 2000000 | 4254.3579 | 3632.1233 | 938.257 | 0.00021878 | 127 | 19.7384 | 4.2544 | 3.6321 | 0.93826 | 0.00021878
| 399.15 | 2000000 | 4252.4858 | 3636.9143 | 939.0911 | 0.00022065 | 126 | 19.7384 | 4.2525 | 3.6369 | 0.93909 | 0.00022065
| 398.15 | 2000000 | 4250.6396 | 3641.7161 | 939.9208 | 0.00022255 | 125 | 19.7384 | 4.2506 | 3.6417 | 0.93992 | 0.00022255
| 397.15 | 2000000 | 4248.8193 | 3646.5281 | 940.7462 | 0.00022448 | 124 | 19.7384 | 4.2488 | 3.6465 | 0.94075 | 0.00022448
| 396.15 | 2000000 | 4247.0244 | 3651.3508 | 941.5673 | 0.00022644 | 123 | 19.7384 | 4.247 | 3.6514 | 0.94157 | 0.00022644
| 395.15 | 2000000 | 4245.2549 | 3656.1836 | 942.384 | 0.00022843 | 122 | 19.7384 | 4.2453 | 3.6562 | 0.94238 | 0.00022843
| 394.15 | 2000000 | 4243.5103 | 3661.0269 | 943.1964 | 0.00023046 | 121 | 19.7384 | 4.2435 | 3.661 | 0.9432 | 0.00023046
| 393.15 | 2000000 | 4241.79 | 3665.8801 | 944.0045 | 0.00023252 | 120 | 19.7384 | 4.2418 | 3.6659 | 0.944 | 0.00023252
| 392.15 | 2000000 | 4240.0952 | 3670.7437 | 944.8081 | 0.00023462 | 119 | 19.7384 | 4.2401 | 3.6707 | 0.94481 | 0.00023462
| 391.15 | 2000000 | 4238.4243 | 3675.6172 | 945.6075 | 0.00023675 | 118 | 19.7384 | 4.2384 | 3.6756 | 0.94561 | 0.00023675
| 390.15 | 2000000 | 4236.7773 | 3680.5005 | 946.4024 | 0.00023892 | 117 | 19.7384 | 4.2368 | 3.6805 | 0.9464 | 0.00023892
| 389.15 | 2000000 | 4235.1543 | 3685.3936 | 947.193 | 0.00024113 | 116 | 19.7384 | 4.2352 | 3.6854 | 0.94719 | 0.00024113
| 388.15 | 2000000 | 4233.5552 | 3690.2964 | 947.9792 | 0.00024337 | 115 | 19.7384 | 4.2336 | 3.6903 | 0.94798 | 0.00024337
| 387.15 | 2000000 | 4231.9795 | 3695.2087 | 948.7611 | 0.00024565 | 114 | 19.7384 | 4.232 | 3.6952 | 0.94876 | 0.00024565
| 386.15 | 2000000 | 4230.4268 | 3700.1306 | 949.5386 | 0.00024798 | 113 | 19.7384 | 4.2304 | 3.7001 | 0.94954 | 0.00024798
| 385.15 | 2000000 | 4228.8975 | 3705.062 | 950.3116 | 0.00025034 | 112 | 19.7384 | 4.2289 | 3.7051 | 0.95031 | 0.00025034
| 384.15 | 2000000 | 4227.3911 | 3710.0024 | 951.0803 | 0.00025275 | 111 | 19.7384 | 4.2274 | 3.71 | 0.95108 | 0.00025275
| 383.15 | 2000000 | 4225.9072 | 3714.9521 | 951.8445 | 0.00025519 | 110 | 19.7384 | 4.2259 | 3.715 | 0.95184 | 0.00025519
| 382.15 | 2000000 | 4224.4463 | 3719.9109 | 952.6044 | 0.00025768 | 109 | 19.7384 | 4.2244 | 3.7199 | 0.9526 | 0.00025768
| 381.15 | 2000000 | 4223.0078 | 3724.8784 | 953.3597 | 0.00026022 | 108 | 19.7384 | 4.223 | 3.7249 | 0.95336 | 0.00026022
| 380.15 | 2000000 | 4221.5913 | 3729.8547 | 954.1107 | 0.0002628 | 107 | 19.7384 | 4.2216 | 3.7299 | 0.95411 | 0.0002628
| 379.15 | 2000000 | 4220.1973 | 3734.8398 | 954.8572 | 0.00026543 | 106 | 19.7384 | 4.2202 | 3.7348 | 0.95486 | 0.00026543
| 378.15 | 2000000 | 4218.8252 | 3739.8333 | 955.5992 | 0.00026811 | 105 | 19.7384 | 4.2188 | 3.7398 | 0.9556 | 0.00026811
| 377.15 | 2000000 | 4217.4746 | 3744.835 | 956.3368 | 0.00027083 | 104 | 19.7384 | 4.2175 | 3.7448 | 0.95634 | 0.00027083
| 376.15 | 2000000 | 4216.146 | 3749.845 | 957.0699 | 0.00027361 | 103 | 19.7384 | 4.2161 | 3.7498 | 0.95707 | 0.00027361
| 375.15 | 2000000 | 4214.8389 | 3754.8628 | 957.7984 | 0.00027644 | 102 | 19.7384 | 4.2148 | 3.7549 | 0.9578 | 0.00027644
| 374.15 | 2000000 | 4213.5537 | 3759.8887 | 958.5225 | 0.00027932 | 101 | 19.7384 | 4.2136 | 3.7599 | 0.95852 | 0.00027932
| 373.15 | 2000000 | 4212.2896 | 3764.9221 | 959.2419 | 0.00028225 | 100 | 19.7384 | 4.2123 | 3.7649 | 0.95924 | 0.00028225
| 372.15 | 2000000 | 4211.0464 | 3769.9631 | 959.9569 | 0.00028524 | 99 | 19.7384 | 4.211 | 3.77 | 0.95996 | 0.00028524
| 371.15 | 2000000 | 4209.8247 | 3775.0115 | 960.6673 | 0.00028829 | 98 | 19.7384 | 4.2098 | 3.775 | 0.96067 | 0.00028829
| 370.15 | 2000000 | 4208.624 | 3780.0669 | 961.373 | 0.0002914 | 97 | 19.7384 | 4.2086 | 3.7801 | 0.96137 | 0.0002914
| 369.15 | 2000000 | 4207.4448 | 3785.1294 | 962.0743 | 0.00029457 | 96 | 19.7384 | 4.2074 | 3.7851 | 0.96207 | 0.00029457
| 368.15 | 2000000 | 4206.2856 | 3790.1985 | 962.7708 | 0.00029779 | 95 | 19.7384 | 4.2063 | 3.7902 | 0.96277 | 0.00029779
| 367.15 | 2000000 | 4205.1479 | 3795.2742 | 963.4628 | 0.00030109 | 94 | 19.7384 | 4.2051 | 3.7953 | 0.96346 | 0.00030109
| 366.15 | 2000000 | 4204.0308 | 3800.356 | 964.15 | 0.00030444 | 93 | 19.7384 | 4.204 | 3.8004 | 0.96415 | 0.00030444
| 365.15 | 2000000 | 4202.9341 | 3805.4438 | 964.8326 | 0.00030787 | 92 | 19.7384 | 4.2029 | 3.8054 | 0.96483 | 0.00030787
| 364.15 | 2000000 | 4201.8584 | 3810.5376 | 965.5105 | 0.00031136 | 91 | 19.7384 | 4.2019 | 3.8105 | 0.96551 | 0.00031136
| 363.15 | 2000000 | 4200.8032 | 3815.6367 | 966.1837 | 0.00031492 | 90 | 19.7384 | 4.2008 | 3.8156 | 0.96618 | 0.00031492
| 362.15 | 2000000 | 4199.7681 | 3820.7412 | 966.8521 | 0.00031855 | 89 | 19.7384 | 4.1998 | 3.8207 | 0.96685 | 0.00031855
| 361.15 | 2000000 | 4198.7539 | 3825.8506 | 967.5157 | 0.00032226 | 88 | 19.7384 | 4.1988 | 3.8259 | 0.96752 | 0.00032226
| 360.15 | 2000000 | 4197.7598 | 3830.9646 | 968.1745 | 0.00032605 | 87 | 19.7384 | 4.1978 | 3.831 | 0.96817 | 0.00032605
| 359.15 | 2000000 | 4196.7861 | 3836.083 | 968.8286 | 0.00032991 | 86 | 19.7384 | 4.1968 | 3.8361 | 0.96883 | 0.00032991
| 358.15 | 2000000 | 4195.833 | 3841.2056 | 969.4777 | 0.00033385 | 85 | 19.7384 | 4.1958 | 3.8412 | 0.96948 | 0.00033385
| 357.15 | 2000000 | 4194.8999 | 3846.3318 | 970.122 | 0.00033788 | 84 | 19.7384 | 4.1949 | 3.8463 | 0.97012 | 0.00033788
| 356.15 | 2000000 | 4193.9873 | 3851.4614 | 970.7614 | 0.00034199 | 83 | 19.7384 | 4.194 | 3.8515 | 0.97076 | 0.00034199
| 355.15 | 2000000 | 4193.0947 | 3856.594 | 971.3959 | 0.00034618 | 82 | 19.7384 | 4.1931 | 3.8566 | 0.9714 | 0.00034618
| 354.15 | 2000000 | 4192.2222 | 3861.7292 | 972.0254 | 0.00035047 | 81 | 19.7384 | 4.1922 | 3.8617 | 0.97203 | 0.00035047
| 353.15 | 2000000 | 4191.3701 | 3866.8669 | 972.6499 | 0.00035485 | 80 | 19.7384 | 4.1914 | 3.8669 | 0.97265 | 0.00035485
| 352.15 | 2000000 | 4190.5381 | 3872.0061 | 973.2693 | 0.00035933 | 79 | 19.7384 | 4.1905 | 3.872 | 0.97327 | 0.00035933
| 351.15 | 2000000 | 4189.7261 | 3877.147 | 973.8838 | 0.0003639 | 78 | 19.7384 | 4.1897 | 3.8771 | 0.97388 | 0.0003639
| 350.15 | 2000000 | 4188.9346 | 3882.2886 | 974.4932 | 0.00036857 | 77 | 19.7384 | 4.1889 | 3.8823 | 0.97449 | 0.00036857
| 349.15 | 2000000 | 4188.1626 | 3887.4309 | 975.0974 | 0.00037335 | 76 | 19.7384 | 4.1882 | 3.8874 | 0.9751 | 0.00037335
| 348.15 | 2000000 | 4187.4111 | 3892.5732 | 975.6965 | 0.00037823 | 75 | 19.7384 | 4.1874 | 3.8926 | 0.9757 | 0.00037823
| 347.15 | 2000000 | 4186.6797 | 3897.7151 | 976.2903 | 0.00038323 | 74 | 19.7384 | 4.1867 | 3.8977 | 0.97629 | 0.00038323
| 346.15 | 2000000 | 4185.9683 | 3902.856 | 976.879 | 0.00038834 | 73 | 19.7384 | 4.186 | 3.9029 | 0.97688 | 0.00038834
| 345.15 | 2000000 | 4185.2773 | 3907.9951 | 977.4623 | 0.00039356 | 72 | 19.7384 | 4.1853 | 3.908 | 0.97746 | 0.00039356
| 344.15 | 2000000 | 4184.606 | 3913.1323 | 978.0404 | 0.00039891 | 71 | 19.7384 | 4.1846 | 3.9131 | 0.97804 | 0.00039891
| 343.15 | 2000000 | 4183.9551 | 3918.2671 | 978.6132 | 0.00040437 | 70 | 19.7384 | 4.184 | 3.9183 | 0.97861 | 0.00040437
| 342.15 | 2000000 | 4183.3242 | 3923.3984 | 979.1805 | 0.00040997 | 69 | 19.7384 | 4.1833 | 3.9234 | 0.97918 | 0.00040997
| 341.15 | 2000000 | 4182.7134 | 3928.5259 | 979.7424 | 0.0004157 | 68 | 19.7384 | 4.1827 | 3.9285 | 0.97974 | 0.0004157
| 340.15 | 2000000 | 4182.123 | 3933.6487 | 980.2988 | 0.00042156 | 67 | 19.7384 | 4.1821 | 3.9336 | 0.9803 | 0.00042156
| 339.15 | 2000000 | 4181.5527 | 3938.7664 | 980.8498 | 0.00042757 | 66 | 19.7384 | 4.1816 | 3.9388 | 0.98085 | 0.00042757
| 338.15 | 2000000 | 4181.0024 | 3943.8782 | 981.3951 | 0.00043372 | 65 | 19.7384 | 4.181 | 3.9439 | 0.9814 | 0.00043372
| 337.15 | 2000000 | 4180.4722 | 3948.9834 | 981.9349 | 0.00044002 | 64 | 19.7384 | 4.1805 | 3.949 | 0.98193 | 0.00044002
| 336.15 | 2000000 | 4179.9624 | 3954.0813 | 982.4689 | 0.00044648 | 63 | 19.7384 | 4.18 | 3.9541 | 0.98247 | 0.00044648
| 335.15 | 2000000 | 4179.4727 | 3959.1709 | 982.9973 | 0.00045309 | 62 | 19.7384 | 4.1795 | 3.9592 | 0.983 | 0.00045309
| 334.15 | 2000000 | 4179.0029 | 3964.2515 | 983.5199 | 0.00045987 | 61 | 19.7384 | 4.179 | 3.9643 | 0.98352 | 0.00045987
| 333.15 | 2000000 | 4178.5537 | 3969.3223 | 984.0367 | 0.00046683 | 60 | 19.7384 | 4.1786 | 3.9693 | 0.98404 | 0.00046683
| 332.15 | 2000000 | 4178.125 | 3974.3826 | 984.5475 | 0.00047396 | 59 | 19.7384 | 4.1781 | 3.9744 | 0.98455 | 0.00047396
| 331.15 | 2000000 | 4177.7163 | 3979.4312 | 985.0526 | 0.00048127 | 58 | 19.7384 | 4.1777 | 3.9794 | 0.98505 | 0.00048127
| 330.15 | 2000000 | 4177.3281 | 3984.4673 | 985.5516 | 0.00048877 | 57 | 19.7384 | 4.1773 | 3.9845 | 0.98555 | 0.00048877
| 329.15 | 2000000 | 4176.96 | 3989.49 | 986.0445 | 0.00049647 | 56 | 19.7384 | 4.177 | 3.9895 | 0.98604 | 0.00049647
| 328.15 | 2000000 | 4176.6123 | 3994.4983 | 986.5313 | 0.00050437 | 55 | 19.7384 | 4.1766 | 3.9945 | 0.98653 | 0.00050437
| 327.15 | 2000000 | 4176.2856 | 3999.4912 | 987.012 | 0.00051248 | 54 | 19.7384 | 4.1763 | 3.9995 | 0.98701 | 0.00051248
| 326.15 | 2000000 | 4175.979 | 4004.4675 | 987.4865 | 0.00052081 | 53 | 19.7384 | 4.176 | 4.0045 | 0.98749 | 0.00052081
| 325.15 | 2000000 | 4175.6929 | 4009.4263 | 987.9546 | 0.00052936 | 52 | 19.7384 | 4.1757 | 4.0094 | 0.98795 | 0.00052936
| 324.15 | 2000000 | 4175.4272 | 4014.3665 | 988.4163 | 0.00053815 | 51 | 19.7384 | 4.1754 | 4.0144 | 0.98842 | 0.00053815
| 323.15 | 2000000 | 4175.1826 | 4019.2869 | 988.8716 | 0.00054718 | 50 | 19.7384 | 4.1752 | 4.0193 | 0.98887 | 0.00054718
| 322.15 | 2000000 | 4174.959 | 4024.186 | 989.3204 | 0.00055647 | 49 | 19.7384 | 4.175 | 4.0242 | 0.98932 | 0.00055647
| 321.15 | 2000000 | 4174.7559 | 4029.063 | 989.7627 | 0.00056601 | 48 | 19.7384 | 4.1748 | 4.0291 | 0.98976 | 0.00056601
| 320.15 | 2000000 | 4174.5737 | 4033.9167 | 990.1982 | 0.00057583 | 47 | 19.7384 | 4.1746 | 4.0339 | 0.9902 | 0.00057583
| 319.15 | 2000000 | 4174.4126 | 4038.7456 | 990.6271 | 0.00058593 | 46 | 19.7384 | 4.1744 | 4.0387 | 0.99063 | 0.00058593
| 318.15 | 2000000 | 4174.2725 | 4043.5483 | 991.049 | 0.00059632 | 45 | 19.7384 | 4.1743 | 4.0435 | 0.99105 | 0.00059632
| 317.15 | 2000000 | 4174.1543 | 4048.3235 | 991.4641 | 0.00060702 | 44 | 19.7384 | 4.1742 | 4.0483 | 0.99146 | 0.00060702
| 316.15 | 2000000 | 4174.0571 | 4053.0701 | 991.8722 | 0.00061804 | 43 | 19.7384 | 4.1741 | 4.0531 | 0.99187 | 0.00061804
| 315.15 | 2000000 | 4173.9819 | 4057.7864 | 992.2731 | 0.00062939 | 42 | 19.7384 | 4.174 | 4.0578 | 0.99227 | 0.00062939
| 314.15 | 2000000 | 4173.9287 | 4062.4709 | 992.6669 | 0.00064108 | 41 | 19.7384 | 4.1739 | 4.0625 | 0.99267 | 0.00064108
| 313.15 | 2000000 | 4173.8979 | 4067.1223 | 993.0535 | 0.00065313 | 40 | 19.7384 | 4.1739 | 4.0671 | 0.99305 | 0.00065313
| 312.15 | 2000000 | 4173.8896 | 4071.7393 | 993.4326 | 0.00066556 | 39 | 19.7384 | 4.1739 | 4.0717 | 0.99343 | 0.00066556
| 311.15 | 2000000 | 4173.9038 | 4076.3196 | 993.8043 | 0.00067837 | 38 | 19.7384 | 4.1739 | 4.0763 | 0.9938 | 0.00067837
| 310.15 | 2000000 | 4173.9414 | 4080.8625 | 994.1683 | 0.00069159 | 37 | 19.7384 | 4.1739 | 4.0809 | 0.99417 | 0.00069159
| 309.15 | 2000000 | 4174.0029 | 4085.3657 | 994.5247 | 0.00070524 | 36 | 19.7384 | 4.174 | 4.0854 | 0.99452 | 0.00070524
| 308.15 | 2000000 | 4174.0889 | 4089.8281 | 994.8733 | 0.00071933 | 35 | 19.7384 | 4.1741 | 4.0898 | 0.99487 | 0.00071933
| 307.15 | 2000000 | 4174.1992 | 4094.2478 | 995.2139 | 0.00073388 | 34 | 19.7384 | 4.1742 | 4.0942 | 0.99521 | 0.00073388
| 306.15 | 2000000 | 4174.335 | 4098.623 | 995.5466 | 0.00074892 | 33 | 19.7384 | 4.1743 | 4.0986 | 0.99555 | 0.00074892
| 305.15 | 2000000 | 4174.4971 | 4102.9526 | 995.871 | 0.00076446 | 32 | 19.7384 | 4.1745 | 4.103 | 0.99587 | 0.00076446
| 304.15 | 2000000 | 4174.686 | 4107.2344 | 996.1871 | 0.00078054 | 31 | 19.7384 | 4.1747 | 4.1072 | 0.99619 | 0.00078054
| 303.15 | 2000000 | 4174.9028 | 4111.4663 | 996.4948 | 0.00079717 | 30 | 19.7384 | 4.1749 | 4.1115 | 0.99649 | 0.00079717
| 302.15 | 2000000 | 4175.1489 | 4115.6475 | 996.7938 | 0.00081438 | 29 | 19.7384 | 4.1751 | 4.1156 | 0.99679 | 0.00081438
| 301.15 | 2000000 | 4175.4253 | 4119.7759 | 997.0842 | 0.0008322 | 28 | 19.7384 | 4.1754 | 4.1198 | 0.99708 | 0.0008322
| 300.15 | 2000000 | 4175.7329 | 4123.8491 | 997.3656 | 0.00085067 | 27 | 19.7384 | 4.1757 | 4.1238 | 0.99737 | 0.00085067
| 299.15 | 2000000 | 4176.0737 | 4127.8667 | 997.6381 | 0.0008698 | 26 | 19.7384 | 4.1761 | 4.1279 | 0.99764 | 0.0008698
| 298.15 | 2000000 | 4176.4497 | 4131.8257 | 997.9012 | 0.00088964 | 25 | 19.7384 | 4.1764 | 4.1318 | 0.9979 | 0.00088964
| 297.15 | 2000000 | 4176.8618 | 4135.7251 | 998.1551 | 0.00091023 | 24 | 19.7384 | 4.1769 | 4.1357 | 0.99816 | 0.00091023
| 296.15 | 2000000 | 4177.313 | 4139.563 | 998.3994 | 0.00093159 | 23 | 19.7384 | 4.1773 | 4.1396 | 0.9984 | 0.00093159
| 295.15 | 2000000 | 4177.8052 | 4143.3379 | 998.6339 | 0.00095378 | 22 | 19.7384 | 4.1778 | 4.1433 | 0.99863 | 0.00095378
| 294.15 | 2000000 | 4178.3418 | 4147.0479 | 998.8585 | 0.00097684 | 21 | 19.7384 | 4.1783 | 4.147 | 0.99886 | 0.00097684
| 293.15 | 2000000 | 4178.9248 | 4150.6919 | 999.0729 | 0.0010008 | 20 | 19.7384 | 4.1789 | 4.1507 | 0.99907 | 0.0010008
| 292.15 | 2000000 | 4179.5581 | 4154.2676 | 999.277 | 0.0010257 | 19 | 19.7384 | 4.1796 | 4.1543 | 0.99928 | 0.0010257
| 291.15 | 2000000 | 4180.2456 | 4157.7744 | 999.4705 | 0.0010517 | 18 | 19.7384 | 4.1802 | 4.1578 | 0.99947 | 0.0010517
| 290.15 | 2000000 | 4180.9917 | 4161.2104 | 999.6532 | 0.0010787 | 17 | 19.7384 | 4.181 | 4.1612 | 0.99965 | 0.0010787
| 289.15 | 2000000 | 4181.8003 | 4164.5747 | 999.8248 | 0.0011069 | 16 | 19.7384 | 4.1818 | 4.1646 | 0.99982 | 0.0011069
| 288.15 | 2000000 | 4182.6768 | 4167.8652 | 999.9851 | 0.0011362 | 15 | 19.7384 | 4.1827 | 4.1679 | 0.99999 | 0.0011362
| 287.15 | 2000000 | 4183.6274 | 4171.082 | 1000.1338 | 0.0011669 | 14 | 19.7384 | 4.1836 | 4.1711 | 1.0001 | 0.0011669
| 286.15 | 2000000 | 4184.6587 | 4174.2231 | 1000.2706 | 0.0011989 | 13 | 19.7384 | 4.1847 | 4.1742 | 1.0003 | 0.0011989
| 285.15 | 2000000 | 4185.7773 | 4177.2886 | 1000.3953 | 0.0012323 | 12 | 19.7384 | 4.1858 | 4.1773 | 1.0004 | 0.0012323
| 284.15 | 2000000 | 4186.9912 | 4180.2769 | 1000.5074 | 0.0012672 | 11 | 19.7384 | 4.187 | 4.1803 | 1.0005 | 0.0012672
| 283.15 | 2000000 | 4188.3096 | 4183.1875 | 1000.6068 | 0.0013038 | 10 | 19.7384 | 4.1883 | 4.1832 | 1.0006 | 0.0013038
| 282.15 | 2000000 | 4189.7422 | 4186.0205 | 1000.693 | 0.0013421 | 9 | 19.7384 | 4.1897 | 4.186 | 1.0007 | 0.0013421
| 281.15 | 2000000 | 4191.2998 | 4188.7759 | 1000.7657 | 0.0013823 | 8 | 19.7384 | 4.1913 | 4.1888 | 1.0008 | 0.0013823
| 280.15 | 2000000 | 4192.9951 | 4191.4531 | 1000.8244 | 0.0014244 | 7 | 19.7384 | 4.193 | 4.1915 | 1.0008 | 0.0014244
| 279.15 | 2000000 | 4194.8403 | 4194.0522 | 1000.8688 | 0.0014686 | 6 | 19.7384 | 4.1948 | 4.1941 | 1.0009 | 0.0014686
| 278.15 | 2000000 | 4196.8516 | 4196.5742 | 1000.8985 | 0.001515 | 5 | 19.7384 | 4.1969 | 4.1966 | 1.0009 | 0.001515
| 277.15 | 2000000 | 4199.0449 | 4199.02 | 1000.9129 | 0.0015638 | 4 | 19.7384 | 4.199 | 4.199 | 1.0009 | 0.0015638
| 276.15 | 2000000 | 4201.4385 | 4201.3901 | 1000.9116 | 0.0016152 | 3 | 19.7384 | 4.2014 | 4.2014 | 1.0009 | 0.0016152
| 275.15 | 2000000 | 4204.0522 | 4203.6855 | 1000.894 | 0.0016694 | 2 | 19.7384 | 4.2041 | 4.2037 | 1.0009 | 0.0016694
| 274.15 | 2000000 | 4206.9092 | 4205.9087 | 1000.8598 | 0.0017265 | 0.99999 | 19.7384 | 4.2069 | 4.2059 | 1.0009 | 0.0017265
| 273.15 | 2000000 | 4210.0337 | 4208.0605 | 1000.8081 | 0.0017868 | -6.1035e-06 | 19.7384 | 4.21 | 4.2081 | 1.0008 | 0.0017868
| 473.15 | 1900000 | 4491.9858 | 3316.7378 | 864.9312 | 0.00013441 | 200 | 18.7515 | 4.492 | 3.3167 | 0.86493 | 0.00013441
| 472.15 | 1900000 | 4486.8081 | 3320.5186 | 866.1184 | 0.00013513 | 199 | 18.7515 | 4.4868 | 3.3205 | 0.86612 | 0.00013513
| 471.15 | 1900000 | 4481.707 | 3324.3169 | 867.2998 | 0.00013585 | 198 | 18.7515 | 4.4817 | 3.3243 | 0.8673 | 0.00013585
| 470.15 | 1900000 | 4476.6807 | 3328.1326 | 868.4753 | 0.00013659 | 197 | 18.7515 | 4.4767 | 3.3281 | 0.86848 | 0.00013659
| 469.15 | 1900000 | 4471.728 | 3331.9658 | 869.645 | 0.00013733 | 196 | 18.7515 | 4.4717 | 3.332 | 0.86965 | 0.00013733
| 468.15 | 1900000 | 4466.8477 | 3335.8164 | 870.809 | 0.00013808 | 195 | 18.7515 | 4.4668 | 3.3358 | 0.87081 | 0.00013808
| 467.15 | 1900000 | 4462.0386 | 3339.6841 | 871.9672 | 0.00013883 | 194 | 18.7515 | 4.462 | 3.3397 | 0.87197 | 0.00013883
| 466.15 | 1900000 | 4457.2993 | 3343.5686 | 873.1197 | 0.0001396 | 193 | 18.7515 | 4.4573 | 3.3436 | 0.87312 | 0.0001396
| 465.15 | 1900000 | 4452.6284 | 3347.4702 | 874.2666 | 0.00014037 | 192 | 18.7515 | 4.4526 | 3.3475 | 0.87427 | 0.00014037
| 464.15 | 1900000 | 4448.0254 | 3351.3887 | 875.4079 | 0.00014115 | 191 | 18.7515 | 4.448 | 3.3514 | 0.87541 | 0.00014115
| 463.15 | 1900000 | 4443.4883 | 3355.3237 | 876.5436 | 0.00014195 | 190 | 18.7515 | 4.4435 | 3.3553 | 0.87654 | 0.00014195
| 462.15 | 1900000 | 4439.0166 | 3359.2754 | 877.674 | 0.00014275 | 189 | 18.7515 | 4.439 | 3.3593 | 0.87767 | 0.00014275
| 461.15 | 1900000 | 4434.6089 | 3363.2434 | 878.7987 | 0.00014355 | 188 | 18.7515 | 4.4346 | 3.3632 | 0.8788 | 0.00014355
| 460.15 | 1900000 | 4430.2637 | 3367.228 | 879.9181 | 0.00014437 | 187 | 18.7515 | 4.4303 | 3.3672 | 0.87992 | 0.00014437
| 459.15 | 1900000 | 4425.981 | 3371.2285 | 881.0321 | 0.0001452 | 186 | 18.7515 | 4.426 | 3.3712 | 0.88103 | 0.0001452
| 458.15 | 1900000 | 4421.7588 | 3375.2454 | 882.1407 | 0.00014603 | 185 | 18.7515 | 4.4218 | 3.3752 | 0.88214 | 0.00014603
| 457.15 | 1900000 | 4417.5962 | 3379.2781 | 883.2441 | 0.00014688 | 184 | 18.7515 | 4.4176 | 3.3793 | 0.88324 | 0.00014688
| 456.15 | 1900000 | 4413.4927 | 3383.3264 | 884.3422 | 0.00014773 | 183 | 18.7515 | 4.4135 | 3.3833 | 0.88434 | 0.00014773
| 455.15 | 1900000 | 4409.4468 | 3387.3909 | 885.4351 | 0.0001486 | 182 | 18.7515 | 4.4094 | 3.3874 | 0.88544 | 0.0001486
| 454.15 | 1900000 | 4405.458 | 3391.4707 | 886.5227 | 0.00014948 | 181 | 18.7515 | 4.4055 | 3.3915 | 0.88652 | 0.00014948
| 453.15 | 1900000 | 4401.5254 | 3395.5664 | 887.6052 | 0.00015036 | 180 | 18.7515 | 4.4015 | 3.3956 | 0.88761 | 0.00015036
| 452.15 | 1900000 | 4397.6475 | 3399.6772 | 888.6825 | 0.00015126 | 179 | 18.7515 | 4.3976 | 3.3997 | 0.88868 | 0.00015126
| 451.15 | 1900000 | 4393.8242 | 3403.8035 | 889.7548 | 0.00015216 | 178 | 18.7515 | 4.3938 | 3.4038 | 0.88975 | 0.00015216
| 450.15 | 1900000 | 4390.0537 | 3407.9448 | 890.822 | 0.00015308 | 177 | 18.7515 | 4.3901 | 3.4079 | 0.89082 | 0.00015308
| 449.15 | 1900000 | 4386.3359 | 3412.1013 | 891.8841 | 0.00015401 | 176 | 18.7515 | 4.3863 | 3.4121 | 0.89188 | 0.00015401
| 448.15 | 1900000 | 4382.6699 | 3416.2727 | 892.9412 | 0.00015495 | 175 | 18.7515 | 4.3827 | 3.4163 | 0.89294 | 0.00015495
| 447.15 | 1900000 | 4379.0542 | 3420.4592 | 893.9933 | 0.0001559 | 174 | 18.7515 | 4.3791 | 3.4205 | 0.89399 | 0.0001559
| 446.15 | 1900000 | 4375.4888 | 3424.6602 | 895.0405 | 0.00015687 | 173 | 18.7515 | 4.3755 | 3.4247 | 0.89504 | 0.00015687
| 445.15 | 1900000 | 4371.9727 | 3428.876 | 896.0828 | 0.00015784 | 172 | 18.7515 | 4.372 | 3.4289 | 0.89608 | 0.00015784
| 444.15 | 1900000 | 4368.5049 | 3433.1064 | 897.1202 | 0.00015883 | 171 | 18.7515 | 4.3685 | 3.4331 | 0.89712 | 0.00015883
| 443.15 | 1900000 | 4365.085 | 3437.3511 | 898.1527 | 0.00015983 | 170 | 18.7515 | 4.3651 | 3.4374 | 0.89815 | 0.00015983
| 442.15 | 1900000 | 4361.7119 | 3441.6104 | 899.1804 | 0.00016084 | 169 | 18.7515 | 4.3617 | 3.4416 | 0.89918 | 0.00016084
| 441.15 | 1900000 | 4358.3848 | 3445.8835 | 900.2032 | 0.00016187 | 168 | 18.7515 | 4.3584 | 3.4459 | 0.9002 | 0.00016187
| 440.15 | 1900000 | 4355.1035 | 3450.1711 | 901.2213 | 0.00016291 | 167 | 18.7515 | 4.3551 | 3.4502 | 0.90122 | 0.00016291
| 439.15 | 1900000 | 4351.8672 | 3454.4727 | 902.2345 | 0.00016396 | 166 | 18.7515 | 4.3519 | 3.4545 | 0.90223 | 0.00016396
| 438.15 | 1900000 | 4348.6748 | 3458.7883 | 903.243 | 0.00016502 | 165 | 18.7515 | 4.3487 | 3.4588 | 0.90324 | 0.00016502
| 437.15 | 1900000 | 4345.5259 | 3463.1177 | 904.2468 | 0.0001661 | 164 | 18.7515 | 4.3455 | 3.4631 | 0.90425 | 0.0001661
| 436.15 | 1900000 | 4342.4204 | 3467.4607 | 905.2459 | 0.00016719 | 163 | 18.7515 | 4.3424 | 3.4675 | 0.90525 | 0.00016719
| 435.15 | 1900000 | 4339.3564 | 3471.8174 | 906.2403 | 0.0001683 | 162 | 18.7515 | 4.3394 | 3.4718 | 0.90624 | 0.0001683
| 434.15 | 1900000 | 4336.3345 | 3476.1877 | 907.23 | 0.00016942 | 161 | 18.7515 | 4.3363 | 3.4762 | 0.90723 | 0.00016942
| 433.15 | 1900000 | 4333.353 | 3480.5715 | 908.2151 | 0.00017056 | 160 | 18.7515 | 4.3334 | 3.4806 | 0.90822 | 0.00017056
| 432.15 | 1900000 | 4330.4126 | 3484.9688 | 909.1956 | 0.00017171 | 159 | 18.7515 | 4.3304 | 3.485 | 0.9092 | 0.00017171
| 431.15 | 1900000 | 4327.5112 | 3489.3792 | 910.1714 | 0.00017288 | 158 | 18.7515 | 4.3275 | 3.4894 | 0.91017 | 0.00017288
| 430.15 | 1900000 | 4324.6499 | 3493.803 | 911.1426 | 0.00017407 | 157 | 18.7515 | 4.3246 | 3.4938 | 0.91114 | 0.00017407
| 429.15 | 1900000 | 4321.8267 | 3498.2397 | 912.1093 | 0.00017527 | 156 | 18.7515 | 4.3218 | 3.4982 | 0.91211 | 0.00017527
| 428.15 | 1900000 | 4319.0415 | 3502.6895 | 913.0714 | 0.00017648 | 155 | 18.7515 | 4.319 | 3.5027 | 0.91307 | 0.00017648
| 427.15 | 1900000 | 4316.2944 | 3507.1521 | 914.0289 | 0.00017771 | 154 | 18.7515 | 4.3163 | 3.5072 | 0.91403 | 0.00017771
| 426.15 | 1900000 | 4313.584 | 3511.6277 | 914.9819 | 0.00017896 | 153 | 18.7515 | 4.3136 | 3.5116 | 0.91498 | 0.00017896
| 425.15 | 1900000 | 4310.9102 | 3516.116 | 915.9305 | 0.00018023 | 152 | 18.7515 | 4.3109 | 3.5161 | 0.91593 | 0.00018023
| 424.15 | 1900000 | 4308.2725 | 3520.6169 | 916.8745 | 0.00018152 | 151 | 18.7515 | 4.3083 | 3.5206 | 0.91687 | 0.00018152
| 423.15 | 1900000 | 4305.6699 | 3525.1306 | 917.814 | 0.00018282 | 150 | 18.7515 | 4.3057 | 3.5251 | 0.91781 | 0.00018282
| 422.15 | 1900000 | 4303.1025 | 3529.6567 | 918.749 | 0.00018414 | 149 | 18.7515 | 4.3031 | 3.5297 | 0.91875 | 0.00018414
| 421.15 | 1900000 | 4300.5703 | 3534.1953 | 919.6796 | 0.00018548 | 148 | 18.7515 | 4.3006 | 3.5342 | 0.91968 | 0.00018548
| 420.15 | 1900000 | 4298.0713 | 3538.7461 | 920.6057 | 0.00018684 | 147 | 18.7515 | 4.2981 | 3.5387 | 0.92061 | 0.00018684
| 419.15 | 1900000 | 4295.6064 | 3543.3091 | 921.5274 | 0.00018822 | 146 | 18.7515 | 4.2956 | 3.5433 | 0.92153 | 0.00018822
| 418.15 | 1900000 | 4293.1748 | 3547.8845 | 922.4446 | 0.00018962 | 145 | 18.7515 | 4.2932 | 3.5479 | 0.92244 | 0.00018962
| 417.15 | 1900000 | 4290.7759 | 3552.4719 | 923.3575 | 0.00019104 | 144 | 18.7515 | 4.2908 | 3.5525 | 0.92336 | 0.00019104
| 416.15 | 1900000 | 4288.4092 | 3557.0713 | 924.2659 | 0.00019248 | 143 | 18.7515 | 4.2884 | 3.5571 | 0.92427 | 0.00019248
| 415.15 | 1900000 | 4286.0742 | 3561.6826 | 925.1699 | 0.00019394 | 142 | 18.7515 | 4.2861 | 3.5617 | 0.92517 | 0.00019394
| 414.15 | 1900000 | 4283.771 | 3566.3059 | 926.0695 | 0.00019543 | 141 | 18.7515 | 4.2838 | 3.5663 | 0.92607 | 0.00019543
| 413.15 | 1900000 | 4281.4985 | 3570.9409 | 926.9648 | 0.00019693 | 140 | 18.7515 | 4.2815 | 3.5709 | 0.92696 | 0.00019693
| 412.15 | 1900000 | 4279.2573 | 3575.5876 | 927.8556 | 0.00019846 | 139 | 18.7515 | 4.2793 | 3.5756 | 0.92786 | 0.00019846
| 411.15 | 1900000 | 4277.0459 | 3580.2461 | 928.7421 | 0.00020001 | 138 | 18.7515 | 4.277 | 3.5802 | 0.92874 | 0.00020001
| 410.15 | 1900000 | 4274.8647 | 3584.916 | 929.6242 | 0.00020159 | 137 | 18.7515 | 4.2749 | 3.5849 | 0.92962 | 0.00020159
| 409.15 | 1900000 | 4272.7129 | 3589.5977 | 930.502 | 0.00020319 | 136 | 18.7515 | 4.2727 | 3.5896 | 0.9305 | 0.00020319
| 408.15 | 1900000 | 4270.5903 | 3594.2905 | 931.3753 | 0.00020481 | 135 | 18.7515 | 4.2706 | 3.5943 | 0.93138 | 0.00020481
| 407.15 | 1900000 | 4268.4971 | 3598.9946 | 932.2443 | 0.00020646 | 134 | 18.7515 | 4.2685 | 3.599 | 0.93224 | 0.00020646
| 406.15 | 1900000 | 4266.4321 | 3603.71 | 933.109 | 0.00020814 | 133 | 18.7515 | 4.2664 | 3.6037 | 0.93311 | 0.00020814
| 405.15 | 1900000 | 4264.395 | 3608.4368 | 933.9694 | 0.00020984 | 132 | 18.7515 | 4.2644 | 3.6084 | 0.93397 | 0.00020984
| 404.15 | 1900000 | 4262.3862 | 3613.1743 | 934.8253 | 0.00021156 | 131 | 18.7515 | 4.2624 | 3.6132 | 0.93483 | 0.00021156
| 403.15 | 1900000 | 4260.4048 | 3617.9231 | 935.677 | 0.00021332 | 130 | 18.7515 | 4.2604 | 3.6179 | 0.93568 | 0.00021332
| 402.15 | 1900000 | 4258.4507 | 3622.6829 | 936.5243 | 0.0002151 | 129 | 18.7515 | 4.2585 | 3.6227 | 0.93652 | 0.0002151
| 401.15 | 1900000 | 4256.5234 | 3627.4534 | 937.3672 | 0.00021691 | 128 | 18.7515 | 4.2565 | 3.6275 | 0.93737 | 0.00021691
| 400.15 | 1900000 | 4254.623 | 3632.2346 | 938.2059 | 0.00021875 | 127 | 18.7515 | 4.2546 | 3.6322 | 0.93821 | 0.00021875
| 399.15 | 1900000 | 4252.749 | 3637.0269 | 939.0402 | 0.00022062 | 126 | 18.7515 | 4.2527 | 3.637 | 0.93904 | 0.00022062
| 398.15 | 1900000 | 4250.9009 | 3641.8293 | 939.8701 | 0.00022252 | 125 | 18.7515 | 4.2509 | 3.6418 | 0.93987 | 0.00022252
| 397.15 | 1900000 | 4249.0786 | 3646.6426 | 940.6957 | 0.00022445 | 124 | 18.7515 | 4.2491 | 3.6466 | 0.9407 | 0.00022445
| 396.15 | 1900000 | 4247.2822 | 3651.4663 | 941.517 | 0.00022641 | 123 | 18.7515 | 4.2473 | 3.6515 | 0.94152 | 0.00022641
| 395.15 | 1900000 | 4245.5107 | 3656.3003 | 942.3339 | 0.00022841 | 122 | 18.7515 | 4.2455 | 3.6563 | 0.94233 | 0.00022841
| 394.15 | 1900000 | 4243.7646 | 3661.1448 | 943.1465 | 0.00023044 | 121 | 18.7515 | 4.2438 | 3.6611 | 0.94315 | 0.00023044
| 393.15 | 1900000 | 4242.043 | 3665.9993 | 943.9547 | 0.0002325 | 120 | 18.7515 | 4.242 | 3.666 | 0.94395 | 0.0002325
| 392.15 | 1900000 | 4240.3462 | 3670.8638 | 944.7585 | 0.0002346 | 119 | 18.7515 | 4.2403 | 3.6709 | 0.94476 | 0.0002346
| 391.15 | 1900000 | 4238.6738 | 3675.7385 | 945.558 | 0.00023673 | 118 | 18.7515 | 4.2387 | 3.6757 | 0.94556 | 0.00023673
| 390.15 | 1900000 | 4237.0254 | 3680.623 | 946.3532 | 0.0002389 | 117 | 18.7515 | 4.237 | 3.6806 | 0.94635 | 0.0002389
| 389.15 | 1900000 | 4235.4009 | 3685.5173 | 947.144 | 0.0002411 | 116 | 18.7515 | 4.2354 | 3.6855 | 0.94714 | 0.0002411
| 388.15 | 1900000 | 4233.8003 | 3690.4214 | 947.9304 | 0.00024335 | 115 | 18.7515 | 4.2338 | 3.6904 | 0.94793 | 0.00024335
| 387.15 | 1900000 | 4232.2231 | 3695.3352 | 948.7124 | 0.00024563 | 114 | 18.7515 | 4.2322 | 3.6953 | 0.94871 | 0.00024563
| 386.15 | 1900000 | 4230.6694 | 3700.2583 | 949.49 | 0.00024795 | 113 | 18.7515 | 4.2307 | 3.7003 | 0.94949 | 0.00024795
| 385.15 | 1900000 | 4229.1387 | 3705.1909 | 950.2632 | 0.00025031 | 112 | 18.7515 | 4.2291 | 3.7052 | 0.95026 | 0.00025031
| 384.15 | 1900000 | 4227.6309 | 3710.1328 | 951.032 | 0.00025272 | 111 | 18.7515 | 4.2276 | 3.7101 | 0.95103 | 0.00025272
| 383.15 | 1900000 | 4226.146 | 3715.0837 | 951.7964 | 0.00025517 | 110 | 18.7515 | 4.2261 | 3.7151 | 0.9518 | 0.00025517
| 382.15 | 1900000 | 4224.6841 | 3720.0437 | 952.5565 | 0.00025766 | 109 | 18.7515 | 4.2247 | 3.72 | 0.95256 | 0.00025766
| 381.15 | 1900000 | 4223.2441 | 3725.0127 | 953.312 | 0.00026019 | 108 | 18.7515 | 4.2232 | 3.725 | 0.95331 | 0.00026019
| 380.15 | 1900000 | 4221.8267 | 3729.9905 | 954.0631 | 0.00026277 | 107 | 18.7515 | 4.2218 | 3.73 | 0.95406 | 0.00026277
| 379.15 | 1900000 | 4220.4312 | 3734.9768 | 954.8098 | 0.0002654 | 106 | 18.7515 | 4.2204 | 3.735 | 0.95481 | 0.0002654
| 378.15 | 1900000 | 4219.0581 | 3739.9717 | 955.5519 | 0.00026808 | 105 | 18.7515 | 4.2191 | 3.74 | 0.95555 | 0.00026808
| 377.15 | 1900000 | 4217.7065 | 3744.9749 | 956.2896 | 0.00027081 | 104 | 18.7515 | 4.2177 | 3.745 | 0.95629 | 0.00027081
| 376.15 | 1900000 | 4216.377 | 3749.9863 | 957.0228 | 0.00027358 | 103 | 18.7515 | 4.2164 | 3.75 | 0.95702 | 0.00027358
| 375.15 | 1900000 | 4215.0688 | 3755.0059 | 957.7515 | 0.00027641 | 102 | 18.7515 | 4.2151 | 3.755 | 0.95775 | 0.00027641
| 374.15 | 1900000 | 4213.7827 | 3760.0332 | 958.4757 | 0.00027929 | 101 | 18.7515 | 4.2138 | 3.76 | 0.95848 | 0.00027929
| 373.15 | 1900000 | 4212.5176 | 3765.0681 | 959.1953 | 0.00028223 | 100 | 18.7515 | 4.2125 | 3.7651 | 0.9592 | 0.00028223
| 372.15 | 1900000 | 4211.2739 | 3770.1108 | 959.9104 | 0.00028522 | 99 | 18.7515 | 4.2113 | 3.7701 | 0.95991 | 0.00028522
| 371.15 | 1900000 | 4210.0513 | 3775.1606 | 960.6209 | 0.00028827 | 98 | 18.7515 | 4.2101 | 3.7752 | 0.96062 | 0.00028827
| 370.15 | 1900000 | 4208.8501 | 3780.2178 | 961.3268 | 0.00029137 | 97 | 18.7515 | 4.2089 | 3.7802 | 0.96133 | 0.00029137
| 369.15 | 1900000 | 4207.6694 | 3785.2817 | 962.0281 | 0.00029454 | 96 | 18.7515 | 4.2077 | 3.7853 | 0.96203 | 0.00029454
| 368.15 | 1900000 | 4206.5103 | 3790.3525 | 962.7248 | 0.00029777 | 95 | 18.7515 | 4.2065 | 3.7904 | 0.96272 | 0.00029777
| 367.15 | 1900000 | 4205.3716 | 3795.4297 | 963.4169 | 0.00030106 | 94 | 18.7515 | 4.2054 | 3.7954 | 0.96342 | 0.00030106
| 366.15 | 1900000 | 4204.2534 | 3800.5134 | 964.1042 | 0.00030442 | 93 | 18.7515 | 4.2043 | 3.8005 | 0.9641 | 0.00030442
| 365.15 | 1900000 | 4203.1562 | 3805.603 | 964.7869 | 0.00030784 | 92 | 18.7515 | 4.2032 | 3.8056 | 0.96479 | 0.00030784
| 364.15 | 1900000 | 4202.0801 | 3810.6985 | 965.4649 | 0.00031133 | 91 | 18.7515 | 4.2021 | 3.8107 | 0.96546 | 0.00031133
| 363.15 | 1900000 | 4201.0239 | 3815.7993 | 966.1382 | 0.00031489 | 90 | 18.7515 | 4.201 | 3.8158 | 0.96614 | 0.00031489
| 362.15 | 1900000 | 4199.9888 | 3820.9055 | 966.8067 | 0.00031853 | 89 | 18.7515 | 4.2 | 3.8209 | 0.96681 | 0.00031853
| 361.15 | 1900000 | 4198.9736 | 3826.0168 | 967.4705 | 0.00032224 | 88 | 18.7515 | 4.199 | 3.826 | 0.96747 | 0.00032224
| 360.15 | 1900000 | 4197.9795 | 3831.1326 | 968.1294 | 0.00032602 | 87 | 18.7515 | 4.198 | 3.8311 | 0.96813 | 0.00032602
| 359.15 | 1900000 | 4197.0054 | 3836.2529 | 968.7835 | 0.00032988 | 86 | 18.7515 | 4.197 | 3.8363 | 0.96878 | 0.00032988
| 358.15 | 1900000 | 4196.0518 | 3841.3774 | 969.4327 | 0.00033382 | 85 | 18.7515 | 4.1961 | 3.8414 | 0.96943 | 0.00033382
| 357.15 | 1900000 | 4195.1182 | 3846.5056 | 970.0771 | 0.00033785 | 84 | 18.7515 | 4.1951 | 3.8465 | 0.97008 | 0.00033785
| 356.15 | 1900000 | 4194.2051 | 3851.637 | 970.7166 | 0.00034196 | 83 | 18.7515 | 4.1942 | 3.8516 | 0.97072 | 0.00034196
| 355.15 | 1900000 | 4193.3125 | 3856.7715 | 971.3512 | 0.00034616 | 82 | 18.7515 | 4.1933 | 3.8568 | 0.97135 | 0.00034616
| 354.15 | 1900000 | 4192.4395 | 3861.9087 | 971.9808 | 0.00035045 | 81 | 18.7515 | 4.1924 | 3.8619 | 0.97198 | 0.00035045
| 353.15 | 1900000 | 4191.5874 | 3867.0483 | 972.6053 | 0.00035483 | 80 | 18.7515 | 4.1916 | 3.867 | 0.97261 | 0.00035483
| 352.15 | 1900000 | 4190.7549 | 3872.1897 | 973.2249 | 0.0003593 | 79 | 18.7515 | 4.1908 | 3.8722 | 0.97322 | 0.0003593
| 351.15 | 1900000 | 4189.9429 | 3877.3325 | 973.8394 | 0.00036387 | 78 | 18.7515 | 4.1899 | 3.8773 | 0.97384 | 0.00036387
| 350.15 | 1900000 | 4189.1509 | 3882.4763 | 974.4489 | 0.00036855 | 77 | 18.7515 | 4.1892 | 3.8825 | 0.97445 | 0.00036855
| 349.15 | 1900000 | 4188.3794 | 3887.6206 | 975.0532 | 0.00037333 | 76 | 18.7515 | 4.1884 | 3.8876 | 0.97505 | 0.00037333
| 348.15 | 1900000 | 4187.6279 | 3892.7649 | 975.6523 | 0.00037821 | 75 | 18.7515 | 4.1876 | 3.8928 | 0.97565 | 0.00037821
| 347.15 | 1900000 | 4186.8965 | 3897.9089 | 976.2463 | 0.0003832 | 74 | 18.7515 | 4.1869 | 3.8979 | 0.97625 | 0.0003832
| 346.15 | 1900000 | 4186.1851 | 3903.052 | 976.835 | 0.00038831 | 73 | 18.7515 | 4.1862 | 3.9031 | 0.97683 | 0.00038831
| 345.15 | 1900000 | 4185.4941 | 3908.1934 | 977.4184 | 0.00039354 | 72 | 18.7515 | 4.1855 | 3.9082 | 0.97742 | 0.00039354
| 344.15 | 1900000 | 4184.8228 | 3913.3328 | 977.9965 | 0.00039888 | 71 | 18.7515 | 4.1848 | 3.9133 | 0.978 | 0.00039888
| 343.15 | 1900000 | 4184.1719 | 3918.4697 | 978.5693 | 0.00040435 | 70 | 18.7515 | 4.1842 | 3.9185 | 0.97857 | 0.00040435
| 342.15 | 1900000 | 4183.5415 | 3923.6033 | 979.1367 | 0.00040995 | 69 | 18.7515 | 4.1835 | 3.9236 | 0.97914 | 0.00040995
| 341.15 | 1900000 | 4182.9307 | 3928.7329 | 979.6987 | 0.00041567 | 68 | 18.7515 | 4.1829 | 3.9287 | 0.9797 | 0.00041567
| 340.15 | 1900000 | 4182.3403 | 3933.8582 | 980.2552 | 0.00042154 | 67 | 18.7515 | 4.1823 | 3.9339 | 0.98026 | 0.00042154
| 339.15 | 1900000 | 4181.7705 | 3938.9783 | 980.8062 | 0.00042755 | 66 | 18.7515 | 4.1818 | 3.939 | 0.98081 | 0.00042755
| 338.15 | 1900000 | 4181.2202 | 3944.0923 | 981.3515 | 0.0004337 | 65 | 18.7515 | 4.1812 | 3.9441 | 0.98135 | 0.0004337
| 337.15 | 1900000 | 4180.6909 | 3949.2 | 981.8913 | 0.00044 | 64 | 18.7515 | 4.1807 | 3.9492 | 0.98189 | 0.00044
| 336.15 | 1900000 | 4180.1812 | 3954.3 | 982.4254 | 0.00044645 | 63 | 18.7515 | 4.1802 | 3.9543 | 0.98243 | 0.00044645
| 335.15 | 1900000 | 4179.6919 | 3959.3921 | 982.9538 | 0.00045307 | 62 | 18.7515 | 4.1797 | 3.9594 | 0.98295 | 0.00045307
| 334.15 | 1900000 | 4179.2231 | 3964.4753 | 983.4764 | 0.00045985 | 61 | 18.7515 | 4.1792 | 3.9645 | 0.98348 | 0.00045985
| 333.15 | 1900000 | 4178.7744 | 3969.5486 | 983.9932 | 0.0004668 | 60 | 18.7515 | 4.1788 | 3.9695 | 0.98399 | 0.0004668
| 332.15 | 1900000 | 4178.3462 | 3974.6113 | 984.5042 | 0.00047393 | 59 | 18.7515 | 4.1783 | 3.9746 | 0.9845 | 0.00047393
| 331.15 | 1900000 | 4177.938 | 3979.6626 | 985.0092 | 0.00048125 | 58 | 18.7515 | 4.1779 | 3.9797 | 0.98501 | 0.00048125
| 330.15 | 1900000 | 4177.5503 | 3984.7012 | 985.5082 | 0.00048875 | 57 | 18.7515 | 4.1776 | 3.9847 | 0.98551 | 0.00048875
| 329.15 | 1900000 | 4177.1831 | 3989.7266 | 986.0012 | 0.00049645 | 56 | 18.7515 | 4.1772 | 3.9897 | 0.986 | 0.00049645
| 328.15 | 1900000 | 4176.8364 | 3994.7375 | 986.488 | 0.00050435 | 55 | 18.7515 | 4.1768 | 3.9947 | 0.98649 | 0.00050435
| 327.15 | 1900000 | 4176.5103 | 3999.7329 | 986.9687 | 0.00051246 | 54 | 18.7515 | 4.1765 | 3.9997 | 0.98697 | 0.00051246
| 326.15 | 1900000 | 4176.2046 | 4004.7122 | 987.4431 | 0.00052079 | 53 | 18.7515 | 4.1762 | 4.0047 | 0.98744 | 0.00052079
| 325.15 | 1900000 | 4175.9199 | 4009.6736 | 987.9113 | 0.00052934 | 52 | 18.7515 | 4.1759 | 4.0097 | 0.98791 | 0.00052934
| 324.15 | 1900000 | 4175.6553 | 4014.6165 | 988.373 | 0.00053813 | 51 | 18.7515 | 4.1757 | 4.0146 | 0.98837 | 0.00053813
| 323.15 | 1900000 | 4175.4116 | 4019.5396 | 988.8283 | 0.00054716 | 50 | 18.7515 | 4.1754 | 4.0195 | 0.98883 | 0.00054716
| 322.15 | 1900000 | 4175.189 | 4024.4417 | 989.2771 | 0.00055645 | 49 | 18.7515 | 4.1752 | 4.0244 | 0.98928 | 0.00055645
| 321.15 | 1900000 | 4174.9868 | 4029.3215 | 989.7194 | 0.000566 | 48 | 18.7515 | 4.175 | 4.0293 | 0.98972 | 0.000566
| 320.15 | 1900000 | 4174.8062 | 4034.178 | 990.1548 | 0.00057581 | 47 | 18.7515 | 4.1748 | 4.0342 | 0.99015 | 0.00057581
| 319.15 | 1900000 | 4174.6465 | 4039.0095 | 990.5837 | 0.00058592 | 46 | 18.7515 | 4.1746 | 4.039 | 0.99058 | 0.00058592
| 318.15 | 1900000 | 4174.5083 | 4043.8152 | 991.0056 | 0.00059631 | 45 | 18.7515 | 4.1745 | 4.0438 | 0.99101 | 0.00059631
| 317.15 | 1900000 | 4174.3911 | 4048.5935 | 991.4207 | 0.00060701 | 44 | 18.7515 | 4.1744 | 4.0486 | 0.99142 | 0.00060701
| 316.15 | 1900000 | 4174.2959 | 4053.343 | 991.8287 | 0.00061803 | 43 | 18.7515 | 4.1743 | 4.0533 | 0.99183 | 0.00061803
| 315.15 | 1900000 | 4174.2222 | 4058.0623 | 992.2296 | 0.00062938 | 42 | 18.7515 | 4.1742 | 4.0581 | 0.99223 | 0.00062938
| 314.15 | 1900000 | 4174.1709 | 4062.75 | 992.6234 | 0.00064107 | 41 | 18.7515 | 4.1742 | 4.0628 | 0.99262 | 0.00064107
| 313.15 | 1900000 | 4174.1416 | 4067.4045 | 993.0099 | 0.00065312 | 40 | 18.7515 | 4.1741 | 4.0674 | 0.99301 | 0.00065312
| 312.15 | 1900000 | 4174.1353 | 4072.0244 | 993.389 | 0.00066555 | 39 | 18.7515 | 4.1741 | 4.072 | 0.99339 | 0.00066555
| 311.15 | 1900000 | 4174.1514 | 4076.6079 | 993.7606 | 0.00067837 | 38 | 18.7515 | 4.1742 | 4.0766 | 0.99376 | 0.00067837
| 310.15 | 1900000 | 4174.1914 | 4081.1541 | 994.1246 | 0.00069159 | 37 | 18.7515 | 4.1742 | 4.0812 | 0.99412 | 0.00069159
| 309.15 | 1900000 | 4174.2549 | 4085.6606 | 994.4809 | 0.00070524 | 36 | 18.7515 | 4.1743 | 4.0857 | 0.99448 | 0.00070524
| 308.15 | 1900000 | 4174.3428 | 4090.1262 | 994.8294 | 0.00071933 | 35 | 18.7515 | 4.1743 | 4.0901 | 0.99483 | 0.00071933
| 307.15 | 1900000 | 4174.4561 | 4094.5493 | 995.17 | 0.00073388 | 34 | 18.7515 | 4.1745 | 4.0945 | 0.99517 | 0.00073388
| 306.15 | 1900000 | 4174.5942 | 4098.9277 | 995.5025 | 0.00074892 | 33 | 18.7515 | 4.1746 | 4.0989 | 0.9955 | 0.00074892
| 305.15 | 1900000 | 4174.7588 | 4103.2607 | 995.8268 | 0.00076447 | 32 | 18.7515 | 4.1748 | 4.1033 | 0.99583 | 0.00076447
| 304.15 | 1900000 | 4174.9507 | 4107.5459 | 996.1429 | 0.00078055 | 31 | 18.7515 | 4.175 | 4.1075 | 0.99614 | 0.00078055
| 303.15 | 1900000 | 4175.1709 | 4111.7817 | 996.4504 | 0.00079718 | 30 | 18.7515 | 4.1752 | 4.1118 | 0.99645 | 0.00079718
| 302.15 | 1900000 | 4175.4199 | 4115.9663 | 996.7494 | 0.00081439 | 29 | 18.7515 | 4.1754 | 4.116 | 0.99675 | 0.00081439
| 301.15 | 1900000 | 4175.6997 | 4120.0981 | 997.0397 | 0.00083222 | 28 | 18.7515 | 4.1757 | 4.1201 | 0.99704 | 0.00083222
| 300.15 | 1900000 | 4176.0107 | 4124.1753 | 997.321 | 0.00085068 | 27 | 18.7515 | 4.176 | 4.1242 | 0.99732 | 0.00085068
| 299.15 | 1900000 | 4176.355 | 4128.1963 | 997.5933 | 0.00086982 | 26 | 18.7515 | 4.1764 | 4.1282 | 0.99759 | 0.00086982
| 298.15 | 1900000 | 4176.7344 | 4132.1592 | 997.8564 | 0.00088967 | 25 | 18.7515 | 4.1767 | 4.1322 | 0.99786 | 0.00088967
| 297.15 | 1900000 | 4177.1509 | 4136.062 | 998.1101 | 0.00091025 | 24 | 18.7515 | 4.1772 | 4.1361 | 0.99811 | 0.00091025
| 296.15 | 1900000 | 4177.606 | 4139.9043 | 998.3542 | 0.00093162 | 23 | 18.7515 | 4.1776 | 4.1399 | 0.99835 | 0.00093162
| 295.15 | 1900000 | 4178.103 | 4143.6831 | 998.5886 | 0.00095381 | 22 | 18.7515 | 4.1781 | 4.1437 | 0.99859 | 0.00095381
| 294.15 | 1900000 | 4178.6436 | 4147.397 | 998.8131 | 0.00097687 | 21 | 18.7515 | 4.1786 | 4.1474 | 0.99881 | 0.00097687
| 293.15 | 1900000 | 4179.2319 | 4151.0449 | 999.0273 | 0.0010008 | 20 | 18.7515 | 4.1792 | 4.151 | 0.99903 | 0.0010008
| 292.15 | 1900000 | 4179.8706 | 4154.6255 | 999.2313 | 0.0010258 | 19 | 18.7515 | 4.1799 | 4.1546 | 0.99923 | 0.0010258
| 291.15 | 1900000 | 4180.5635 | 4158.1362 | 999.4246 | 0.0010517 | 18 | 18.7515 | 4.1806 | 4.1581 | 0.99942 | 0.0010517
| 290.15 | 1900000 | 4181.3149 | 4161.5767 | 999.6071 | 0.0010788 | 17 | 18.7515 | 4.1813 | 4.1616 | 0.99961 | 0.0010788
| 289.15 | 1900000 | 4182.1294 | 4164.9453 | 999.7785 | 0.0011069 | 16 | 18.7515 | 4.1821 | 4.1649 | 0.99978 | 0.0011069
| 288.15 | 1900000 | 4183.0122 | 4168.2407 | 999.9386 | 0.0011363 | 15 | 18.7515 | 4.183 | 4.1682 | 0.99994 | 0.0011363
| 287.15 | 1900000 | 4183.9697 | 4171.4624 | 1000.0872 | 0.0011669 | 14 | 18.7515 | 4.184 | 4.1715 | 1.0001 | 0.0011669
| 286.15 | 1900000 | 4185.0078 | 4174.6084 | 1000.2238 | 0.0011989 | 13 | 18.7515 | 4.185 | 4.1746 | 1.0002 | 0.0011989
| 285.15 | 1900000 | 4186.1338 | 4177.6787 | 1000.3482 | 0.0012324 | 12 | 18.7515 | 4.1861 | 4.1777 | 1.0003 | 0.0012324
| 284.15 | 1900000 | 4187.356 | 4180.6724 | 1000.4601 | 0.0012673 | 11 | 18.7515 | 4.1874 | 4.1807 | 1.0005 | 0.0012673
| 283.15 | 1900000 | 4188.6826 | 4183.5884 | 1000.5593 | 0.0013039 | 10 | 18.7515 | 4.1887 | 4.1836 | 1.0006 | 0.0013039
| 282.15 | 1900000 | 4190.124 | 4186.4272 | 1000.6452 | 0.0013422 | 9 | 18.7515 | 4.1901 | 4.1864 | 1.0006 | 0.0013422
| 281.15 | 1900000 | 4191.6909 | 4189.188 | 1000.7176 | 0.0013824 | 8 | 18.7515 | 4.1917 | 4.1892 | 1.0007 | 0.0013824
| 280.15 | 1900000 | 4193.396 | 4191.8711 | 1000.7761 | 0.0014245 | 7 | 18.7515 | 4.1934 | 4.1919 | 1.0008 | 0.0014245
| 279.15 | 1900000 | 4195.252 | 4194.4766 | 1000.8201 | 0.0014687 | 6 | 18.7515 | 4.1953 | 4.1945 | 1.0008 | 0.0014687
| 278.15 | 1900000 | 4197.2744 | 4197.0049 | 1000.8495 | 0.0015152 | 5 | 18.7515 | 4.1973 | 4.197 | 1.0008 | 0.0015152
| 277.15 | 1900000 | 4199.4795 | 4199.457 | 1000.8636 | 0.001564 | 4 | 18.7515 | 4.1995 | 4.1995 | 1.0009 | 0.001564
| 276.15 | 1900000 | 4201.8857 | 4201.834 | 1000.862 | 0.0016154 | 3 | 18.7515 | 4.2019 | 4.2018 | 1.0009 | 0.0016154
| 275.15 | 1900000 | 4204.5132 | 4204.1367 | 1000.8441 | 0.0016696 | 2 | 18.7515 | 4.2045 | 4.2041 | 1.0008 | 0.0016696
| 274.15 | 1900000 | 4207.3843 | 4206.3672 | 1000.8095 | 0.0017267 | 0.99999 | 18.7515 | 4.2074 | 4.2064 | 1.0008 | 0.0017267
| 273.15 | 1900000 | 4210.5244 | 4208.5269 | 1000.7574 | 0.001787 | -6.1035e-06 | 18.7515 | 4.2105 | 4.2085 | 1.0008 | 0.001787
| 473.15 | 1800000 | 4492.5713 | 3316.8145 | 864.8549 | 0.00013438 | 200 | 17.7646 | 4.4926 | 3.3168 | 0.86485 | 0.00013438
| 472.15 | 1800000 | 4487.3848 | 3320.5952 | 866.0427 | 0.0001351 | 199 | 17.7646 | 4.4874 | 3.3206 | 0.86604 | 0.0001351
| 471.15 | 1800000 | 4482.2754 | 3324.3936 | 867.2246 | 0.00013583 | 198 | 17.7646 | 4.4823 | 3.3244 | 0.86722 | 0.00013583
| 470.15 | 1800000 | 4477.2412 | 3328.2095 | 868.4007 | 0.00013656 | 197 | 17.7646 | 4.4772 | 3.3282 | 0.8684 | 0.00013656
| 469.15 | 1800000 | 4472.2803 | 3332.0427 | 869.5709 | 0.0001373 | 196 | 17.7646 | 4.4723 | 3.332 | 0.86957 | 0.0001373
| 468.15 | 1800000 | 4467.3926 | 3335.8931 | 870.7354 | 0.00013805 | 195 | 17.7646 | 4.4674 | 3.3359 | 0.87074 | 0.00013805
| 467.15 | 1800000 | 4462.5757 | 3339.761 | 871.894 | 0.00013881 | 194 | 17.7646 | 4.4626 | 3.3398 | 0.87189 | 0.00013881
| 466.15 | 1800000 | 4457.8291 | 3343.6458 | 873.0471 | 0.00013957 | 193 | 17.7646 | 4.4578 | 3.3436 | 0.87305 | 0.00013957
| 465.15 | 1800000 | 4453.1514 | 3347.5474 | 874.1945 | 0.00014035 | 192 | 17.7646 | 4.4532 | 3.3475 | 0.87419 | 0.00014035
| 464.15 | 1800000 | 4448.541 | 3351.4658 | 875.3363 | 0.00014113 | 191 | 17.7646 | 4.4485 | 3.3515 | 0.87534 | 0.00014113
| 463.15 | 1800000 | 4443.9971 | 3355.4009 | 876.4725 | 0.00014192 | 190 | 17.7646 | 4.444 | 3.3554 | 0.87647 | 0.00014192
| 462.15 | 1800000 | 4439.5181 | 3359.3528 | 877.6033 | 0.00014272 | 189 | 17.7646 | 4.4395 | 3.3594 | 0.8776 | 0.00014272
| 461.15 | 1800000 | 4435.104 | 3363.321 | 878.7285 | 0.00014353 | 188 | 17.7646 | 4.4351 | 3.3633 | 0.87873 | 0.00014353
| 460.15 | 1800000 | 4430.7524 | 3367.3054 | 879.8484 | 0.00014435 | 187 | 17.7646 | 4.4308 | 3.3673 | 0.87985 | 0.00014435
| 459.15 | 1800000 | 4426.4629 | 3371.3062 | 880.9628 | 0.00014517 | 186 | 17.7646 | 4.4265 | 3.3713 | 0.88096 | 0.00014517
| 458.15 | 1800000 | 4422.2344 | 3375.3232 | 882.0719 | 0.00014601 | 185 | 17.7646 | 4.4222 | 3.3753 | 0.88207 | 0.00014601
| 457.15 | 1800000 | 4418.0659 | 3379.356 | 883.1757 | 0.00014685 | 184 | 17.7646 | 4.4181 | 3.3794 | 0.88318 | 0.00014685
| 456.15 | 1800000 | 4413.9565 | 3383.4048 | 884.2742 | 0.00014771 | 183 | 17.7646 | 4.414 | 3.3834 | 0.88427 | 0.00014771
| 455.15 | 1800000 | 4409.9048 | 3387.4692 | 885.3675 | 0.00014858 | 182 | 17.7646 | 4.4099 | 3.3875 | 0.88537 | 0.00014858
| 454.15 | 1800000 | 4405.9106 | 3391.5496 | 886.4556 | 0.00014945 | 181 | 17.7646 | 4.4059 | 3.3915 | 0.88646 | 0.00014945
| 453.15 | 1800000 | 4401.9722 | 3395.6453 | 887.5385 | 0.00015034 | 180 | 17.7646 | 4.402 | 3.3956 | 0.88754 | 0.00015034
| 452.15 | 1800000 | 4398.0889 | 3399.7563 | 888.6162 | 0.00015123 | 179 | 17.7646 | 4.3981 | 3.3998 | 0.88862 | 0.00015123
| 451.15 | 1800000 | 4394.2598 | 3403.8828 | 889.6888 | 0.00015214 | 178 | 17.7646 | 4.3943 | 3.4039 | 0.88969 | 0.00015214
| 450.15 | 1800000 | 4390.4844 | 3408.0244 | 890.7565 | 0.00015306 | 177 | 17.7646 | 4.3905 | 3.408 | 0.89076 | 0.00015306
| 449.15 | 1800000 | 4386.7612 | 3412.1812 | 891.819 | 0.00015399 | 176 | 17.7646 | 4.3868 | 3.4122 | 0.89182 | 0.00015399
| 448.15 | 1800000 | 4383.0898 | 3416.353 | 892.8765 | 0.00015493 | 175 | 17.7646 | 4.3831 | 3.4164 | 0.89288 | 0.00015493
| 447.15 | 1800000 | 4379.4692 | 3420.5396 | 893.929 | 0.00015588 | 174 | 17.7646 | 4.3795 | 3.4205 | 0.89393 | 0.00015588
| 446.15 | 1800000 | 4375.8989 | 3424.741 | 894.9766 | 0.00015684 | 173 | 17.7646 | 4.3759 | 3.4247 | 0.89498 | 0.00015684
| 445.15 | 1800000 | 4372.3784 | 3428.957 | 896.0192 | 0.00015782 | 172 | 17.7646 | 4.3724 | 3.429 | 0.89602 | 0.00015782
| 444.15 | 1800000 | 4368.9058 | 3433.1877 | 897.057 | 0.0001588 | 171 | 17.7646 | 4.3689 | 3.4332 | 0.89706 | 0.0001588
| 443.15 | 1800000 | 4365.481 | 3437.4329 | 898.0898 | 0.0001598 | 170 | 17.7646 | 4.3655 | 3.4374 | 0.89809 | 0.0001598
| 442.15 | 1800000 | 4362.1035 | 3441.6924 | 899.1179 | 0.00016082 | 169 | 17.7646 | 4.3621 | 3.4417 | 0.89912 | 0.00016082
| 441.15 | 1800000 | 4358.7725 | 3445.9663 | 900.1411 | 0.00016184 | 168 | 17.7646 | 4.3588 | 3.446 | 0.90014 | 0.00016184
| 440.15 | 1800000 | 4355.4868 | 3450.2542 | 901.1595 | 0.00016288 | 167 | 17.7646 | 4.3555 | 3.4503 | 0.90116 | 0.00016288
| 439.15 | 1800000 | 4352.2461 | 3454.5562 | 902.1731 | 0.00016393 | 166 | 17.7646 | 4.3522 | 3.4546 | 0.90217 | 0.00016393
| 438.15 | 1800000 | 4349.0493 | 3458.8721 | 903.1819 | 0.000165 | 165 | 17.7646 | 4.349 | 3.4589 | 0.90318 | 0.000165
| 437.15 | 1800000 | 4345.8965 | 3463.2019 | 904.186 | 0.00016608 | 164 | 17.7646 | 4.3459 | 3.4632 | 0.90419 | 0.00016608
| 436.15 | 1800000 | 4342.7866 | 3467.5454 | 905.1855 | 0.00016717 | 163 | 17.7646 | 4.3428 | 3.4675 | 0.90519 | 0.00016717
| 435.15 | 1800000 | 4339.7192 | 3471.9026 | 906.1802 | 0.00016828 | 162 | 17.7646 | 4.3397 | 3.4719 | 0.90618 | 0.00016828
| 434.15 | 1800000 | 4336.6929 | 3476.2734 | 907.1702 | 0.0001694 | 161 | 17.7646 | 4.3367 | 3.4763 | 0.90717 | 0.0001694
| 433.15 | 1800000 | 4333.708 | 3480.6577 | 908.1556 | 0.00017054 | 160 | 17.7646 | 4.3337 | 3.4807 | 0.90816 | 0.00017054
| 432.15 | 1800000 | 4330.7637 | 3485.0554 | 909.1364 | 0.00017169 | 159 | 17.7646 | 4.3308 | 3.4851 | 0.90914 | 0.00017169
| 431.15 | 1800000 | 4327.8594 | 3489.4663 | 910.1125 | 0.00017286 | 158 | 17.7646 | 4.3279 | 3.4895 | 0.91011 | 0.00017286
| 430.15 | 1800000 | 4324.9937 | 3493.8906 | 911.084 | 0.00017404 | 157 | 17.7646 | 4.325 | 3.4939 | 0.91108 | 0.00017404
| 429.15 | 1800000 | 4322.1675 | 3498.3279 | 912.051 | 0.00017524 | 156 | 17.7646 | 4.3222 | 3.4983 | 0.91205 | 0.00017524
| 428.15 | 1800000 | 4319.3789 | 3502.7783 | 913.0134 | 0.00017646 | 155 | 17.7646 | 4.3194 | 3.5028 | 0.91301 | 0.00017646
| 427.15 | 1800000 | 4316.6284 | 3507.2417 | 913.9713 | 0.00017769 | 154 | 17.7646 | 4.3166 | 3.5072 | 0.91397 | 0.00017769
| 426.15 | 1800000 | 4313.9146 | 3511.7178 | 914.9246 | 0.00017894 | 153 | 17.7646 | 4.3139 | 3.5117 | 0.91492 | 0.00017894
| 425.15 | 1800000 | 4311.2373 | 3516.2068 | 915.8734 | 0.00018021 | 152 | 17.7646 | 4.3112 | 3.5162 | 0.91587 | 0.00018021
| 424.15 | 1800000 | 4308.5967 | 3520.7083 | 916.8176 | 0.00018149 | 151 | 17.7646 | 4.3086 | 3.5207 | 0.91682 | 0.00018149
| 423.15 | 1800000 | 4305.9912 | 3525.2227 | 917.7574 | 0.0001828 | 150 | 17.7646 | 4.306 | 3.5252 | 0.91776 | 0.0001828
| 422.15 | 1800000 | 4303.4209 | 3529.7493 | 918.6927 | 0.00018412 | 149 | 17.7646 | 4.3034 | 3.5297 | 0.91869 | 0.00018412
| 421.15 | 1800000 | 4300.8853 | 3534.2886 | 919.6236 | 0.00018546 | 148 | 17.7646 | 4.3009 | 3.5343 | 0.91962 | 0.00018546
| 420.15 | 1800000 | 4298.3838 | 3538.8401 | 920.55 | 0.00018682 | 147 | 17.7646 | 4.2984 | 3.5388 | 0.92055 | 0.00018682
| 419.15 | 1800000 | 4295.916 | 3543.4038 | 921.4719 | 0.0001882 | 146 | 17.7646 | 4.2959 | 3.5434 | 0.92147 | 0.0001882
| 418.15 | 1800000 | 4293.4814 | 3547.98 | 922.3895 | 0.0001896 | 145 | 17.7646 | 4.2935 | 3.548 | 0.92239 | 0.0001896
| 417.15 | 1800000 | 4291.0796 | 3552.5681 | 923.3026 | 0.00019102 | 144 | 17.7646 | 4.2911 | 3.5526 | 0.9233 | 0.00019102
| 416.15 | 1800000 | 4288.71 | 3557.1682 | 924.2112 | 0.00019246 | 143 | 17.7646 | 4.2887 | 3.5572 | 0.92421 | 0.00019246
| 415.15 | 1800000 | 4286.3726 | 3561.7805 | 925.1155 | 0.00019392 | 142 | 17.7646 | 4.2864 | 3.5618 | 0.92512 | 0.00019392
| 414.15 | 1800000 | 4284.0669 | 3566.4045 | 926.0153 | 0.0001954 | 141 | 17.7646 | 4.2841 | 3.5664 | 0.92602 | 0.0001954
| 413.15 | 1800000 | 4281.792 | 3571.0403 | 926.9108 | 0.00019691 | 140 | 17.7646 | 4.2818 | 3.571 | 0.92691 | 0.00019691
| 412.15 | 1800000 | 4279.5483 | 3575.688 | 927.8019 | 0.00019844 | 139 | 17.7646 | 4.2795 | 3.5757 | 0.9278 | 0.00019844
| 411.15 | 1800000 | 4277.3345 | 3580.3472 | 928.6886 | 0.00019999 | 138 | 17.7646 | 4.2773 | 3.5803 | 0.92869 | 0.00019999
| 410.15 | 1800000 | 4275.1509 | 3585.0181 | 929.5709 | 0.00020156 | 137 | 17.7646 | 4.2752 | 3.585 | 0.92957 | 0.00020156
| 409.15 | 1800000 | 4272.9971 | 3589.7002 | 930.4489 | 0.00020316 | 136 | 17.7646 | 4.273 | 3.5897 | 0.93045 | 0.00020316
| 408.15 | 1800000 | 4270.8721 | 3594.394 | 931.3225 | 0.00020479 | 135 | 17.7646 | 4.2709 | 3.5944 | 0.93132 | 0.00020479
| 407.15 | 1800000 | 4268.7764 | 3599.0991 | 932.1918 | 0.00020643 | 134 | 17.7646 | 4.2688 | 3.5991 | 0.93219 | 0.00020643
| 406.15 | 1800000 | 4266.7095 | 3603.8154 | 933.0566 | 0.00020811 | 133 | 17.7646 | 4.2667 | 3.6038 | 0.93306 | 0.00020811
| 405.15 | 1800000 | 4264.6704 | 3608.543 | 933.9172 | 0.00020981 | 132 | 17.7646 | 4.2647 | 3.6085 | 0.93392 | 0.00020981
| 404.15 | 1800000 | 4262.6592 | 3613.2817 | 934.7734 | 0.00021154 | 131 | 17.7646 | 4.2627 | 3.6133 | 0.93477 | 0.00021154
| 403.15 | 1800000 | 4260.6758 | 3618.0315 | 935.6252 | 0.00021329 | 130 | 17.7646 | 4.2607 | 3.618 | 0.93563 | 0.00021329
| 402.15 | 1800000 | 4258.7197 | 3622.7922 | 936.4728 | 0.00021507 | 129 | 17.7646 | 4.2587 | 3.6228 | 0.93647 | 0.00021507
| 401.15 | 1800000 | 4256.7905 | 3627.5637 | 937.3159 | 0.00021688 | 128 | 17.7646 | 4.2568 | 3.6276 | 0.93732 | 0.00021688
| 400.15 | 1800000 | 4254.8882 | 3632.3462 | 938.1548 | 0.00021872 | 127 | 17.7646 | 4.2549 | 3.6323 | 0.93815 | 0.00021872
| 399.15 | 1800000 | 4253.0122 | 3637.1392 | 938.9893 | 0.00022059 | 126 | 17.7646 | 4.253 | 3.6371 | 0.93899 | 0.00022059
| 398.15 | 1800000 | 4251.1621 | 3641.9429 | 939.8194 | 0.00022249 | 125 | 17.7646 | 4.2512 | 3.6419 | 0.93982 | 0.00022249
| 397.15 | 1800000 | 4249.3384 | 3646.7573 | 940.6452 | 0.00022442 | 124 | 17.7646 | 4.2493 | 3.6468 | 0.94065 | 0.00022442
| 396.15 | 1800000 | 4247.54 | 3651.582 | 941.4666 | 0.00022639 | 123 | 17.7646 | 4.2475 | 3.6516 | 0.94147 | 0.00022639
| 395.15 | 1800000 | 4245.7671 | 3656.4172 | 942.2838 | 0.00022838 | 122 | 17.7646 | 4.2458 | 3.6564 | 0.94228 | 0.00022838
| 394.15 | 1800000 | 4244.019 | 3661.2627 | 943.0965 | 0.00023041 | 121 | 17.7646 | 4.244 | 3.6613 | 0.9431 | 0.00023041
| 393.15 | 1800000 | 4242.2959 | 3666.1182 | 943.9049 | 0.00023247 | 120 | 17.7646 | 4.2423 | 3.6661 | 0.9439 | 0.00023247
| 392.15 | 1800000 | 4240.5977 | 3670.9841 | 944.709 | 0.00023457 | 119 | 17.7646 | 4.2406 | 3.671 | 0.94471 | 0.00023457
| 391.15 | 1800000 | 4238.9233 | 3675.8599 | 945.5087 | 0.0002367 | 118 | 17.7646 | 4.2389 | 3.6759 | 0.94551 | 0.0002367
| 390.15 | 1800000 | 4237.2739 | 3680.7456 | 946.304 | 0.00023887 | 117 | 17.7646 | 4.2373 | 3.6807 | 0.9463 | 0.00023887
| 389.15 | 1800000 | 4235.6479 | 3685.6411 | 947.0949 | 0.00024108 | 116 | 17.7646 | 4.2356 | 3.6856 | 0.94709 | 0.00024108
| 388.15 | 1800000 | 4234.0459 | 3690.5466 | 947.8815 | 0.00024332 | 115 | 17.7646 | 4.234 | 3.6905 | 0.94788 | 0.00024332
| 387.15 | 1800000 | 4232.4673 | 3695.4614 | 948.6636 | 0.0002456 | 114 | 17.7646 | 4.2325 | 3.6955 | 0.94866 | 0.0002456
| 386.15 | 1800000 | 4230.9121 | 3700.386 | 949.4415 | 0.00024792 | 113 | 17.7646 | 4.2309 | 3.7004 | 0.94944 | 0.00024792
| 385.15 | 1800000 | 4229.3799 | 3705.3198 | 950.2148 | 0.00025029 | 112 | 17.7646 | 4.2294 | 3.7053 | 0.95021 | 0.00025029
| 384.15 | 1800000 | 4227.8711 | 3710.2629 | 950.9838 | 0.00025269 | 111 | 17.7646 | 4.2279 | 3.7103 | 0.95098 | 0.00025269
| 383.15 | 1800000 | 4226.3848 | 3715.2153 | 951.7484 | 0.00025514 | 110 | 17.7646 | 4.2264 | 3.7152 | 0.95175 | 0.00025514
| 382.15 | 1800000 | 4224.9214 | 3720.1768 | 952.5085 | 0.00025763 | 109 | 17.7646 | 4.2249 | 3.7202 | 0.95251 | 0.00025763
| 381.15 | 1800000 | 4223.4805 | 3725.147 | 953.2642 | 0.00026017 | 108 | 17.7646 | 4.2235 | 3.7251 | 0.95326 | 0.00026017
| 380.15 | 1800000 | 4222.062 | 3730.1262 | 954.0155 | 0.00026275 | 107 | 17.7646 | 4.2221 | 3.7301 | 0.95402 | 0.00026275
| 379.15 | 1800000 | 4220.6655 | 3735.114 | 954.7623 | 0.00026538 | 106 | 17.7646 | 4.2207 | 3.7351 | 0.95476 | 0.00026538
| 378.15 | 1800000 | 4219.291 | 3740.1104 | 955.5046 | 0.00026805 | 105 | 17.7646 | 4.2193 | 3.7401 | 0.9555 | 0.00026805
| 377.15 | 1800000 | 4217.939 | 3745.115 | 956.2424 | 0.00027078 | 104 | 17.7646 | 4.2179 | 3.7451 | 0.95624 | 0.00027078
| 376.15 | 1800000 | 4216.6079 | 3750.1279 | 956.9758 | 0.00027356 | 103 | 17.7646 | 4.2166 | 3.7501 | 0.95698 | 0.00027356
| 375.15 | 1800000 | 4215.2993 | 3755.1489 | 957.7046 | 0.00027638 | 102 | 17.7646 | 4.2153 | 3.7551 | 0.9577 | 0.00027638
| 374.15 | 1800000 | 4214.0117 | 3760.1777 | 958.4289 | 0.00027926 | 101 | 17.7646 | 4.214 | 3.7602 | 0.95843 | 0.00027926
| 373.15 | 1800000 | 4212.7461 | 3765.2144 | 959.1487 | 0.0002822 | 100 | 17.7646 | 4.2127 | 3.7652 | 0.95915 | 0.0002822
| 372.15 | 1800000 | 4211.5015 | 3770.2583 | 959.8639 | 0.00028519 | 99 | 17.7646 | 4.2115 | 3.7703 | 0.95986 | 0.00028519
| 371.15 | 1800000 | 4210.2778 | 3775.3098 | 960.5745 | 0.00028824 | 98 | 17.7646 | 4.2103 | 3.7753 | 0.96057 | 0.00028824
| 370.15 | 1800000 | 4209.0757 | 3780.3687 | 961.2806 | 0.00029135 | 97 | 17.7646 | 4.2091 | 3.7804 | 0.96128 | 0.00029135
| 369.15 | 1800000 | 4207.8945 | 3785.4343 | 961.982 | 0.00029451 | 96 | 17.7646 | 4.2079 | 3.7854 | 0.96198 | 0.00029451
| 368.15 | 1800000 | 4206.7344 | 3790.5066 | 962.6788 | 0.00029774 | 95 | 17.7646 | 4.2067 | 3.7905 | 0.96268 | 0.00029774
| 367.15 | 1800000 | 4205.5952 | 3795.5854 | 963.371 | 0.00030103 | 94 | 17.7646 | 4.2056 | 3.7956 | 0.96337 | 0.00030103
| 366.15 | 1800000 | 4204.4766 | 3800.6709 | 964.0585 | 0.00030439 | 93 | 17.7646 | 4.2045 | 3.8007 | 0.96406 | 0.00030439
| 365.15 | 1800000 | 4203.3789 | 3805.7622 | 964.7413 | 0.00030781 | 92 | 17.7646 | 4.2034 | 3.8058 | 0.96474 | 0.00030781
| 364.15 | 1800000 | 4202.3018 | 3810.8594 | 965.4194 | 0.0003113 | 91 | 17.7646 | 4.2023 | 3.8109 | 0.96542 | 0.0003113
| 363.15 | 1800000 | 4201.2451 | 3815.9619 | 966.0927 | 0.00031487 | 90 | 17.7646 | 4.2012 | 3.816 | 0.96609 | 0.00031487
| 362.15 | 1800000 | 4200.2095 | 3821.0701 | 966.7614 | 0.0003185 | 89 | 17.7646 | 4.2002 | 3.8211 | 0.96676 | 0.0003185
| 361.15 | 1800000 | 4199.1938 | 3826.1831 | 967.4252 | 0.00032221 | 88 | 17.7646 | 4.1992 | 3.8262 | 0.96743 | 0.00032221
| 360.15 | 1800000 | 4198.1992 | 3831.3008 | 968.0842 | 0.00032599 | 87 | 17.7646 | 4.1982 | 3.8313 | 0.96808 | 0.00032599
| 359.15 | 1800000 | 4197.2246 | 3836.4229 | 968.7385 | 0.00032986 | 86 | 17.7646 | 4.1972 | 3.8364 | 0.96874 | 0.00032986
| 358.15 | 1800000 | 4196.2705 | 3841.5491 | 969.3878 | 0.0003338 | 85 | 17.7646 | 4.1963 | 3.8415 | 0.96939 | 0.0003338
| 357.15 | 1800000 | 4195.3369 | 3846.6792 | 970.0323 | 0.00033782 | 84 | 17.7646 | 4.1953 | 3.8467 | 0.97003 | 0.00033782
| 356.15 | 1800000 | 4194.4233 | 3851.8127 | 970.6719 | 0.00034193 | 83 | 17.7646 | 4.1944 | 3.8518 | 0.97067 | 0.00034193
| 355.15 | 1800000 | 4193.5303 | 3856.9492 | 971.3065 | 0.00034613 | 82 | 17.7646 | 4.1935 | 3.8569 | 0.97131 | 0.00034613
| 354.15 | 1800000 | 4192.6572 | 3862.0884 | 971.9362 | 0.00035042 | 81 | 17.7646 | 4.1927 | 3.8621 | 0.97194 | 0.00035042
| 353.15 | 1800000 | 4191.8047 | 3867.2297 | 972.5609 | 0.0003548 | 80 | 17.7646 | 4.1918 | 3.8672 | 0.97256 | 0.0003548
| 352.15 | 1800000 | 4190.9722 | 3872.373 | 973.1805 | 0.00035927 | 79 | 17.7646 | 4.191 | 3.8724 | 0.97318 | 0.00035927
| 351.15 | 1800000 | 4190.1602 | 3877.5181 | 973.7951 | 0.00036385 | 78 | 17.7646 | 4.1902 | 3.8775 | 0.9738 | 0.00036385
| 350.15 | 1800000 | 4189.3682 | 3882.6638 | 974.4046 | 0.00036852 | 77 | 17.7646 | 4.1894 | 3.8827 | 0.9744 | 0.00036852
| 349.15 | 1800000 | 4188.5962 | 3887.8103 | 975.009 | 0.0003733 | 76 | 17.7646 | 4.1886 | 3.8878 | 0.97501 | 0.0003733
| 348.15 | 1800000 | 4187.8447 | 3892.9568 | 975.6082 | 0.00037818 | 75 | 17.7646 | 4.1878 | 3.893 | 0.97561 | 0.00037818
| 347.15 | 1800000 | 4187.1133 | 3898.1028 | 976.2021 | 0.00038318 | 74 | 17.7646 | 4.1871 | 3.8981 | 0.9762 | 0.00038318
| 346.15 | 1800000 | 4186.4019 | 3903.248 | 976.791 | 0.00038829 | 73 | 17.7646 | 4.1864 | 3.9032 | 0.97679 | 0.00038829
| 345.15 | 1800000 | 4185.7109 | 3908.3916 | 977.3745 | 0.00039351 | 72 | 17.7646 | 4.1857 | 3.9084 | 0.97737 | 0.00039351
| 344.15 | 1800000 | 4185.04 | 3913.5332 | 977.9526 | 0.00039885 | 71 | 17.7646 | 4.185 | 3.9135 | 0.97795 | 0.00039885
| 343.15 | 1800000 | 4184.3892 | 3918.6724 | 978.5255 | 0.00040432 | 70 | 17.7646 | 4.1844 | 3.9187 | 0.97853 | 0.00040432
| 342.15 | 1800000 | 4183.7588 | 3923.8081 | 979.093 | 0.00040992 | 69 | 17.7646 | 4.1838 | 3.9238 | 0.97909 | 0.00040992
| 341.15 | 1800000 | 4183.1484 | 3928.9402 | 979.655 | 0.00041565 | 68 | 17.7646 | 4.1831 | 3.9289 | 0.97965 | 0.00041565
| 340.15 | 1800000 | 4182.5581 | 3934.0679 | 980.2115 | 0.00042152 | 67 | 17.7646 | 4.1826 | 3.9341 | 0.98021 | 0.00042152
| 339.15 | 1800000 | 4181.9883 | 3939.1902 | 980.7625 | 0.00042752 | 66 | 17.7646 | 4.182 | 3.9392 | 0.98076 | 0.00042752
| 338.15 | 1800000 | 4181.439 | 3944.3066 | 981.3079 | 0.00043367 | 65 | 17.7646 | 4.1814 | 3.9443 | 0.98131 | 0.00043367
| 337.15 | 1800000 | 4180.9097 | 3949.4165 | 981.8477 | 0.00043997 | 64 | 17.7646 | 4.1809 | 3.9494 | 0.98185 | 0.00043997
| 336.15 | 1800000 | 4180.4004 | 3954.5193 | 982.3819 | 0.00044643 | 63 | 17.7646 | 4.1804 | 3.9545 | 0.98238 | 0.00044643
| 335.15 | 1800000 | 4179.9116 | 3959.6138 | 982.9103 | 0.00045305 | 62 | 17.7646 | 4.1799 | 3.9596 | 0.98291 | 0.00045305
| 334.15 | 1800000 | 4179.4434 | 3964.6992 | 983.433 | 0.00045983 | 61 | 17.7646 | 4.1794 | 3.9647 | 0.98343 | 0.00045983
| 333.15 | 1800000 | 4178.9951 | 3969.7751 | 983.9498 | 0.00046678 | 60 | 17.7646 | 4.179 | 3.9698 | 0.98395 | 0.00046678
| 332.15 | 1800000 | 4178.5674 | 3974.8403 | 984.4608 | 0.00047391 | 59 | 17.7646 | 4.1786 | 3.9748 | 0.98446 | 0.00047391
| 331.15 | 1800000 | 4178.1602 | 3979.894 | 984.9658 | 0.00048122 | 58 | 17.7646 | 4.1782 | 3.9799 | 0.98497 | 0.00048122
| 330.15 | 1800000 | 4177.7729 | 3984.9353 | 985.4648 | 0.00048873 | 57 | 17.7646 | 4.1778 | 3.9849 | 0.98546 | 0.00048873
| 329.15 | 1800000 | 4177.4067 | 3989.9631 | 985.9578 | 0.00049643 | 56 | 17.7646 | 4.1774 | 3.99 | 0.98596 | 0.00049643
| 328.15 | 1800000 | 4177.061 | 3994.9768 | 986.4446 | 0.00050433 | 55 | 17.7646 | 4.1771 | 3.995 | 0.98644 | 0.00050433
| 327.15 | 1800000 | 4176.7354 | 3999.9749 | 986.9254 | 0.00051244 | 54 | 17.7646 | 4.1767 | 4 | 0.98693 | 0.00051244
| 326.15 | 1800000 | 4176.4307 | 4004.9568 | 987.3998 | 0.00052077 | 53 | 17.7646 | 4.1764 | 4.005 | 0.9874 | 0.00052077
| 325.15 | 1800000 | 4176.1465 | 4009.9209 | 987.8679 | 0.00052932 | 52 | 17.7646 | 4.1761 | 4.0099 | 0.98787 | 0.00052932
| 324.15 | 1800000 | 4175.8833 | 4014.8665 | 988.3297 | 0.00053811 | 51 | 17.7646 | 4.1759 | 4.0149 | 0.98833 | 0.00053811
| 323.15 | 1800000 | 4175.6406 | 4019.7922 | 988.785 | 0.00054715 | 50 | 17.7646 | 4.1756 | 4.0198 | 0.98878 | 0.00054715
| 322.15 | 1800000 | 4175.4189 | 4024.6973 | 989.2338 | 0.00055643 | 49 | 17.7646 | 4.1754 | 4.0247 | 0.98923 | 0.00055643
| 321.15 | 1800000 | 4175.2188 | 4029.5798 | 989.676 | 0.00056598 | 48 | 17.7646 | 4.1752 | 4.0296 | 0.98968 | 0.00056598
| 320.15 | 1800000 | 4175.0391 | 4034.4392 | 990.1115 | 0.0005758 | 47 | 17.7646 | 4.175 | 4.0344 | 0.99011 | 0.0005758
| 319.15 | 1800000 | 4174.8809 | 4039.2739 | 990.5403 | 0.0005859 | 46 | 17.7646 | 4.1749 | 4.0393 | 0.99054 | 0.0005859
| 318.15 | 1800000 | 4174.7437 | 4044.0823 | 990.9622 | 0.0005963 | 45 | 17.7646 | 4.1747 | 4.0441 | 0.99096 | 0.0005963
| 317.15 | 1800000 | 4174.6279 | 4048.8635 | 991.3772 | 0.000607 | 44 | 17.7646 | 4.1746 | 4.0489 | 0.99138 | 0.000607
| 316.15 | 1800000 | 4174.5342 | 4053.616 | 991.7852 | 0.00061802 | 43 | 17.7646 | 4.1745 | 4.0536 | 0.99179 | 0.00061802
| 315.15 | 1800000 | 4174.4624 | 4058.3384 | 992.1862 | 0.00062937 | 42 | 17.7646 | 4.1745 | 4.0583 | 0.99219 | 0.00062937
| 314.15 | 1800000 | 4174.4126 | 4063.0291 | 992.5798 | 0.00064106 | 41 | 17.7646 | 4.1744 | 4.063 | 0.99258 | 0.00064106
| 313.15 | 1800000 | 4174.3853 | 4067.6868 | 992.9662 | 0.00065312 | 40 | 17.7646 | 4.1744 | 4.0677 | 0.99297 | 0.00065312
| 312.15 | 1800000 | 4174.3809 | 4072.3096 | 993.3453 | 0.00066554 | 39 | 17.7646 | 4.1744 | 4.0723 | 0.99335 | 0.00066554
| 311.15 | 1800000 | 4174.3994 | 4076.8965 | 993.7169 | 0.00067836 | 38 | 17.7646 | 4.1744 | 4.0769 | 0.99372 | 0.00067836
| 310.15 | 1800000 | 4174.4414 | 4081.4456 | 994.0808 | 0.00069158 | 37 | 17.7646 | 4.1744 | 4.0814 | 0.99408 | 0.00069158
| 309.15 | 1800000 | 4174.5073 | 4085.9556 | 994.4371 | 0.00070523 | 36 | 17.7646 | 4.1745 | 4.086 | 0.99444 | 0.00070523
| 308.15 | 1800000 | 4174.5977 | 4090.4243 | 994.7855 | 0.00071933 | 35 | 17.7646 | 4.1746 | 4.0904 | 0.99479 | 0.00071933
| 307.15 | 1800000 | 4174.7129 | 4094.8508 | 995.126 | 0.00073388 | 34 | 17.7646 | 4.1747 | 4.0949 | 0.99513 | 0.00073388
| 306.15 | 1800000 | 4174.854 | 4099.2329 | 995.4584 | 0.00074893 | 33 | 17.7646 | 4.1749 | 4.0992 | 0.99546 | 0.00074893
| 305.15 | 1800000 | 4175.021 | 4103.5688 | 995.7827 | 0.00076447 | 32 | 17.7646 | 4.175 | 4.1036 | 0.99578 | 0.00076447
| 304.15 | 1800000 | 4175.2158 | 4107.8574 | 996.0986 | 0.00078055 | 31 | 17.7646 | 4.1752 | 4.1079 | 0.9961 | 0.00078055
| 303.15 | 1800000 | 4175.439 | 4112.0967 | 996.4061 | 0.00079719 | 30 | 17.7646 | 4.1754 | 4.1121 | 0.99641 | 0.00079719
| 302.15 | 1800000 | 4175.6909 | 4116.2852 | 996.705 | 0.0008144 | 29 | 17.7646 | 4.1757 | 4.1163 | 0.99671 | 0.0008144
| 301.15 | 1800000 | 4175.9736 | 4120.4204 | 996.9951 | 0.00083223 | 28 | 17.7646 | 4.176 | 4.1204 | 0.997 | 0.00083223
| 300.15 | 1800000 | 4176.2886 | 4124.501 | 997.2764 | 0.0008507 | 27 | 17.7646 | 4.1763 | 4.1245 | 0.99728 | 0.0008507
| 299.15 | 1800000 | 4176.6367 | 4128.5259 | 997.5486 | 0.00086984 | 26 | 17.7646 | 4.1766 | 4.1285 | 0.99755 | 0.00086984
| 298.15 | 1800000 | 4177.0195 | 4132.4927 | 997.8115 | 0.00088969 | 25 | 17.7646 | 4.177 | 4.1325 | 0.99781 | 0.00088969
| 297.15 | 1800000 | 4177.4399 | 4136.3994 | 998.0651 | 0.00091028 | 24 | 17.7646 | 4.1774 | 4.1364 | 0.99807 | 0.00091028
| 296.15 | 1800000 | 4177.8994 | 4140.2456 | 998.3091 | 0.00093165 | 23 | 17.7646 | 4.1779 | 4.1402 | 0.99831 | 0.00093165
| 295.15 | 1800000 | 4178.4004 | 4144.0283 | 998.5434 | 0.00095385 | 22 | 17.7646 | 4.1784 | 4.144 | 0.99854 | 0.00095385
| 294.15 | 1800000 | 4178.9458 | 4147.7466 | 998.7676 | 0.00097691 | 21 | 17.7646 | 4.1789 | 4.1477 | 0.99877 | 0.00097691
| 293.15 | 1800000 | 4179.5391 | 4151.3984 | 998.9818 | 0.0010009 | 20 | 17.7646 | 4.1795 | 4.1514 | 0.99898 | 0.0010009
| 292.15 | 1800000 | 4180.1826 | 4154.9829 | 999.1855 | 0.0010258 | 19 | 17.7646 | 4.1802 | 4.155 | 0.99919 | 0.0010258
| 291.15 | 1800000 | 4180.8809 | 4158.4985 | 999.3787 | 0.0010518 | 18 | 17.7646 | 4.1809 | 4.1585 | 0.99938 | 0.0010518
| 290.15 | 1800000 | 4181.6382 | 4161.9434 | 999.561 | 0.0010788 | 17 | 17.7646 | 4.1816 | 4.1619 | 0.99956 | 0.0010788
| 289.15 | 1800000 | 4182.459 | 4165.3164 | 999.7322 | 0.001107 | 16 | 17.7646 | 4.1825 | 4.1653 | 0.99973 | 0.001107
| 288.15 | 1800000 | 4183.3481 | 4168.6167 | 999.8922 | 0.0011364 | 15 | 17.7646 | 4.1833 | 4.1686 | 0.99989 | 0.0011364
| 287.15 | 1800000 | 4184.312 | 4171.8428 | 1000.0405 | 0.001167 | 14 | 17.7646 | 4.1843 | 4.1718 | 1 | 0.001167
| 286.15 | 1800000 | 4185.3574 | 4174.9941 | 1000.1768 | 0.001199 | 13 | 17.7646 | 4.1854 | 4.175 | 1.0002 | 0.001199
| 285.15 | 1800000 | 4186.4907 | 4178.0693 | 1000.3011 | 0.0012325 | 12 | 17.7646 | 4.1865 | 4.1781 | 1.0003 | 0.0012325
| 284.15 | 1800000 | 4187.7207 | 4181.0679 | 1000.4128 | 0.0012674 | 11 | 17.7646 | 4.1877 | 4.1811 | 1.0004 | 0.0012674
| 283.15 | 1800000 | 4189.0557 | 4183.9893 | 1000.5117 | 0.001304 | 10 | 17.7646 | 4.1891 | 4.184 | 1.0005 | 0.001304
| 282.15 | 1800000 | 4190.5063 | 4186.8335 | 1000.5974 | 0.0013424 | 9 | 17.7646 | 4.1905 | 4.1868 | 1.0006 | 0.0013424
| 281.15 | 1800000 | 4192.0825 | 4189.6001 | 1000.6694 | 0.0013825 | 8 | 17.7646 | 4.1921 | 4.1896 | 1.0007 | 0.0013825
| 280.15 | 1800000 | 4193.7974 | 4192.2891 | 1000.7277 | 0.0014246 | 7 | 17.7646 | 4.1938 | 4.1923 | 1.0007 | 0.0014246
| 279.15 | 1800000 | 4195.6641 | 4194.9009 | 1000.7715 | 0.0014689 | 6 | 17.7646 | 4.1957 | 4.1949 | 1.0008 | 0.0014689
| 278.15 | 1800000 | 4197.6978 | 4197.4355 | 1000.8005 | 0.0015153 | 5 | 17.7646 | 4.1977 | 4.1974 | 1.0008 | 0.0015153
| 277.15 | 1800000 | 4199.9146 | 4199.8945 | 1000.8143 | 0.0015642 | 4 | 17.7646 | 4.1999 | 4.1999 | 1.0008 | 0.0015642
| 276.15 | 1800000 | 4202.3335 | 4202.2783 | 1000.8124 | 0.0016156 | 3 | 17.7646 | 4.2023 | 4.2023 | 1.0008 | 0.0016156
| 275.15 | 1800000 | 4204.9746 | 4204.5884 | 1000.7942 | 0.0016698 | 2 | 17.7646 | 4.205 | 4.2046 | 1.0008 | 0.0016698
| 274.15 | 1800000 | 4207.8604 | 4206.8262 | 1000.7592 | 0.001727 | 0.99999 | 17.7646 | 4.2079 | 4.2068 | 1.0008 | 0.001727
| 273.15 | 1800000 | 4211.0156 | 4208.9937 | 1000.7068 | 0.0017873 | -6.1035e-06 | 17.7646 | 4.211 | 4.209 | 1.0007 | 0.0017873
| 473.15 | 1700000 | 4493.1572 | 3316.8914 | 864.7786 | 0.00013436 | 200 | 16.7776 | 4.4932 | 3.3169 | 0.86478 | 0.00013436
| 472.15 | 1700000 | 4487.9624 | 3320.6721 | 865.9669 | 0.00013508 | 199 | 16.7776 | 4.488 | 3.3207 | 0.86597 | 0.00013508
| 471.15 | 1700000 | 4482.8447 | 3324.4705 | 867.1494 | 0.0001358 | 198 | 16.7776 | 4.4828 | 3.3245 | 0.86715 | 0.0001358
| 470.15 | 1700000 | 4477.8022 | 3328.2864 | 868.326 | 0.00013654 | 197 | 16.7776 | 4.4778 | 3.3283 | 0.86833 | 0.00013654
| 469.15 | 1700000 | 4472.834 | 3332.1196 | 869.4968 | 0.00013728 | 196 | 16.7776 | 4.4728 | 3.3321 | 0.8695 | 0.00013728
| 468.15 | 1700000 | 4467.938 | 3335.9702 | 870.6617 | 0.00013803 | 195 | 16.7776 | 4.4679 | 3.336 | 0.87066 | 0.00013803
| 467.15 | 1700000 | 4463.1138 | 3339.8379 | 871.8209 | 0.00013878 | 194 | 16.7776 | 4.4631 | 3.3398 | 0.87182 | 0.00013878
| 466.15 | 1700000 | 4458.3599 | 3343.7227 | 872.9744 | 0.00013955 | 193 | 16.7776 | 4.4584 | 3.3437 | 0.87297 | 0.00013955
| 465.15 | 1700000 | 4453.6743 | 3347.6245 | 874.1223 | 0.00014032 | 192 | 16.7776 | 4.4537 | 3.3476 | 0.87412 | 0.00014032
| 464.15 | 1700000 | 4449.0571 | 3351.543 | 875.2646 | 0.00014111 | 191 | 16.7776 | 4.4491 | 3.3515 | 0.87526 | 0.00014111
| 463.15 | 1700000 | 4444.5063 | 3355.4783 | 876.4014 | 0.0001419 | 190 | 16.7776 | 4.4445 | 3.3555 | 0.8764 | 0.0001419
| 462.15 | 1700000 | 4440.0205 | 3359.4302 | 877.5325 | 0.0001427 | 189 | 16.7776 | 4.44 | 3.3594 | 0.87753 | 0.0001427
| 461.15 | 1700000 | 4435.5996 | 3363.3984 | 878.6583 | 0.0001435 | 188 | 16.7776 | 4.4356 | 3.3634 | 0.87866 | 0.0001435
| 460.15 | 1700000 | 4431.2417 | 3367.3831 | 879.7786 | 0.00014432 | 187 | 16.7776 | 4.4312 | 3.3674 | 0.87978 | 0.00014432
| 459.15 | 1700000 | 4426.9458 | 3371.384 | 880.8935 | 0.00014515 | 186 | 16.7776 | 4.4269 | 3.3714 | 0.88089 | 0.00014515
| 458.15 | 1700000 | 4422.7109 | 3375.4011 | 882.0031 | 0.00014598 | 185 | 16.7776 | 4.4227 | 3.3754 | 0.882 | 0.00014598
| 457.15 | 1700000 | 4418.5366 | 3379.4341 | 883.1073 | 0.00014683 | 184 | 16.7776 | 4.4185 | 3.3794 | 0.88311 | 0.00014683
| 456.15 | 1700000 | 4414.4209 | 3383.4832 | 884.2062 | 0.00014769 | 183 | 16.7776 | 4.4144 | 3.3835 | 0.88421 | 0.00014769
| 455.15 | 1700000 | 4410.3633 | 3387.5479 | 885.2999 | 0.00014855 | 182 | 16.7776 | 4.4104 | 3.3875 | 0.8853 | 0.00014855
| 454.15 | 1700000 | 4406.3633 | 3391.6282 | 886.3884 | 0.00014943 | 181 | 16.7776 | 4.4064 | 3.3916 | 0.88639 | 0.00014943
| 453.15 | 1700000 | 4402.4189 | 3395.7241 | 887.4717 | 0.00015031 | 180 | 16.7776 | 4.4024 | 3.3957 | 0.88747 | 0.00015031
| 452.15 | 1700000 | 4398.5303 | 3399.8354 | 888.5499 | 0.00015121 | 179 | 16.7776 | 4.3985 | 3.3998 | 0.88855 | 0.00015121
| 451.15 | 1700000 | 4394.6958 | 3403.9622 | 889.6229 | 0.00015211 | 178 | 16.7776 | 4.3947 | 3.404 | 0.88962 | 0.00015211
| 450.15 | 1700000 | 4390.915 | 3408.104 | 890.6909 | 0.00015303 | 177 | 16.7776 | 4.3909 | 3.4081 | 0.89069 | 0.00015303
| 449.15 | 1700000 | 4387.187 | 3412.2612 | 891.7538 | 0.00015396 | 176 | 16.7776 | 4.3872 | 3.4123 | 0.89175 | 0.00015396
| 448.15 | 1700000 | 4383.5103 | 3416.4331 | 892.8118 | 0.0001549 | 175 | 16.7776 | 4.3835 | 3.4164 | 0.89281 | 0.0001549
| 447.15 | 1700000 | 4379.8853 | 3420.6201 | 893.8647 | 0.00015585 | 174 | 16.7776 | 4.3799 | 3.4206 | 0.89386 | 0.00015585
| 446.15 | 1700000 | 4376.3101 | 3424.8218 | 894.9126 | 0.00015682 | 173 | 16.7776 | 4.3763 | 3.4248 | 0.89491 | 0.00015682
| 445.15 | 1700000 | 4372.7842 | 3429.0383 | 895.9556 | 0.00015779 | 172 | 16.7776 | 4.3728 | 3.429 | 0.89596 | 0.00015779
| 444.15 | 1700000 | 4369.3071 | 3433.2693 | 896.9938 | 0.00015878 | 171 | 16.7776 | 4.3693 | 3.4333 | 0.89699 | 0.00015878
| 443.15 | 1700000 | 4365.8779 | 3437.5149 | 898.027 | 0.00015978 | 170 | 16.7776 | 4.3659 | 3.4375 | 0.89803 | 0.00015978
| 442.15 | 1700000 | 4362.4956 | 3441.7747 | 899.0554 | 0.00016079 | 169 | 16.7776 | 4.3625 | 3.4418 | 0.89906 | 0.00016079
| 441.15 | 1700000 | 4359.1602 | 3446.0488 | 900.0789 | 0.00016182 | 168 | 16.7776 | 4.3592 | 3.446 | 0.90008 | 0.00016182
| 440.15 | 1700000 | 4355.8701 | 3450.3372 | 901.0977 | 0.00016286 | 167 | 16.7776 | 4.3559 | 3.4503 | 0.9011 | 0.00016286
| 439.15 | 1700000 | 4352.625 | 3454.6394 | 902.1116 | 0.00016391 | 166 | 16.7776 | 4.3526 | 3.4546 | 0.90211 | 0.00016391
| 438.15 | 1700000 | 4349.4243 | 3458.9558 | 903.1208 | 0.00016497 | 165 | 16.7776 | 4.3494 | 3.459 | 0.90312 | 0.00016497
| 437.15 | 1700000 | 4346.2676 | 3463.2861 | 904.1252 | 0.00016605 | 164 | 16.7776 | 4.3463 | 3.4633 | 0.90413 | 0.00016605
| 436.15 | 1700000 | 4343.1533 | 3467.6301 | 905.125 | 0.00016714 | 163 | 16.7776 | 4.3432 | 3.4676 | 0.90512 | 0.00016714
| 435.15 | 1700000 | 4340.082 | 3471.9878 | 906.12 | 0.00016825 | 162 | 16.7776 | 4.3401 | 3.472 | 0.90612 | 0.00016825
| 434.15 | 1700000 | 4337.0522 | 3476.3591 | 907.1104 | 0.00016937 | 161 | 16.7776 | 4.3371 | 3.4764 | 0.90711 | 0.00016937
| 433.15 | 1700000 | 4334.0635 | 3480.7439 | 908.0961 | 0.00017051 | 160 | 16.7776 | 4.3341 | 3.4807 | 0.9081 | 0.00017051
| 432.15 | 1700000 | 4331.1152 | 3485.1421 | 909.0771 | 0.00017166 | 159 | 16.7776 | 4.3311 | 3.4851 | 0.90908 | 0.00017166
| 431.15 | 1700000 | 4328.207 | 3489.5537 | 910.0536 | 0.00017283 | 158 | 16.7776 | 4.3282 | 3.4896 | 0.91005 | 0.00017283
| 430.15 | 1700000 | 4325.3384 | 3493.9785 | 911.0255 | 0.00017402 | 157 | 16.7776 | 4.3253 | 3.494 | 0.91103 | 0.00017402
| 429.15 | 1700000 | 4322.5083 | 3498.4163 | 911.9927 | 0.00017521 | 156 | 16.7776 | 4.3225 | 3.4984 | 0.91199 | 0.00017521
| 428.15 | 1700000 | 4319.7163 | 3502.8672 | 912.9554 | 0.00017643 | 155 | 16.7776 | 4.3197 | 3.5029 | 0.91296 | 0.00017643
| 427.15 | 1700000 | 4316.9624 | 3507.3311 | 913.9136 | 0.00017766 | 154 | 16.7776 | 4.317 | 3.5073 | 0.91391 | 0.00017766
| 426.15 | 1700000 | 4314.2456 | 3511.8079 | 914.8672 | 0.00017891 | 153 | 16.7776 | 4.3142 | 3.5118 | 0.91487 | 0.00017891
| 425.15 | 1700000 | 4311.5654 | 3516.2974 | 915.8162 | 0.00018018 | 152 | 16.7776 | 4.3116 | 3.5163 | 0.91582 | 0.00018018
| 424.15 | 1700000 | 4308.9209 | 3520.7998 | 916.7608 | 0.00018147 | 151 | 16.7776 | 4.3089 | 3.5208 | 0.91676 | 0.00018147
| 423.15 | 1700000 | 4306.3125 | 3525.3147 | 917.7009 | 0.00018277 | 150 | 16.7776 | 4.3063 | 3.5253 | 0.9177 | 0.00018277
| 422.15 | 1700000 | 4303.7393 | 3529.842 | 918.6365 | 0.00018409 | 149 | 16.7776 | 4.3037 | 3.5298 | 0.91864 | 0.00018409
| 421.15 | 1700000 | 4301.2007 | 3534.3818 | 919.5676 | 0.00018543 | 148 | 16.7776 | 4.3012 | 3.5344 | 0.91957 | 0.00018543
| 420.15 | 1700000 | 4298.6963 | 3538.9341 | 920.4943 | 0.00018679 | 147 | 16.7776 | 4.2987 | 3.5389 | 0.92049 | 0.00018679
| 419.15 | 1700000 | 4296.2256 | 3543.4988 | 921.4164 | 0.00018817 | 146 | 16.7776 | 4.2962 | 3.5435 | 0.92142 | 0.00018817
| 418.15 | 1700000 | 4293.7881 | 3548.0754 | 922.3342 | 0.00018957 | 145 | 16.7776 | 4.2938 | 3.5481 | 0.92233 | 0.00018957
| 417.15 | 1700000 | 4291.3838 | 3552.6643 | 923.2476 | 0.00019099 | 144 | 16.7776 | 4.2914 | 3.5527 | 0.92325 | 0.00019099
| 416.15 | 1700000 | 4289.0117 | 3557.2654 | 924.1565 | 0.00019243 | 143 | 16.7776 | 4.289 | 3.5573 | 0.92416 | 0.00019243
| 415.15 | 1700000 | 4286.6714 | 3561.8782 | 925.061 | 0.00019389 | 142 | 16.7776 | 4.2867 | 3.5619 | 0.92506 | 0.00019389
| 414.15 | 1700000 | 4284.3633 | 3566.5032 | 925.9611 | 0.00019538 | 141 | 16.7776 | 4.2844 | 3.5665 | 0.92596 | 0.00019538
| 413.15 | 1700000 | 4282.0859 | 3571.1396 | 926.8568 | 0.00019688 | 140 | 16.7776 | 4.2821 | 3.5711 | 0.92686 | 0.00019688
| 412.15 | 1700000 | 4279.8394 | 3575.7881 | 927.7481 | 0.00019841 | 139 | 16.7776 | 4.2798 | 3.5758 | 0.92775 | 0.00019841
| 411.15 | 1700000 | 4277.6235 | 3580.4482 | 928.6351 | 0.00019996 | 138 | 16.7776 | 4.2776 | 3.5804 | 0.92864 | 0.00019996
| 410.15 | 1700000 | 4275.4375 | 3585.1199 | 929.5176 | 0.00020154 | 137 | 16.7776 | 4.2754 | 3.5851 | 0.92952 | 0.00020154
| 409.15 | 1700000 | 4273.2812 | 3589.803 | 930.3958 | 0.00020314 | 136 | 16.7776 | 4.2733 | 3.5898 | 0.9304 | 0.00020314
| 408.15 | 1700000 | 4271.1543 | 3594.4978 | 931.2697 | 0.00020476 | 135 | 16.7776 | 4.2712 | 3.5945 | 0.93127 | 0.00020476
| 407.15 | 1700000 | 4269.0562 | 3599.2036 | 932.1392 | 0.00020641 | 134 | 16.7776 | 4.2691 | 3.5992 | 0.93214 | 0.00020641
| 406.15 | 1700000 | 4266.9868 | 3603.9209 | 933.0043 | 0.00020808 | 133 | 16.7776 | 4.267 | 3.6039 | 0.933 | 0.00020808
| 405.15 | 1700000 | 4264.9458 | 3608.6494 | 933.8651 | 0.00020978 | 132 | 16.7776 | 4.2649 | 3.6086 | 0.93387 | 0.00020978
| 404.15 | 1700000 | 4262.9326 | 3613.3892 | 934.7214 | 0.00021151 | 131 | 16.7776 | 4.2629 | 3.6134 | 0.93472 | 0.00021151
| 403.15 | 1700000 | 4260.9473 | 3618.1399 | 935.5735 | 0.00021327 | 130 | 16.7776 | 4.2609 | 3.6181 | 0.93557 | 0.00021327
| 402.15 | 1700000 | 4258.9888 | 3622.9016 | 936.4212 | 0.00021505 | 129 | 16.7776 | 4.259 | 3.6229 | 0.93642 | 0.00021505
| 401.15 | 1700000 | 4257.0576 | 3627.6741 | 937.2646 | 0.00021686 | 128 | 16.7776 | 4.2571 | 3.6277 | 0.93726 | 0.00021686
| 400.15 | 1700000 | 4255.1533 | 3632.4575 | 938.1036 | 0.0002187 | 127 | 16.7776 | 4.2552 | 3.6325 | 0.9381 | 0.0002187
| 399.15 | 1700000 | 4253.2759 | 3637.2517 | 938.9383 | 0.00022057 | 126 | 16.7776 | 4.2533 | 3.6373 | 0.93894 | 0.00022057
| 398.15 | 1700000 | 4251.4238 | 3642.0564 | 939.7687 | 0.00022247 | 125 | 16.7776 | 4.2514 | 3.6421 | 0.93977 | 0.00022247
| 397.15 | 1700000 | 4249.5981 | 3646.8718 | 940.5947 | 0.0002244 | 124 | 16.7776 | 4.2496 | 3.6469 | 0.94059 | 0.0002244
| 396.15 | 1700000 | 4247.7983 | 3651.6978 | 941.4163 | 0.00022636 | 123 | 16.7776 | 4.2478 | 3.6517 | 0.94142 | 0.00022636
| 395.15 | 1700000 | 4246.0234 | 3656.5339 | 942.2336 | 0.00022836 | 122 | 16.7776 | 4.246 | 3.6565 | 0.94223 | 0.00022836
| 394.15 | 1700000 | 4244.2739 | 3661.3806 | 943.0465 | 0.00023038 | 121 | 16.7776 | 4.2443 | 3.6614 | 0.94305 | 0.00023038
| 393.15 | 1700000 | 4242.5493 | 3666.2373 | 943.8551 | 0.00023245 | 120 | 16.7776 | 4.2425 | 3.6662 | 0.94386 | 0.00023245
| 392.15 | 1700000 | 4240.8491 | 3671.1042 | 944.6594 | 0.00023454 | 119 | 16.7776 | 4.2408 | 3.6711 | 0.94466 | 0.00023454
| 391.15 | 1700000 | 4239.1733 | 3675.9812 | 945.4592 | 0.00023667 | 118 | 16.7776 | 4.2392 | 3.676 | 0.94546 | 0.00023667
| 390.15 | 1700000 | 4237.5225 | 3680.8682 | 946.2547 | 0.00023884 | 117 | 16.7776 | 4.2375 | 3.6809 | 0.94625 | 0.00023884
| 389.15 | 1700000 | 4235.895 | 3685.7651 | 947.0458 | 0.00024105 | 116 | 16.7776 | 4.2359 | 3.6858 | 0.94705 | 0.00024105
| 388.15 | 1700000 | 4234.2915 | 3690.6716 | 947.8326 | 0.00024329 | 115 | 16.7776 | 4.2343 | 3.6907 | 0.94783 | 0.00024329
| 387.15 | 1700000 | 4232.7114 | 3695.5879 | 948.6149 | 0.00024558 | 114 | 16.7776 | 4.2327 | 3.6956 | 0.94861 | 0.00024558
| 386.15 | 1700000 | 4231.1548 | 3700.5137 | 949.3929 | 0.0002479 | 113 | 16.7776 | 4.2312 | 3.7005 | 0.94939 | 0.0002479
| 385.15 | 1700000 | 4229.6216 | 3705.4487 | 950.1664 | 0.00025026 | 112 | 16.7776 | 4.2296 | 3.7054 | 0.95017 | 0.00025026
| 384.15 | 1700000 | 4228.1113 | 3710.3933 | 950.9355 | 0.00025267 | 111 | 16.7776 | 4.2281 | 3.7104 | 0.95094 | 0.00025267
| 383.15 | 1700000 | 4226.624 | 3715.3469 | 951.7003 | 0.00025511 | 110 | 16.7776 | 4.2266 | 3.7153 | 0.9517 | 0.00025511
| 382.15 | 1700000 | 4225.1592 | 3720.3096 | 952.4606 | 0.0002576 | 109 | 16.7776 | 4.2252 | 3.7203 | 0.95246 | 0.0002576
| 381.15 | 1700000 | 4223.7173 | 3725.2815 | 953.2164 | 0.00026014 | 108 | 16.7776 | 4.2237 | 3.7253 | 0.95322 | 0.00026014
| 380.15 | 1700000 | 4222.2974 | 3730.262 | 953.9678 | 0.00026272 | 107 | 16.7776 | 4.2223 | 3.7303 | 0.95397 | 0.00026272
| 379.15 | 1700000 | 4220.8999 | 3735.2512 | 954.7148 | 0.00026535 | 106 | 16.7776 | 4.2209 | 3.7353 | 0.95471 | 0.00026535
| 378.15 | 1700000 | 4219.5244 | 3740.2488 | 955.4572 | 0.00026803 | 105 | 16.7776 | 4.2195 | 3.7402 | 0.95546 | 0.00026803
| 377.15 | 1700000 | 4218.1709 | 3745.2551 | 956.1953 | 0.00027075 | 104 | 16.7776 | 4.2182 | 3.7453 | 0.9562 | 0.00027075
| 376.15 | 1700000 | 4216.8394 | 3750.2693 | 956.9287 | 0.00027353 | 103 | 16.7776 | 4.2168 | 3.7503 | 0.95693 | 0.00027353
| 375.15 | 1700000 | 4215.5293 | 3755.2917 | 957.6577 | 0.00027636 | 102 | 16.7776 | 4.2155 | 3.7553 | 0.95766 | 0.00027636
| 374.15 | 1700000 | 4214.2412 | 3760.3223 | 958.3821 | 0.00027924 | 101 | 16.7776 | 4.2142 | 3.7603 | 0.95838 | 0.00027924
| 373.15 | 1700000 | 4212.9741 | 3765.3604 | 959.102 | 0.00028217 | 100 | 16.7776 | 4.213 | 3.7654 | 0.9591 | 0.00028217
| 372.15 | 1700000 | 4211.729 | 3770.406 | 959.8173 | 0.00028516 | 99 | 16.7776 | 4.2117 | 3.7704 | 0.95982 | 0.00028516
| 371.15 | 1700000 | 4210.5044 | 3775.4592 | 960.5281 | 0.00028821 | 98 | 16.7776 | 4.2105 | 3.7755 | 0.96053 | 0.00028821
| 370.15 | 1700000 | 4209.3018 | 3780.5195 | 961.2343 | 0.00029132 | 97 | 16.7776 | 4.2093 | 3.7805 | 0.96123 | 0.00029132
| 369.15 | 1700000 | 4208.1196 | 3785.5867 | 961.9359 | 0.00029449 | 96 | 16.7776 | 4.2081 | 3.7856 | 0.96194 | 0.00029449
| 368.15 | 1700000 | 4206.959 | 3790.6606 | 962.6328 | 0.00029771 | 95 | 16.7776 | 4.207 | 3.7907 | 0.96263 | 0.00029771
| 367.15 | 1700000 | 4205.8188 | 3795.7415 | 963.325 | 0.00030101 | 94 | 16.7776 | 4.2058 | 3.7957 | 0.96333 | 0.00030101
| 366.15 | 1700000 | 4204.6997 | 3800.8284 | 964.0126 | 0.00030436 | 93 | 16.7776 | 4.2047 | 3.8008 | 0.96401 | 0.00030436
| 365.15 | 1700000 | 4203.6011 | 3805.9214 | 964.6956 | 0.00030779 | 92 | 16.7776 | 4.2036 | 3.8059 | 0.9647 | 0.00030779
| 364.15 | 1700000 | 4202.5234 | 3811.0203 | 965.3738 | 0.00031128 | 91 | 16.7776 | 4.2025 | 3.811 | 0.96537 | 0.00031128
| 363.15 | 1700000 | 4201.4663 | 3816.1248 | 966.0472 | 0.00031484 | 90 | 16.7776 | 4.2015 | 3.8161 | 0.96605 | 0.00031484
| 362.15 | 1700000 | 4200.4302 | 3821.2344 | 966.716 | 0.00031847 | 89 | 16.7776 | 4.2004 | 3.8212 | 0.96672 | 0.00031847
| 361.15 | 1700000 | 4199.4141 | 3826.3494 | 967.3799 | 0.00032218 | 88 | 16.7776 | 4.1994 | 3.8263 | 0.96738 | 0.00032218
| 360.15 | 1700000 | 4198.4189 | 3831.4688 | 968.0391 | 0.00032597 | 87 | 16.7776 | 4.1984 | 3.8315 | 0.96804 | 0.00032597
| 359.15 | 1700000 | 4197.4438 | 3836.5928 | 968.6934 | 0.00032983 | 86 | 16.7776 | 4.1974 | 3.8366 | 0.96869 | 0.00032983
| 358.15 | 1700000 | 4196.4893 | 3841.7209 | 969.3428 | 0.00033377 | 85 | 16.7776 | 4.1965 | 3.8417 | 0.96934 | 0.00033377
| 357.15 | 1700000 | 4195.5552 | 3846.853 | 969.9874 | 0.0003378 | 84 | 16.7776 | 4.1956 | 3.8469 | 0.96999 | 0.0003378
| 356.15 | 1700000 | 4194.6416 | 3851.9883 | 970.6271 | 0.00034191 | 83 | 16.7776 | 4.1946 | 3.852 | 0.97063 | 0.00034191
| 355.15 | 1700000 | 4193.748 | 3857.1267 | 971.2618 | 0.00034611 | 82 | 16.7776 | 4.1937 | 3.8571 | 0.97126 | 0.00034611
| 354.15 | 1700000 | 4192.875 | 3862.2678 | 971.8915 | 0.00035039 | 81 | 16.7776 | 4.1929 | 3.8623 | 0.97189 | 0.00035039
| 353.15 | 1700000 | 4192.022 | 3867.4114 | 972.5163 | 0.00035477 | 80 | 16.7776 | 4.192 | 3.8674 | 0.97252 | 0.00035477
| 352.15 | 1700000 | 4191.1895 | 3872.5566 | 973.136 | 0.00035925 | 79 | 16.7776 | 4.1912 | 3.8726 | 0.97314 | 0.00035925
| 351.15 | 1700000 | 4190.377 | 3877.7036 | 973.7507 | 0.00036382 | 78 | 16.7776 | 4.1904 | 3.8777 | 0.97375 | 0.00036382
| 350.15 | 1700000 | 4189.585 | 3882.8516 | 974.3603 | 0.0003685 | 77 | 16.7776 | 4.1896 | 3.8829 | 0.97436 | 0.0003685
| 349.15 | 1700000 | 4188.813 | 3888 | 974.9647 | 0.00037327 | 76 | 16.7776 | 4.1888 | 3.888 | 0.97496 | 0.00037327
| 348.15 | 1700000 | 4188.0615 | 3893.1487 | 975.564 | 0.00037816 | 75 | 16.7776 | 4.1881 | 3.8931 | 0.97556 | 0.00037816
| 347.15 | 1700000 | 4187.3301 | 3898.2969 | 976.1581 | 0.00038315 | 74 | 16.7776 | 4.1873 | 3.8983 | 0.97616 | 0.00038315
| 346.15 | 1700000 | 4186.6187 | 3903.4441 | 976.7469 | 0.00038826 | 73 | 16.7776 | 4.1866 | 3.9034 | 0.97675 | 0.00038826
| 345.15 | 1700000 | 4185.9277 | 3908.5901 | 977.3305 | 0.00039348 | 72 | 16.7776 | 4.1859 | 3.9086 | 0.97733 | 0.00039348
| 344.15 | 1700000 | 4185.2568 | 3913.7339 | 977.9088 | 0.00039883 | 71 | 16.7776 | 4.1853 | 3.9137 | 0.97791 | 0.00039883
| 343.15 | 1700000 | 4184.6064 | 3918.8752 | 978.4816 | 0.0004043 | 70 | 16.7776 | 4.1846 | 3.9189 | 0.97848 | 0.0004043
| 342.15 | 1700000 | 4183.9761 | 3924.0132 | 979.0491 | 0.0004099 | 69 | 16.7776 | 4.184 | 3.924 | 0.97905 | 0.0004099
| 341.15 | 1700000 | 4183.3657 | 3929.1475 | 979.6112 | 0.00041563 | 68 | 16.7776 | 4.1834 | 3.9291 | 0.97961 | 0.00041563
| 340.15 | 1700000 | 4182.7759 | 3934.2773 | 980.1678 | 0.00042149 | 67 | 16.7776 | 4.1828 | 3.9343 | 0.98017 | 0.00042149
| 339.15 | 1700000 | 4182.2065 | 3939.4021 | 980.7189 | 0.0004275 | 66 | 16.7776 | 4.1822 | 3.9394 | 0.98072 | 0.0004275
| 338.15 | 1700000 | 4181.6572 | 3944.521 | 981.2643 | 0.00043365 | 65 | 16.7776 | 4.1817 | 3.9445 | 0.98126 | 0.00043365
| 337.15 | 1700000 | 4181.1284 | 3949.6333 | 981.8042 | 0.00043995 | 64 | 16.7776 | 4.1811 | 3.9496 | 0.9818 | 0.00043995
| 336.15 | 1700000 | 4180.6196 | 3954.7383 | 982.3384 | 0.00044641 | 63 | 16.7776 | 4.1806 | 3.9547 | 0.98234 | 0.00044641
| 335.15 | 1700000 | 4180.1313 | 3959.8352 | 982.8668 | 0.00045302 | 62 | 16.7776 | 4.1801 | 3.9598 | 0.98287 | 0.00045302
| 334.15 | 1700000 | 4179.6636 | 3964.9233 | 983.3895 | 0.00045981 | 61 | 16.7776 | 4.1797 | 3.9649 | 0.98339 | 0.00045981
| 333.15 | 1700000 | 4179.2158 | 3970.0017 | 983.9064 | 0.00046676 | 60 | 16.7776 | 4.1792 | 3.97 | 0.98391 | 0.00046676
| 332.15 | 1700000 | 4178.7886 | 3975.0693 | 984.4174 | 0.00047389 | 59 | 16.7776 | 4.1788 | 3.9751 | 0.98442 | 0.00047389
| 331.15 | 1700000 | 4178.3823 | 3980.1257 | 984.9224 | 0.0004812 | 58 | 16.7776 | 4.1784 | 3.9801 | 0.98492 | 0.0004812
| 330.15 | 1700000 | 4177.9961 | 3985.1694 | 985.4214 | 0.00048871 | 57 | 16.7776 | 4.178 | 3.9852 | 0.98542 | 0.00048871
| 329.15 | 1700000 | 4177.6304 | 3990.2 | 985.9144 | 0.0004964 | 56 | 16.7776 | 4.1776 | 3.9902 | 0.98591 | 0.0004964
| 328.15 | 1700000 | 4177.2852 | 3995.2161 | 986.4013 | 0.00050431 | 55 | 16.7776 | 4.1773 | 3.9952 | 0.9864 | 0.00050431
| 327.15 | 1700000 | 4176.9604 | 4000.217 | 986.882 | 0.00051242 | 54 | 16.7776 | 4.177 | 4.0002 | 0.98688 | 0.00051242
| 326.15 | 1700000 | 4176.6567 | 4005.2014 | 987.3564 | 0.00052075 | 53 | 16.7776 | 4.1767 | 4.0052 | 0.98736 | 0.00052075
| 325.15 | 1700000 | 4176.374 | 4010.1685 | 987.8246 | 0.0005293 | 52 | 16.7776 | 4.1764 | 4.0102 | 0.98782 | 0.0005293
| 324.15 | 1700000 | 4176.1113 | 4015.1167 | 988.2863 | 0.0005381 | 51 | 16.7776 | 4.1761 | 4.0151 | 0.98829 | 0.0005381
| 323.15 | 1700000 | 4175.8701 | 4020.0454 | 988.7416 | 0.00054713 | 50 | 16.7776 | 4.1759 | 4.02 | 0.98874 | 0.00054713
| 322.15 | 1700000 | 4175.6494 | 4024.9529 | 989.1904 | 0.00055642 | 49 | 16.7776 | 4.1756 | 4.025 | 0.98919 | 0.00055642
| 321.15 | 1700000 | 4175.4502 | 4029.8386 | 989.6326 | 0.00056596 | 48 | 16.7776 | 4.1755 | 4.0298 | 0.98963 | 0.00056596
| 320.15 | 1700000 | 4175.272 | 4034.7007 | 990.0681 | 0.00057578 | 47 | 16.7776 | 4.1753 | 4.0347 | 0.99007 | 0.00057578
| 319.15 | 1700000 | 4175.1147 | 4039.5381 | 990.4969 | 0.00058589 | 46 | 16.7776 | 4.1751 | 4.0395 | 0.9905 | 0.00058589
| 318.15 | 1700000 | 4174.9795 | 4044.3496 | 990.9188 | 0.00059628 | 45 | 16.7776 | 4.175 | 4.0443 | 0.99092 | 0.00059628
| 317.15 | 1700000 | 4174.8652 | 4049.1338 | 991.3337 | 0.00060699 | 44 | 16.7776 | 4.1749 | 4.0491 | 0.99133 | 0.00060699
| 316.15 | 1700000 | 4174.7729 | 4053.8892 | 991.7417 | 0.00061801 | 43 | 16.7776 | 4.1748 | 4.0539 | 0.99174 | 0.00061801
| 315.15 | 1700000 | 4174.7031 | 4058.6145 | 992.1426 | 0.00062936 | 42 | 16.7776 | 4.1747 | 4.0586 | 0.99214 | 0.00062936
| 314.15 | 1700000 | 4174.6548 | 4063.3083 | 992.5363 | 0.00064105 | 41 | 16.7776 | 4.1747 | 4.0633 | 0.99254 | 0.00064105
| 313.15 | 1700000 | 4174.6294 | 4067.969 | 992.9227 | 0.00065311 | 40 | 16.7776 | 4.1746 | 4.068 | 0.99292 | 0.00065311
| 312.15 | 1700000 | 4174.627 | 4072.5952 | 993.3016 | 0.00066554 | 39 | 16.7776 | 4.1746 | 4.0726 | 0.9933 | 0.00066554
| 311.15 | 1700000 | 4174.6475 | 4077.1851 | 993.6732 | 0.00067835 | 38 | 16.7776 | 4.1746 | 4.0772 | 0.99367 | 0.00067835
| 310.15 | 1700000 | 4174.6914 | 4081.7375 | 994.037 | 0.00069158 | 37 | 16.7776 | 4.1747 | 4.0817 | 0.99404 | 0.00069158
| 309.15 | 1700000 | 4174.7593 | 4086.2505 | 994.3932 | 0.00070523 | 36 | 16.7776 | 4.1748 | 4.0863 | 0.99439 | 0.00070523
| 308.15 | 1700000 | 4174.8521 | 4090.7227 | 994.7416 | 0.00071933 | 35 | 16.7776 | 4.1749 | 4.0907 | 0.99474 | 0.00071933
| 307.15 | 1700000 | 4174.9697 | 4095.1523 | 995.082 | 0.00073388 | 34 | 16.7776 | 4.175 | 4.0952 | 0.99508 | 0.00073388
| 306.15 | 1700000 | 4175.1133 | 4099.5381 | 995.4144 | 0.00074893 | 33 | 16.7776 | 4.1751 | 4.0995 | 0.99541 | 0.00074893
| 305.15 | 1700000 | 4175.2837 | 4103.8774 | 995.7386 | 0.00076448 | 32 | 16.7776 | 4.1753 | 4.1039 | 0.99574 | 0.00076448
| 304.15 | 1700000 | 4175.481 | 4108.1694 | 996.0544 | 0.00078056 | 31 | 16.7776 | 4.1755 | 4.1082 | 0.99605 | 0.00078056
| 303.15 | 1700000 | 4175.707 | 4112.4121 | 996.3618 | 0.0007972 | 30 | 16.7776 | 4.1757 | 4.1124 | 0.99636 | 0.0007972
| 302.15 | 1700000 | 4175.9624 | 4116.604 | 996.6606 | 0.00081442 | 29 | 16.7776 | 4.176 | 4.1166 | 0.99666 | 0.00081442
| 301.15 | 1700000 | 4176.2485 | 4120.7427 | 996.9506 | 0.00083225 | 28 | 16.7776 | 4.1762 | 4.1207 | 0.99695 | 0.00083225
| 300.15 | 1700000 | 4176.5664 | 4124.8276 | 997.2318 | 0.00085072 | 27 | 16.7776 | 4.1766 | 4.1248 | 0.99723 | 0.00085072
| 299.15 | 1700000 | 4176.918 | 4128.856 | 997.5038 | 0.00086986 | 26 | 16.7776 | 4.1769 | 4.1289 | 0.9975 | 0.00086986
| 298.15 | 1700000 | 4177.3052 | 4132.8262 | 997.7667 | 0.00088971 | 25 | 16.7776 | 4.1773 | 4.1328 | 0.99777 | 0.00088971
| 297.15 | 1700000 | 4177.7295 | 4136.7373 | 998.0201 | 0.00091031 | 24 | 16.7776 | 4.1777 | 4.1367 | 0.99802 | 0.00091031
| 296.15 | 1700000 | 4178.1929 | 4140.5869 | 998.264 | 0.00093168 | 23 | 16.7776 | 4.1782 | 4.1406 | 0.99826 | 0.00093168
| 295.15 | 1700000 | 4178.6982 | 4144.3735 | 998.4981 | 0.00095388 | 22 | 16.7776 | 4.1787 | 4.1444 | 0.9985 | 0.00095388
| 294.15 | 1700000 | 4179.2485 | 4148.0962 | 998.7222 | 0.00097695 | 21 | 16.7776 | 4.1792 | 4.1481 | 0.99872 | 0.00097695
| 293.15 | 1700000 | 4179.8462 | 4151.7524 | 998.9362 | 0.0010009 | 20 | 16.7776 | 4.1798 | 4.1518 | 0.99894 | 0.0010009
| 292.15 | 1700000 | 4180.4951 | 4155.3408 | 999.1398 | 0.0010259 | 19 | 16.7776 | 4.1805 | 4.1553 | 0.99914 | 0.0010259
| 291.15 | 1700000 | 4181.1987 | 4158.8608 | 999.3328 | 0.0010518 | 18 | 16.7776 | 4.1812 | 4.1589 | 0.99933 | 0.0010518
| 290.15 | 1700000 | 4181.9619 | 4162.3101 | 999.5149 | 0.0010789 | 17 | 16.7776 | 4.182 | 4.1623 | 0.99951 | 0.0010789
| 289.15 | 1700000 | 4182.7886 | 4165.688 | 999.686 | 0.0011071 | 16 | 16.7776 | 4.1828 | 4.1657 | 0.99969 | 0.0011071
| 288.15 | 1700000 | 4183.6841 | 4168.9927 | 999.8456 | 0.0011364 | 15 | 16.7776 | 4.1837 | 4.169 | 0.99985 | 0.0011364
| 287.15 | 1700000 | 4184.6548 | 4172.2236 | 999.9938 | 0.0011671 | 14 | 16.7776 | 4.1847 | 4.1722 | 0.99999 | 0.0011671
| 286.15 | 1700000 | 4185.707 | 4175.3794 | 1000.1299 | 0.0011991 | 13 | 16.7776 | 4.1857 | 4.1754 | 1.0001 | 0.0011991
| 285.15 | 1700000 | 4186.8481 | 4178.46 | 1000.2539 | 0.0012326 | 12 | 16.7776 | 4.1868 | 4.1785 | 1.0003 | 0.0012326
| 284.15 | 1700000 | 4188.0859 | 4181.4639 | 1000.3654 | 0.0012675 | 11 | 16.7776 | 4.1881 | 4.1815 | 1.0004 | 0.0012675
| 283.15 | 1700000 | 4189.4292 | 4184.3906 | 1000.4641 | 0.0013041 | 10 | 16.7776 | 4.1894 | 4.1844 | 1.0005 | 0.0013041
| 282.15 | 1700000 | 4190.8887 | 4187.2407 | 1000.5494 | 0.0013425 | 9 | 16.7776 | 4.1909 | 4.1872 | 1.0005 | 0.0013425
| 281.15 | 1700000 | 4192.4746 | 4190.0127 | 1000.6213 | 0.0013826 | 8 | 16.7776 | 4.1925 | 4.19 | 1.0006 | 0.0013826
| 280.15 | 1700000 | 4194.1992 | 4192.7075 | 1000.6793 | 0.0014248 | 7 | 16.7776 | 4.1942 | 4.1927 | 1.0007 | 0.0014248
| 279.15 | 1700000 | 4196.0767 | 4195.3257 | 1000.7228 | 0.001469 | 6 | 16.7776 | 4.1961 | 4.1953 | 1.0007 | 0.001469
| 278.15 | 1700000 | 4198.1216 | 4197.8667 | 1000.7515 | 0.0015155 | 5 | 16.7776 | 4.1981 | 4.1979 | 1.0008 | 0.0015155
| 277.15 | 1700000 | 4200.3506 | 4200.332 | 1000.765 | 0.0015644 | 4 | 16.7776 | 4.2004 | 4.2003 | 1.0008 | 0.0015644
| 276.15 | 1700000 | 4202.7817 | 4202.7227 | 1000.7628 | 0.0016158 | 3 | 16.7776 | 4.2028 | 4.2027 | 1.0008 | 0.0016158
| 275.15 | 1700000 | 4205.4365 | 4205.04 | 1000.7442 | 0.00167 | 2 | 16.7776 | 4.2054 | 4.205 | 1.0007 | 0.00167
| 274.15 | 1700000 | 4208.3364 | 4207.2852 | 1000.7089 | 0.0017272 | 0.99999 | 16.7776 | 4.2083 | 4.2073 | 1.0007 | 0.0017272
| 273.15 | 1700000 | 4211.5073 | 4209.4604 | 1000.6561 | 0.0017875 | -6.1035e-06 | 16.7776 | 4.2115 | 4.2095 | 1.0007 | 0.0017875
| 473.15 | 1600000 | 4493.7441 | 3316.9683 | 864.7021 | 0.00013433 | 200 | 15.7907 | 4.4937 | 3.317 | 0.8647 | 0.00013433
| 472.15 | 1600000 | 4488.541 | 3320.749 | 865.8911 | 0.00013505 | 199 | 15.7907 | 4.4885 | 3.3207 | 0.86589 | 0.00013505
| 471.15 | 1600000 | 4483.415 | 3324.5474 | 867.0741 | 0.00013578 | 198 | 15.7907 | 4.4834 | 3.3245 | 0.86707 | 0.00013578
| 470.15 | 1600000 | 4478.3643 | 3328.3633 | 868.2512 | 0.00013651 | 197 | 15.7907 | 4.4784 | 3.3284 | 0.86825 | 0.00013651
| 469.15 | 1600000 | 4473.3877 | 3332.1965 | 869.4225 | 0.00013725 | 196 | 15.7907 | 4.4734 | 3.3322 | 0.86942 | 0.00013725
| 468.15 | 1600000 | 4468.4844 | 3336.0471 | 870.588 | 0.000138 | 195 | 15.7907 | 4.4685 | 3.336 | 0.87059 | 0.000138
| 467.15 | 1600000 | 4463.6523 | 3339.915 | 871.7477 | 0.00013876 | 194 | 15.7907 | 4.4637 | 3.3399 | 0.87175 | 0.00013876
| 466.15 | 1600000 | 4458.8911 | 3343.7998 | 872.9018 | 0.00013952 | 193 | 15.7907 | 4.4589 | 3.3438 | 0.8729 | 0.00013952
| 465.15 | 1600000 | 4454.1982 | 3347.7017 | 874.0502 | 0.0001403 | 192 | 15.7907 | 4.4542 | 3.3477 | 0.87405 | 0.0001403
| 464.15 | 1600000 | 4449.5737 | 3351.6204 | 875.1929 | 0.00014108 | 191 | 15.7907 | 4.4496 | 3.3516 | 0.87519 | 0.00014108
| 463.15 | 1600000 | 4445.0161 | 3355.5557 | 876.3301 | 0.00014187 | 190 | 15.7907 | 4.445 | 3.3556 | 0.87633 | 0.00014187
| 462.15 | 1600000 | 4440.5239 | 3359.5076 | 877.4618 | 0.00014267 | 189 | 15.7907 | 4.4405 | 3.3595 | 0.87746 | 0.00014267
| 461.15 | 1600000 | 4436.0957 | 3363.4761 | 878.588 | 0.00014348 | 188 | 15.7907 | 4.4361 | 3.3635 | 0.87859 | 0.00014348
| 460.15 | 1600000 | 4431.7314 | 3367.4609 | 879.7088 | 0.0001443 | 187 | 15.7907 | 4.4317 | 3.3675 | 0.87971 | 0.0001443
| 459.15 | 1600000 | 4427.4292 | 3371.4619 | 880.8242 | 0.00014512 | 186 | 15.7907 | 4.4274 | 3.3715 | 0.88082 | 0.00014512
| 458.15 | 1600000 | 4423.1885 | 3375.479 | 881.9341 | 0.00014596 | 185 | 15.7907 | 4.4232 | 3.3755 | 0.88193 | 0.00014596
| 457.15 | 1600000 | 4419.0073 | 3379.5122 | 883.0388 | 0.0001468 | 184 | 15.7907 | 4.419 | 3.3795 | 0.88304 | 0.0001468
| 456.15 | 1600000 | 4414.8857 | 3383.5615 | 884.1382 | 0.00014766 | 183 | 15.7907 | 4.4149 | 3.3836 | 0.88414 | 0.00014766
| 455.15 | 1600000 | 4410.8228 | 3387.6262 | 885.2323 | 0.00014853 | 182 | 15.7907 | 4.4108 | 3.3876 | 0.88523 | 0.00014853
| 454.15 | 1600000 | 4406.8164 | 3391.707 | 886.3212 | 0.0001494 | 181 | 15.7907 | 4.4068 | 3.3917 | 0.88632 | 0.0001494
| 453.15 | 1600000 | 4402.8667 | 3395.803 | 887.405 | 0.00015029 | 180 | 15.7907 | 4.4029 | 3.3958 | 0.8874 | 0.00015029
| 452.15 | 1600000 | 4398.9727 | 3399.9148 | 888.4835 | 0.00015118 | 179 | 15.7907 | 4.399 | 3.3999 | 0.88848 | 0.00015118
| 451.15 | 1600000 | 4395.1328 | 3404.0417 | 889.557 | 0.00015209 | 178 | 15.7907 | 4.3951 | 3.404 | 0.88956 | 0.00015209
| 450.15 | 1600000 | 4391.3467 | 3408.1838 | 890.6254 | 0.00015301 | 177 | 15.7907 | 4.3913 | 3.4082 | 0.89063 | 0.00015301
| 449.15 | 1600000 | 4387.6128 | 3412.3411 | 891.6887 | 0.00015394 | 176 | 15.7907 | 4.3876 | 3.4123 | 0.89169 | 0.00015394
| 448.15 | 1600000 | 4383.9316 | 3416.5134 | 892.747 | 0.00015488 | 175 | 15.7907 | 4.3839 | 3.4165 | 0.89275 | 0.00015488
| 447.15 | 1600000 | 4380.3013 | 3420.7007 | 893.8003 | 0.00015583 | 174 | 15.7907 | 4.3803 | 3.4207 | 0.8938 | 0.00015583
| 446.15 | 1600000 | 4376.7212 | 3424.9028 | 894.8486 | 0.00015679 | 173 | 15.7907 | 4.3767 | 3.4249 | 0.89485 | 0.00015679
| 445.15 | 1600000 | 4373.1904 | 3429.1196 | 895.892 | 0.00015777 | 172 | 15.7907 | 4.3732 | 3.4291 | 0.89589 | 0.00015777
| 444.15 | 1600000 | 4369.7085 | 3433.3508 | 896.9305 | 0.00015875 | 171 | 15.7907 | 4.3697 | 3.4334 | 0.89693 | 0.00015875
| 443.15 | 1600000 | 4366.2749 | 3437.5967 | 897.9641 | 0.00015975 | 170 | 15.7907 | 4.3663 | 3.4376 | 0.89796 | 0.00015975
| 442.15 | 1600000 | 4362.8882 | 3441.8569 | 898.9928 | 0.00016077 | 169 | 15.7907 | 4.3629 | 3.4419 | 0.89899 | 0.00016077
| 441.15 | 1600000 | 4359.5479 | 3446.1313 | 900.0167 | 0.00016179 | 168 | 15.7907 | 4.3595 | 3.4461 | 0.90002 | 0.00016179
| 440.15 | 1600000 | 4356.2539 | 3450.4202 | 901.0358 | 0.00016283 | 167 | 15.7907 | 4.3563 | 3.4504 | 0.90104 | 0.00016283
| 439.15 | 1600000 | 4353.0044 | 3454.7229 | 902.0501 | 0.00016388 | 166 | 15.7907 | 4.353 | 3.4547 | 0.90205 | 0.00016388
| 438.15 | 1600000 | 4349.7998 | 3459.0398 | 903.0596 | 0.00016495 | 165 | 15.7907 | 4.3498 | 3.459 | 0.90306 | 0.00016495
| 437.15 | 1600000 | 4346.6387 | 3463.3704 | 904.0644 | 0.00016603 | 164 | 15.7907 | 4.3466 | 3.4634 | 0.90406 | 0.00016603
| 436.15 | 1600000 | 4343.521 | 3467.7148 | 905.0645 | 0.00016712 | 163 | 15.7907 | 4.3435 | 3.4677 | 0.90506 | 0.00016712
| 435.15 | 1600000 | 4340.4453 | 3472.073 | 906.0599 | 0.00016823 | 162 | 15.7907 | 4.3404 | 3.4721 | 0.90606 | 0.00016823
| 434.15 | 1600000 | 4337.4116 | 3476.4448 | 907.0505 | 0.00016935 | 161 | 15.7907 | 4.3374 | 3.4764 | 0.90705 | 0.00016935
| 433.15 | 1600000 | 4334.4189 | 3480.8301 | 908.0366 | 0.00017049 | 160 | 15.7907 | 4.3344 | 3.4808 | 0.90804 | 0.00017049
| 432.15 | 1600000 | 4331.4673 | 3485.229 | 909.0179 | 0.00017164 | 159 | 15.7907 | 4.3315 | 3.4852 | 0.90902 | 0.00017164
| 431.15 | 1600000 | 4328.5557 | 3489.6409 | 909.9947 | 0.00017281 | 158 | 15.7907 | 4.3286 | 3.4896 | 0.90999 | 0.00017281
| 430.15 | 1600000 | 4325.6831 | 3494.0662 | 910.9669 | 0.00017399 | 157 | 15.7907 | 4.3257 | 3.4941 | 0.91097 | 0.00017399
| 429.15 | 1600000 | 4322.8496 | 3498.5046 | 911.9344 | 0.00017519 | 156 | 15.7907 | 4.3228 | 3.4985 | 0.91193 | 0.00017519
| 428.15 | 1600000 | 4320.0542 | 3502.9563 | 912.8974 | 0.00017641 | 155 | 15.7907 | 4.3201 | 3.503 | 0.9129 | 0.00017641
| 427.15 | 1600000 | 4317.2969 | 3507.4207 | 913.8558 | 0.00017764 | 154 | 15.7907 | 4.3173 | 3.5074 | 0.91386 | 0.00017764
| 426.15 | 1600000 | 4314.5767 | 3511.8979 | 914.8098 | 0.00017889 | 153 | 15.7907 | 4.3146 | 3.5119 | 0.91481 | 0.00017889
| 425.15 | 1600000 | 4311.8931 | 3516.3882 | 915.7591 | 0.00018016 | 152 | 15.7907 | 4.3119 | 3.5164 | 0.91576 | 0.00018016
| 424.15 | 1600000 | 4309.2461 | 3520.8911 | 916.7039 | 0.00018144 | 151 | 15.7907 | 4.3092 | 3.5209 | 0.9167 | 0.00018144
| 423.15 | 1600000 | 4306.6343 | 3525.4067 | 917.6443 | 0.00018274 | 150 | 15.7907 | 4.3066 | 3.5254 | 0.91764 | 0.00018274
| 422.15 | 1600000 | 4304.0581 | 3529.9348 | 918.5801 | 0.00018407 | 149 | 15.7907 | 4.3041 | 3.5299 | 0.91858 | 0.00018407
| 421.15 | 1600000 | 4301.5166 | 3534.4753 | 919.5115 | 0.00018541 | 148 | 15.7907 | 4.3015 | 3.5345 | 0.91951 | 0.00018541
| 420.15 | 1600000 | 4299.0093 | 3539.0283 | 920.4385 | 0.00018677 | 147 | 15.7907 | 4.299 | 3.539 | 0.92044 | 0.00018677
| 419.15 | 1600000 | 4296.5356 | 3543.5935 | 921.3609 | 0.00018815 | 146 | 15.7907 | 4.2965 | 3.5436 | 0.92136 | 0.00018815
| 418.15 | 1600000 | 4294.0952 | 3548.1709 | 922.2789 | 0.00018955 | 145 | 15.7907 | 4.2941 | 3.5482 | 0.92228 | 0.00018955
| 417.15 | 1600000 | 4291.688 | 3552.7605 | 923.1926 | 0.00019097 | 144 | 15.7907 | 4.2917 | 3.5528 | 0.92319 | 0.00019097
| 416.15 | 1600000 | 4289.3135 | 3557.3623 | 924.1017 | 0.00019241 | 143 | 15.7907 | 4.2893 | 3.5574 | 0.9241 | 0.00019241
| 415.15 | 1600000 | 4286.9707 | 3561.9761 | 925.0065 | 0.00019387 | 142 | 15.7907 | 4.287 | 3.562 | 0.92501 | 0.00019387
| 414.15 | 1600000 | 4284.6597 | 3566.6016 | 925.9068 | 0.00019535 | 141 | 15.7907 | 4.2847 | 3.5666 | 0.92591 | 0.00019535
| 413.15 | 1600000 | 4282.3799 | 3571.239 | 926.8028 | 0.00019686 | 140 | 15.7907 | 4.2824 | 3.5712 | 0.9268 | 0.00019686
| 412.15 | 1600000 | 4280.1309 | 3575.8884 | 927.6943 | 0.00019839 | 139 | 15.7907 | 4.2801 | 3.5759 | 0.92769 | 0.00019839
| 411.15 | 1600000 | 4277.9126 | 3580.5493 | 928.5815 | 0.00019994 | 138 | 15.7907 | 4.2779 | 3.5805 | 0.92858 | 0.00019994
| 410.15 | 1600000 | 4275.7241 | 3585.2217 | 929.4643 | 0.00020151 | 137 | 15.7907 | 4.2757 | 3.5852 | 0.92946 | 0.00020151
| 409.15 | 1600000 | 4273.5654 | 3589.9058 | 930.3428 | 0.00020311 | 136 | 15.7907 | 4.2736 | 3.5899 | 0.93034 | 0.00020311
| 408.15 | 1600000 | 4271.436 | 3594.6013 | 931.2168 | 0.00020473 | 135 | 15.7907 | 4.2714 | 3.5946 | 0.93122 | 0.00020473
| 407.15 | 1600000 | 4269.3359 | 3599.3083 | 932.0865 | 0.00020638 | 134 | 15.7907 | 4.2693 | 3.5993 | 0.93209 | 0.00020638
| 406.15 | 1600000 | 4267.2642 | 3604.0266 | 932.9518 | 0.00020806 | 133 | 15.7907 | 4.2673 | 3.604 | 0.93295 | 0.00020806
| 405.15 | 1600000 | 4265.2212 | 3608.7559 | 933.8128 | 0.00020976 | 132 | 15.7907 | 4.2652 | 3.6088 | 0.93381 | 0.00020976
| 404.15 | 1600000 | 4263.2061 | 3613.4966 | 934.6694 | 0.00021148 | 131 | 15.7907 | 4.2632 | 3.6135 | 0.93467 | 0.00021148
| 403.15 | 1600000 | 4261.2183 | 3618.2483 | 935.5217 | 0.00021324 | 130 | 15.7907 | 4.2612 | 3.6182 | 0.93552 | 0.00021324
| 402.15 | 1600000 | 4259.2583 | 3623.011 | 936.3697 | 0.00021502 | 129 | 15.7907 | 4.2593 | 3.623 | 0.93637 | 0.00021502
| 401.15 | 1600000 | 4257.3252 | 3627.7844 | 937.2133 | 0.00021683 | 128 | 15.7907 | 4.2573 | 3.6278 | 0.93721 | 0.00021683
| 400.15 | 1600000 | 4255.4189 | 3632.5688 | 938.0525 | 0.00021867 | 127 | 15.7907 | 4.2554 | 3.6326 | 0.93805 | 0.00021867
| 399.15 | 1600000 | 4253.5396 | 3637.364 | 938.8874 | 0.00022054 | 126 | 15.7907 | 4.2535 | 3.6374 | 0.93889 | 0.00022054
| 398.15 | 1600000 | 4251.686 | 3642.1699 | 939.7179 | 0.00022244 | 125 | 15.7907 | 4.2517 | 3.6422 | 0.93972 | 0.00022244
| 397.15 | 1600000 | 4249.8584 | 3646.9863 | 940.5441 | 0.00022437 | 124 | 15.7907 | 4.2499 | 3.647 | 0.94054 | 0.00022437
| 396.15 | 1600000 | 4248.0566 | 3651.8132 | 941.3659 | 0.00022633 | 123 | 15.7907 | 4.2481 | 3.6518 | 0.94137 | 0.00022633
| 395.15 | 1600000 | 4246.2798 | 3656.6506 | 942.1834 | 0.00022833 | 122 | 15.7907 | 4.2463 | 3.6567 | 0.94218 | 0.00022833
| 394.15 | 1600000 | 4244.5288 | 3661.4985 | 942.9965 | 0.00023036 | 121 | 15.7907 | 4.2445 | 3.6615 | 0.943 | 0.00023036
| 393.15 | 1600000 | 4242.8022 | 3666.3564 | 943.8053 | 0.00023242 | 120 | 15.7907 | 4.2428 | 3.6664 | 0.94381 | 0.00023242
| 392.15 | 1600000 | 4241.1011 | 3671.2246 | 944.6097 | 0.00023452 | 119 | 15.7907 | 4.2411 | 3.6712 | 0.94461 | 0.00023452
| 391.15 | 1600000 | 4239.4238 | 3676.1028 | 945.4098 | 0.00023665 | 118 | 15.7907 | 4.2394 | 3.6761 | 0.94541 | 0.00023665
| 390.15 | 1600000 | 4237.771 | 3680.991 | 946.2054 | 0.00023882 | 117 | 15.7907 | 4.2378 | 3.681 | 0.94621 | 0.00023882
| 389.15 | 1600000 | 4236.1421 | 3685.8889 | 946.9967 | 0.00024102 | 116 | 15.7907 | 4.2361 | 3.6859 | 0.947 | 0.00024102
| 388.15 | 1600000 | 4234.5371 | 3690.7966 | 947.7836 | 0.00024327 | 115 | 15.7907 | 4.2345 | 3.6908 | 0.94778 | 0.00024327
| 387.15 | 1600000 | 4232.9556 | 3695.7141 | 948.5662 | 0.00024555 | 114 | 15.7907 | 4.233 | 3.6957 | 0.94857 | 0.00024555
| 386.15 | 1600000 | 4231.3979 | 3700.6414 | 949.3443 | 0.00024787 | 113 | 15.7907 | 4.2314 | 3.7006 | 0.94934 | 0.00024787
| 385.15 | 1600000 | 4229.8633 | 3705.5776 | 950.118 | 0.00025023 | 112 | 15.7907 | 4.2299 | 3.7056 | 0.95012 | 0.00025023
| 384.15 | 1600000 | 4228.3516 | 3710.5234 | 950.8873 | 0.00025264 | 111 | 15.7907 | 4.2284 | 3.7105 | 0.95089 | 0.00025264
| 383.15 | 1600000 | 4226.8633 | 3715.4785 | 951.6522 | 0.00025509 | 110 | 15.7907 | 4.2269 | 3.7155 | 0.95165 | 0.00025509
| 382.15 | 1600000 | 4225.397 | 3720.4426 | 952.4126 | 0.00025758 | 109 | 15.7907 | 4.2254 | 3.7204 | 0.95241 | 0.00025758
| 381.15 | 1600000 | 4223.9541 | 3725.4158 | 953.1686 | 0.00026011 | 108 | 15.7907 | 4.224 | 3.7254 | 0.95317 | 0.00026011
| 380.15 | 1600000 | 4222.5332 | 3730.3977 | 953.9202 | 0.00026269 | 107 | 15.7907 | 4.2225 | 3.7304 | 0.95392 | 0.00026269
| 379.15 | 1600000 | 4221.1343 | 3735.3882 | 954.6673 | 0.00026532 | 106 | 15.7907 | 4.2211 | 3.7354 | 0.95467 | 0.00026532
| 378.15 | 1600000 | 4219.7578 | 3740.3875 | 955.4099 | 0.000268 | 105 | 15.7907 | 4.2198 | 3.7404 | 0.95541 | 0.000268
| 377.15 | 1600000 | 4218.4033 | 3745.395 | 956.148 | 0.00027073 | 104 | 15.7907 | 4.2184 | 3.7454 | 0.95615 | 0.00027073
| 376.15 | 1600000 | 4217.0708 | 3750.4109 | 956.8817 | 0.0002735 | 103 | 15.7907 | 4.2171 | 3.7504 | 0.95688 | 0.0002735
| 375.15 | 1600000 | 4215.7598 | 3755.4348 | 957.6107 | 0.00027633 | 102 | 15.7907 | 4.2158 | 3.7554 | 0.95761 | 0.00027633
| 374.15 | 1600000 | 4214.4707 | 3760.4668 | 958.3353 | 0.00027921 | 101 | 15.7907 | 4.2145 | 3.7605 | 0.95834 | 0.00027921
| 373.15 | 1600000 | 4213.2026 | 3765.5066 | 959.0554 | 0.00028215 | 100 | 15.7907 | 4.2132 | 3.7655 | 0.95906 | 0.00028215
| 372.15 | 1600000 | 4211.9565 | 3770.5537 | 959.7708 | 0.00028514 | 99 | 15.7907 | 4.212 | 3.7706 | 0.95977 | 0.00028514
| 371.15 | 1600000 | 4210.7314 | 3775.6084 | 960.4817 | 0.00028819 | 98 | 15.7907 | 4.2107 | 3.7756 | 0.96048 | 0.00028819
| 370.15 | 1600000 | 4209.5278 | 3780.6704 | 961.188 | 0.00029129 | 97 | 15.7907 | 4.2095 | 3.7807 | 0.96119 | 0.00029129
| 369.15 | 1600000 | 4208.3452 | 3785.7393 | 961.8896 | 0.00029446 | 96 | 15.7907 | 4.2083 | 3.7857 | 0.96189 | 0.00029446
| 368.15 | 1600000 | 4207.1831 | 3790.8149 | 962.5867 | 0.00029769 | 95 | 15.7907 | 4.2072 | 3.7908 | 0.96259 | 0.00029769
| 367.15 | 1600000 | 4206.0425 | 3795.8972 | 963.2791 | 0.00030098 | 94 | 15.7907 | 4.206 | 3.7959 | 0.96328 | 0.00030098
| 366.15 | 1600000 | 4204.9229 | 3800.9858 | 963.9669 | 0.00030434 | 93 | 15.7907 | 4.2049 | 3.801 | 0.96397 | 0.00030434
| 365.15 | 1600000 | 4203.8237 | 3806.0806 | 964.6498 | 0.00030776 | 92 | 15.7907 | 4.2038 | 3.8061 | 0.96465 | 0.00030776
| 364.15 | 1600000 | 4202.7456 | 3811.1812 | 965.3282 | 0.00031125 | 91 | 15.7907 | 4.2027 | 3.8112 | 0.96533 | 0.00031125
| 363.15 | 1600000 | 4201.688 | 3816.2874 | 966.0018 | 0.00031481 | 90 | 15.7907 | 4.2017 | 3.8163 | 0.966 | 0.00031481
| 362.15 | 1600000 | 4200.6509 | 3821.3989 | 966.6706 | 0.00031845 | 89 | 15.7907 | 4.2007 | 3.8214 | 0.96667 | 0.00031845
| 361.15 | 1600000 | 4199.6348 | 3826.5156 | 967.3347 | 0.00032216 | 88 | 15.7907 | 4.1996 | 3.8265 | 0.96733 | 0.00032216
| 360.15 | 1600000 | 4198.6387 | 3831.637 | 967.9939 | 0.00032594 | 87 | 15.7907 | 4.1986 | 3.8316 | 0.96799 | 0.00032594
| 359.15 | 1600000 | 4197.6636 | 3836.7629 | 968.6483 | 0.0003298 | 86 | 15.7907 | 4.1977 | 3.8368 | 0.96865 | 0.0003298
| 358.15 | 1600000 | 4196.7085 | 3841.8928 | 969.2979 | 0.00033375 | 85 | 15.7907 | 4.1967 | 3.8419 | 0.9693 | 0.00033375
| 357.15 | 1600000 | 4195.7739 | 3847.0266 | 969.9425 | 0.00033777 | 84 | 15.7907 | 4.1958 | 3.847 | 0.96994 | 0.00033777
| 356.15 | 1600000 | 4194.8599 | 3852.1641 | 970.5823 | 0.00034188 | 83 | 15.7907 | 4.1949 | 3.8522 | 0.97058 | 0.00034188
| 355.15 | 1600000 | 4193.9663 | 3857.3044 | 971.2171 | 0.00034608 | 82 | 15.7907 | 4.194 | 3.8573 | 0.97122 | 0.00034608
| 354.15 | 1600000 | 4193.0928 | 3862.4475 | 971.8469 | 0.00035037 | 81 | 15.7907 | 4.1931 | 3.8624 | 0.97185 | 0.00035037
| 353.15 | 1600000 | 4192.2397 | 3867.593 | 972.4717 | 0.00035475 | 80 | 15.7907 | 4.1922 | 3.8676 | 0.97247 | 0.00035475
| 352.15 | 1600000 | 4191.4067 | 3872.7402 | 973.0916 | 0.00035922 | 79 | 15.7907 | 4.1914 | 3.8727 | 0.97309 | 0.00035922
| 351.15 | 1600000 | 4190.5942 | 3877.8892 | 973.7063 | 0.0003638 | 78 | 15.7907 | 4.1906 | 3.8779 | 0.97371 | 0.0003638
| 350.15 | 1600000 | 4189.8022 | 3883.0393 | 974.316 | 0.00036847 | 77 | 15.7907 | 4.1898 | 3.883 | 0.97432 | 0.00036847
| 349.15 | 1600000 | 4189.0303 | 3888.1897 | 974.9205 | 0.00037325 | 76 | 15.7907 | 4.189 | 3.8882 | 0.97492 | 0.00037325
| 348.15 | 1600000 | 4188.2783 | 3893.3406 | 975.5198 | 0.00037813 | 75 | 15.7907 | 4.1883 | 3.8933 | 0.97552 | 0.00037813
| 347.15 | 1600000 | 4187.5469 | 3898.491 | 976.114 | 0.00038313 | 74 | 15.7907 | 4.1875 | 3.8985 | 0.97611 | 0.00038313
| 346.15 | 1600000 | 4186.8354 | 3903.6404 | 976.7029 | 0.00038823 | 73 | 15.7907 | 4.1868 | 3.9036 | 0.9767 | 0.00038823
| 345.15 | 1600000 | 4186.1445 | 3908.7883 | 977.2865 | 0.00039346 | 72 | 15.7907 | 4.1861 | 3.9088 | 0.97729 | 0.00039346
| 344.15 | 1600000 | 4185.4741 | 3913.9346 | 977.8648 | 0.0003988 | 71 | 15.7907 | 4.1855 | 3.9139 | 0.97786 | 0.0003988
| 343.15 | 1600000 | 4184.8237 | 3919.0781 | 978.4378 | 0.00040427 | 70 | 15.7907 | 4.1848 | 3.9191 | 0.97844 | 0.00040427
| 342.15 | 1600000 | 4184.1934 | 3924.2183 | 979.0054 | 0.00040987 | 69 | 15.7907 | 4.1842 | 3.9242 | 0.97901 | 0.00040987
| 341.15 | 1600000 | 4183.5835 | 3929.355 | 979.5674 | 0.0004156 | 68 | 15.7907 | 4.1836 | 3.9294 | 0.97957 | 0.0004156
| 340.15 | 1600000 | 4182.9941 | 3934.4871 | 980.1241 | 0.00042147 | 67 | 15.7907 | 4.183 | 3.9345 | 0.98012 | 0.00042147
| 339.15 | 1600000 | 4182.4248 | 3939.6143 | 980.6752 | 0.00042747 | 66 | 15.7907 | 4.1824 | 3.9396 | 0.98068 | 0.00042747
| 338.15 | 1600000 | 4181.876 | 3944.7354 | 981.2207 | 0.00043363 | 65 | 15.7907 | 4.1819 | 3.9447 | 0.98122 | 0.00043363
| 337.15 | 1600000 | 4181.3472 | 3949.8501 | 981.7606 | 0.00043993 | 64 | 15.7907 | 4.1813 | 3.9499 | 0.98176 | 0.00043993
| 336.15 | 1600000 | 4180.8389 | 3954.9575 | 982.2948 | 0.00044638 | 63 | 15.7907 | 4.1808 | 3.955 | 0.98229 | 0.00044638
| 335.15 | 1600000 | 4180.3511 | 3960.0569 | 982.8233 | 0.000453 | 62 | 15.7907 | 4.1804 | 3.9601 | 0.98282 | 0.000453
| 334.15 | 1600000 | 4179.8838 | 3965.1475 | 983.346 | 0.00045978 | 61 | 15.7907 | 4.1799 | 3.9651 | 0.98335 | 0.00045978
| 333.15 | 1600000 | 4179.437 | 3970.2283 | 983.8629 | 0.00046674 | 60 | 15.7907 | 4.1794 | 3.9702 | 0.98386 | 0.00046674
| 332.15 | 1600000 | 4179.0103 | 3975.2986 | 984.3739 | 0.00047387 | 59 | 15.7907 | 4.179 | 3.9753 | 0.98437 | 0.00047387
| 331.15 | 1600000 | 4178.6045 | 3980.3574 | 984.879 | 0.00048118 | 58 | 15.7907 | 4.1786 | 3.9804 | 0.98488 | 0.00048118
| 330.15 | 1600000 | 4178.2188 | 3985.4038 | 985.3781 | 0.00048868 | 57 | 15.7907 | 4.1782 | 3.9854 | 0.98538 | 0.00048868
| 329.15 | 1600000 | 4177.854 | 3990.4368 | 985.871 | 0.00049638 | 56 | 15.7907 | 4.1779 | 3.9904 | 0.98587 | 0.00049638
| 328.15 | 1600000 | 4177.5098 | 3995.4556 | 986.358 | 0.00050429 | 55 | 15.7907 | 4.1775 | 3.9955 | 0.98636 | 0.00050429
| 327.15 | 1600000 | 4177.186 | 4000.4592 | 986.8386 | 0.0005124 | 54 | 15.7907 | 4.1772 | 4.0005 | 0.98684 | 0.0005124
| 326.15 | 1600000 | 4176.8833 | 4005.4463 | 987.3131 | 0.00052073 | 53 | 15.7907 | 4.1769 | 4.0054 | 0.98731 | 0.00052073
| 325.15 | 1600000 | 4176.6011 | 4010.416 | 987.7812 | 0.00052929 | 52 | 15.7907 | 4.1766 | 4.0104 | 0.98778 | 0.00052929
| 324.15 | 1600000 | 4176.3398 | 4015.3669 | 988.243 | 0.00053808 | 51 | 15.7907 | 4.1763 | 4.0154 | 0.98824 | 0.00053808
| 323.15 | 1600000 | 4176.0996 | 4020.2983 | 988.6983 | 0.00054711 | 50 | 15.7907 | 4.1761 | 4.0203 | 0.9887 | 0.00054711
| 322.15 | 1600000 | 4175.8804 | 4025.2087 | 989.147 | 0.0005564 | 49 | 15.7907 | 4.1759 | 4.0252 | 0.98915 | 0.0005564
| 321.15 | 1600000 | 4175.6821 | 4030.0972 | 989.5892 | 0.00056595 | 48 | 15.7907 | 4.1757 | 4.0301 | 0.98959 | 0.00056595
| 320.15 | 1600000 | 4175.5049 | 4034.9622 | 990.0247 | 0.00057577 | 47 | 15.7907 | 4.1755 | 4.035 | 0.99002 | 0.00057577
| 319.15 | 1600000 | 4175.3491 | 4039.8025 | 990.4534 | 0.00058587 | 46 | 15.7907 | 4.1753 | 4.0398 | 0.99045 | 0.00058587
| 318.15 | 1600000 | 4175.2153 | 4044.6169 | 990.8753 | 0.00059627 | 45 | 15.7907 | 4.1752 | 4.0446 | 0.99088 | 0.00059627
| 317.15 | 1600000 | 4175.1025 | 4049.4041 | 991.2903 | 0.00060697 | 44 | 15.7907 | 4.1751 | 4.0494 | 0.99129 | 0.00060697
| 316.15 | 1600000 | 4175.0122 | 4054.1626 | 991.6982 | 0.00061799 | 43 | 15.7907 | 4.175 | 4.0542 | 0.9917 | 0.00061799
| 315.15 | 1600000 | 4174.9434 | 4058.8909 | 992.0991 | 0.00062935 | 42 | 15.7907 | 4.1749 | 4.0589 | 0.9921 | 0.00062935
| 314.15 | 1600000 | 4174.8975 | 4063.5876 | 992.4927 | 0.00064104 | 41 | 15.7907 | 4.1749 | 4.0636 | 0.99249 | 0.00064104
| 313.15 | 1600000 | 4174.8735 | 4068.2515 | 992.879 | 0.0006531 | 40 | 15.7907 | 4.1749 | 4.0683 | 0.99288 | 0.0006531
| 312.15 | 1600000 | 4174.873 | 4072.8809 | 993.258 | 0.00066553 | 39 | 15.7907 | 4.1749 | 4.0729 | 0.99326 | 0.00066553
| 311.15 | 1600000 | 4174.8955 | 4077.4739 | 993.6295 | 0.00067835 | 38 | 15.7907 | 4.1749 | 4.0775 | 0.99363 | 0.00067835
| 310.15 | 1600000 | 4174.9419 | 4082.0295 | 993.9933 | 0.00069158 | 37 | 15.7907 | 4.1749 | 4.082 | 0.99399 | 0.00069158
| 309.15 | 1600000 | 4175.0122 | 4086.5459 | 994.3494 | 0.00070523 | 36 | 15.7907 | 4.175 | 4.0865 | 0.99435 | 0.00070523
| 308.15 | 1600000 | 4175.1069 | 4091.0212 | 994.6977 | 0.00071933 | 35 | 15.7907 | 4.1751 | 4.091 | 0.9947 | 0.00071933
| 307.15 | 1600000 | 4175.2271 | 4095.4543 | 995.038 | 0.00073389 | 34 | 15.7907 | 4.1752 | 4.0955 | 0.99504 | 0.00073389
| 306.15 | 1600000 | 4175.3735 | 4099.8433 | 995.3704 | 0.00074893 | 33 | 15.7907 | 4.1754 | 4.0998 | 0.99537 | 0.00074893
| 305.15 | 1600000 | 4175.5464 | 4104.186 | 995.6944 | 0.00076448 | 32 | 15.7907 | 4.1755 | 4.1042 | 0.99569 | 0.00076448
| 304.15 | 1600000 | 4175.7466 | 4108.4814 | 996.0102 | 0.00078057 | 31 | 15.7907 | 4.1757 | 4.1085 | 0.99601 | 0.00078057
| 303.15 | 1600000 | 4175.9756 | 4112.7275 | 996.3174 | 0.00079721 | 30 | 15.7907 | 4.176 | 4.1127 | 0.99632 | 0.00079721
| 302.15 | 1600000 | 4176.2339 | 4116.9229 | 996.6161 | 0.00081443 | 29 | 15.7907 | 4.1762 | 4.1169 | 0.99662 | 0.00081443
| 301.15 | 1600000 | 4176.5229 | 4121.0654 | 996.9061 | 0.00083226 | 28 | 15.7907 | 4.1765 | 4.1211 | 0.99691 | 0.00083226
| 300.15 | 1600000 | 4176.8447 | 4125.1538 | 997.1871 | 0.00085073 | 27 | 15.7907 | 4.1768 | 4.1252 | 0.99719 | 0.00085073
| 299.15 | 1600000 | 4177.1997 | 4129.186 | 997.459 | 0.00086988 | 26 | 15.7907 | 4.1772 | 4.1292 | 0.99746 | 0.00086988
| 298.15 | 1600000 | 4177.5908 | 4133.1602 | 997.7218 | 0.00088974 | 25 | 15.7907 | 4.1776 | 4.1332 | 0.99772 | 0.00088974
| 297.15 | 1600000 | 4178.019 | 4137.0752 | 997.9751 | 0.00091033 | 24 | 15.7907 | 4.178 | 4.1371 | 0.99798 | 0.00091033
| 296.15 | 1600000 | 4178.4868 | 4140.9287 | 998.2188 | 0.00093171 | 23 | 15.7907 | 4.1785 | 4.1409 | 0.99822 | 0.00093171
| 295.15 | 1600000 | 4178.9966 | 4144.7192 | 998.4528 | 0.00095391 | 22 | 15.7907 | 4.179 | 4.1447 | 0.99845 | 0.00095391
| 294.15 | 1600000 | 4179.5513 | 4148.4458 | 998.6768 | 0.00097699 | 21 | 15.7907 | 4.1796 | 4.1484 | 0.99868 | 0.00097699
| 293.15 | 1600000 | 4180.1543 | 4152.1064 | 998.8906 | 0.001001 | 20 | 15.7907 | 4.1802 | 4.1521 | 0.99889 | 0.001001
| 292.15 | 1600000 | 4180.8081 | 4155.6992 | 999.094 | 0.0010259 | 19 | 15.7907 | 4.1808 | 4.1557 | 0.99909 | 0.0010259
| 291.15 | 1600000 | 4181.5171 | 4159.2231 | 999.2868 | 0.0010519 | 18 | 15.7907 | 4.1815 | 4.1592 | 0.99929 | 0.0010519
| 290.15 | 1600000 | 4182.2856 | 4162.6772 | 999.4688 | 0.0010789 | 17 | 15.7907 | 4.1823 | 4.1627 | 0.99947 | 0.0010789
| 289.15 | 1600000 | 4183.1182 | 4166.0596 | 999.6396 | 0.0011071 | 16 | 15.7907 | 4.1831 | 4.1661 | 0.99964 | 0.0011071
| 288.15 | 1600000 | 4184.0205 | 4169.3691 | 999.7991 | 0.0011365 | 15 | 15.7907 | 4.184 | 4.1694 | 0.9998 | 0.0011365
| 287.15 | 1600000 | 4184.998 | 4172.6045 | 999.947 | 0.0011672 | 14 | 15.7907 | 4.185 | 4.1726 | 0.99995 | 0.0011672
| 286.15 | 1600000 | 4186.0571 | 4175.7656 | 1000.083 | 0.0011992 | 13 | 15.7907 | 4.1861 | 4.1758 | 1.0001 | 0.0011992
| 285.15 | 1600000 | 4187.2056 | 4178.8511 | 1000.2068 | 0.0012327 | 12 | 15.7907 | 4.1872 | 4.1789 | 1.0002 | 0.0012327
| 284.15 | 1600000 | 4188.4512 | 4181.8599 | 1000.318 | 0.0012676 | 11 | 15.7907 | 4.1885 | 4.1819 | 1.0003 | 0.0012676
| 283.15 | 1600000 | 4189.8032 | 4184.7925 | 1000.4164 | 0.0013043 | 10 | 15.7907 | 4.1898 | 4.1848 | 1.0004 | 0.0013043
| 282.15 | 1600000 | 4191.2715 | 4187.6475 | 1000.5016 | 0.0013426 | 9 | 15.7907 | 4.1913 | 4.1876 | 1.0005 | 0.0013426
| 281.15 | 1600000 | 4192.8667 | 4190.4258 | 1000.5732 | 0.0013828 | 8 | 15.7907 | 4.1929 | 4.1904 | 1.0006 | 0.0013828
| 280.15 | 1600000 | 4194.6016 | 4193.1265 | 1000.6309 | 0.0014249 | 7 | 15.7907 | 4.1946 | 4.1931 | 1.0006 | 0.0014249
| 279.15 | 1600000 | 4196.4893 | 4195.7505 | 1000.6741 | 0.0014692 | 6 | 15.7907 | 4.1965 | 4.1958 | 1.0007 | 0.0014692
| 278.15 | 1600000 | 4198.5454 | 4198.2983 | 1000.7025 | 0.0015157 | 5 | 15.7907 | 4.1985 | 4.1983 | 1.0007 | 0.0015157
| 277.15 | 1600000 | 4200.7866 | 4200.77 | 1000.7157 | 0.0015645 | 4 | 15.7907 | 4.2008 | 4.2008 | 1.0007 | 0.0015645
| 276.15 | 1600000 | 4203.2305 | 4203.168 | 1000.7131 | 0.001616 | 3 | 15.7907 | 4.2032 | 4.2032 | 1.0007 | 0.001616
| 275.15 | 1600000 | 4205.8989 | 4205.4922 | 1000.6943 | 0.0016702 | 2 | 15.7907 | 4.2059 | 4.2055 | 1.0007 | 0.0016702
| 274.15 | 1600000 | 4208.813 | 4207.7451 | 1000.6586 | 0.0017274 | 0.99999 | 15.7907 | 4.2088 | 4.2077 | 1.0007 | 0.0017274
| 273.15 | 1600000 | 4211.999 | 4209.9282 | 1000.6054 | 0.0017878 | -6.1035e-06 | 15.7907 | 4.212 | 4.2099 | 1.0006 | 0.0017878
| 473.15 | 1500000 | 2908.7749 | 2020.9224 | 7.5505 | 1.5733e-05 | 200 | 14.8038 | 2.9088 | 2.0209 | 0.0075505 | 1.5733e-05
| 472.15 | 1500000 | 2940.46 | 2040.588 | 7.5753 | 1.5688e-05 | 199 | 14.8038 | 2.9405 | 2.0406 | 0.0075753 | 1.5688e-05
| 471.15 | 1500000 | 4483.9858 | 3324.6243 | 866.9988 | 0.00013575 | 198 | 14.8038 | 4.484 | 3.3246 | 0.867 | 0.00013575
| 470.15 | 1500000 | 4478.9272 | 3328.4402 | 868.1765 | 0.00013649 | 197 | 14.8038 | 4.4789 | 3.3284 | 0.86818 | 0.00013649
| 469.15 | 1500000 | 4473.9429 | 3332.2737 | 869.3483 | 0.00013723 | 196 | 14.8038 | 4.4739 | 3.3323 | 0.86935 | 0.00013723
| 468.15 | 1500000 | 4469.0312 | 3336.1243 | 870.5143 | 0.00013798 | 195 | 14.8038 | 4.469 | 3.3361 | 0.87051 | 0.00013798
| 467.15 | 1500000 | 4464.1919 | 3339.9922 | 871.6745 | 0.00013873 | 194 | 14.8038 | 4.4642 | 3.34 | 0.87167 | 0.00013873
| 466.15 | 1500000 | 4459.4229 | 3343.877 | 872.829 | 0.0001395 | 193 | 14.8038 | 4.4594 | 3.3439 | 0.87283 | 0.0001395
| 465.15 | 1500000 | 4454.7231 | 3347.7788 | 873.9779 | 0.00014027 | 192 | 14.8038 | 4.4547 | 3.3478 | 0.87398 | 0.00014027
| 464.15 | 1500000 | 4450.0913 | 3351.6975 | 875.1212 | 0.00014106 | 191 | 14.8038 | 4.4501 | 3.3517 | 0.87512 | 0.00014106
| 463.15 | 1500000 | 4445.5264 | 3355.6331 | 876.2589 | 0.00014185 | 190 | 14.8038 | 4.4455 | 3.3556 | 0.87626 | 0.00014185
| 462.15 | 1500000 | 4441.0273 | 3359.5852 | 877.3911 | 0.00014265 | 189 | 14.8038 | 4.441 | 3.3596 | 0.87739 | 0.00014265
| 461.15 | 1500000 | 4436.5928 | 3363.5537 | 878.5177 | 0.00014345 | 188 | 14.8038 | 4.4366 | 3.3636 | 0.87852 | 0.00014345
| 460.15 | 1500000 | 4432.2217 | 3367.5386 | 879.6389 | 0.00014427 | 187 | 14.8038 | 4.4322 | 3.3675 | 0.87964 | 0.00014427
| 459.15 | 1500000 | 4427.9131 | 3371.5398 | 880.7548 | 0.0001451 | 186 | 14.8038 | 4.4279 | 3.3715 | 0.88075 | 0.0001451
| 458.15 | 1500000 | 4423.666 | 3375.5571 | 881.8652 | 0.00014593 | 185 | 14.8038 | 4.4237 | 3.3756 | 0.88187 | 0.00014593
| 457.15 | 1500000 | 4419.479 | 3379.5906 | 882.9703 | 0.00014678 | 184 | 14.8038 | 4.4195 | 3.3796 | 0.88297 | 0.00014678
| 456.15 | 1500000 | 4415.3516 | 3383.6399 | 884.0701 | 0.00014764 | 183 | 14.8038 | 4.4154 | 3.3836 | 0.88407 | 0.00014764
| 455.15 | 1500000 | 4411.2822 | 3387.7051 | 885.1647 | 0.0001485 | 182 | 14.8038 | 4.4113 | 3.3877 | 0.88516 | 0.0001485
| 454.15 | 1500000 | 4407.2705 | 3391.7856 | 886.254 | 0.00014938 | 181 | 14.8038 | 4.4073 | 3.3918 | 0.88625 | 0.00014938
| 453.15 | 1500000 | 4403.3149 | 3395.8821 | 887.3381 | 0.00015026 | 180 | 14.8038 | 4.4033 | 3.3959 | 0.88734 | 0.00015026
| 452.15 | 1500000 | 4399.415 | 3399.9939 | 888.4171 | 0.00015116 | 179 | 14.8038 | 4.3994 | 3.4 | 0.88842 | 0.00015116
| 451.15 | 1500000 | 4395.5698 | 3404.1211 | 889.491 | 0.00015207 | 178 | 14.8038 | 4.3956 | 3.4041 | 0.88949 | 0.00015207
| 450.15 | 1500000 | 4391.7783 | 3408.2637 | 890.5598 | 0.00015298 | 177 | 14.8038 | 4.3918 | 3.4083 | 0.89056 | 0.00015298
| 449.15 | 1500000 | 4388.0396 | 3412.4211 | 891.6235 | 0.00015391 | 176 | 14.8038 | 4.388 | 3.4124 | 0.89162 | 0.00015391
| 448.15 | 1500000 | 4384.353 | 3416.5938 | 892.6822 | 0.00015485 | 175 | 14.8038 | 4.3844 | 3.4166 | 0.89268 | 0.00015485
| 447.15 | 1500000 | 4380.7178 | 3420.7812 | 893.7358 | 0.0001558 | 174 | 14.8038 | 4.3807 | 3.4208 | 0.89374 | 0.0001558
| 446.15 | 1500000 | 4377.1328 | 3424.9836 | 894.7845 | 0.00015677 | 173 | 14.8038 | 4.3771 | 3.425 | 0.89478 | 0.00015677
| 445.15 | 1500000 | 4373.5972 | 3429.2007 | 895.8283 | 0.00015774 | 172 | 14.8038 | 4.3736 | 3.4292 | 0.89583 | 0.00015774
| 444.15 | 1500000 | 4370.1108 | 3433.4324 | 896.8672 | 0.00015873 | 171 | 14.8038 | 4.3701 | 3.4334 | 0.89687 | 0.00015873
| 443.15 | 1500000 | 4366.6724 | 3437.6787 | 897.9011 | 0.00015973 | 170 | 14.8038 | 4.3667 | 3.4377 | 0.8979 | 0.00015973
| 442.15 | 1500000 | 4363.2812 | 3441.9392 | 898.9302 | 0.00016074 | 169 | 14.8038 | 4.3633 | 3.4419 | 0.89893 | 0.00016074
| 441.15 | 1500000 | 4359.9365 | 3446.2141 | 899.9545 | 0.00016177 | 168 | 14.8038 | 4.3599 | 3.4462 | 0.89995 | 0.00016177
| 440.15 | 1500000 | 4356.6377 | 3450.5032 | 900.9739 | 0.00016281 | 167 | 14.8038 | 4.3566 | 3.4505 | 0.90097 | 0.00016281
| 439.15 | 1500000 | 4353.3843 | 3454.8064 | 901.9885 | 0.00016386 | 166 | 14.8038 | 4.3534 | 3.4548 | 0.90199 | 0.00016386
| 438.15 | 1500000 | 4350.1753 | 3459.1238 | 902.9984 | 0.00016492 | 165 | 14.8038 | 4.3502 | 3.4591 | 0.903 | 0.00016492
| 437.15 | 1500000 | 4347.0103 | 3463.4548 | 904.0035 | 0.000166 | 164 | 14.8038 | 4.347 | 3.4635 | 0.904 | 0.000166
| 436.15 | 1500000 | 4343.8882 | 3467.7998 | 905.004 | 0.00016709 | 163 | 14.8038 | 4.3439 | 3.4678 | 0.905 | 0.00016709
| 435.15 | 1500000 | 4340.8091 | 3472.1584 | 905.9996 | 0.0001682 | 162 | 14.8038 | 4.3408 | 3.4722 | 0.906 | 0.0001682
| 434.15 | 1500000 | 4337.7715 | 3476.5308 | 906.9907 | 0.00016932 | 161 | 14.8038 | 4.3378 | 3.4765 | 0.90699 | 0.00016932
| 433.15 | 1500000 | 4334.7754 | 3480.9165 | 907.977 | 0.00017046 | 160 | 14.8038 | 4.3348 | 3.4809 | 0.90798 | 0.00017046
| 432.15 | 1500000 | 4331.8198 | 3485.3157 | 908.9587 | 0.00017161 | 159 | 14.8038 | 4.3318 | 3.4853 | 0.90896 | 0.00017161
| 431.15 | 1500000 | 4328.9043 | 3489.7283 | 909.9357 | 0.00017278 | 158 | 14.8038 | 4.3289 | 3.4897 | 0.90994 | 0.00017278
| 430.15 | 1500000 | 4326.0283 | 3494.1541 | 910.9082 | 0.00017396 | 157 | 14.8038 | 4.326 | 3.4942 | 0.91091 | 0.00017396
| 429.15 | 1500000 | 4323.1909 | 3498.593 | 911.8761 | 0.00017516 | 156 | 14.8038 | 4.3232 | 3.4986 | 0.91188 | 0.00017516
| 428.15 | 1500000 | 4320.3926 | 3503.0452 | 912.8394 | 0.00017638 | 155 | 14.8038 | 4.3204 | 3.503 | 0.91284 | 0.00017638
| 427.15 | 1500000 | 4317.6318 | 3507.5103 | 913.7981 | 0.00017761 | 154 | 14.8038 | 4.3176 | 3.5075 | 0.9138 | 0.00017761
| 426.15 | 1500000 | 4314.9082 | 3511.9883 | 914.7523 | 0.00017886 | 153 | 14.8038 | 4.3149 | 3.512 | 0.91475 | 0.00017886
| 425.15 | 1500000 | 4312.2217 | 3516.479 | 915.7019 | 0.00018013 | 152 | 14.8038 | 4.3122 | 3.5165 | 0.9157 | 0.00018013
| 424.15 | 1500000 | 4309.5713 | 3520.9824 | 916.647 | 0.00018142 | 151 | 14.8038 | 4.3096 | 3.521 | 0.91665 | 0.00018142
| 423.15 | 1500000 | 4306.9565 | 3525.4988 | 917.5876 | 0.00018272 | 150 | 14.8038 | 4.307 | 3.5255 | 0.91759 | 0.00018272
| 422.15 | 1500000 | 4304.377 | 3530.0273 | 918.5238 | 0.00018404 | 149 | 14.8038 | 4.3044 | 3.53 | 0.91852 | 0.00018404
| 421.15 | 1500000 | 4301.8325 | 3534.5686 | 919.4554 | 0.00018538 | 148 | 14.8038 | 4.3018 | 3.5346 | 0.91946 | 0.00018538
| 420.15 | 1500000 | 4299.3223 | 3539.1223 | 920.3826 | 0.00018674 | 147 | 14.8038 | 4.2993 | 3.5391 | 0.92038 | 0.00018674
| 419.15 | 1500000 | 4296.8457 | 3543.6882 | 921.3054 | 0.00018812 | 146 | 14.8038 | 4.2968 | 3.5437 | 0.92131 | 0.00018812
| 418.15 | 1500000 | 4294.4028 | 3548.2666 | 922.2236 | 0.00018952 | 145 | 14.8038 | 4.2944 | 3.5483 | 0.92222 | 0.00018952
| 417.15 | 1500000 | 4291.9927 | 3552.8569 | 923.1375 | 0.00019094 | 144 | 14.8038 | 4.292 | 3.5529 | 0.92314 | 0.00019094
| 416.15 | 1500000 | 4289.6152 | 3557.4595 | 924.0469 | 0.00019238 | 143 | 14.8038 | 4.2896 | 3.5575 | 0.92405 | 0.00019238
| 415.15 | 1500000 | 4287.27 | 3562.0737 | 924.952 | 0.00019384 | 142 | 14.8038 | 4.2873 | 3.5621 | 0.92495 | 0.00019384
| 414.15 | 1500000 | 4284.9565 | 3566.7002 | 925.8525 | 0.00019533 | 141 | 14.8038 | 4.285 | 3.5667 | 0.92585 | 0.00019533
| 413.15 | 1500000 | 4282.6738 | 3571.3386 | 926.7487 | 0.00019683 | 140 | 14.8038 | 4.2827 | 3.5713 | 0.92675 | 0.00019683
| 412.15 | 1500000 | 4280.4229 | 3575.9885 | 927.6406 | 0.00019836 | 139 | 14.8038 | 4.2804 | 3.576 | 0.92764 | 0.00019836
| 411.15 | 1500000 | 4278.2017 | 3580.6504 | 928.528 | 0.00019991 | 138 | 14.8038 | 4.2782 | 3.5807 | 0.92853 | 0.00019991
| 410.15 | 1500000 | 4276.0112 | 3585.3237 | 929.411 | 0.00020149 | 137 | 14.8038 | 4.276 | 3.5853 | 0.92941 | 0.00020149
| 409.15 | 1500000 | 4273.8501 | 3590.0088 | 930.2897 | 0.00020309 | 136 | 14.8038 | 4.2739 | 3.59 | 0.93029 | 0.00020309
| 408.15 | 1500000 | 4271.7188 | 3594.7051 | 931.1639 | 0.00020471 | 135 | 14.8038 | 4.2717 | 3.5947 | 0.93116 | 0.00020471
| 407.15 | 1500000 | 4269.6162 | 3599.4128 | 932.0339 | 0.00020636 | 134 | 14.8038 | 4.2696 | 3.5994 | 0.93203 | 0.00020636
| 406.15 | 1500000 | 4267.5425 | 3604.1321 | 932.8994 | 0.00020803 | 133 | 14.8038 | 4.2675 | 3.6041 | 0.9329 | 0.00020803
| 405.15 | 1500000 | 4265.4971 | 3608.8623 | 933.7606 | 0.00020973 | 132 | 14.8038 | 4.2655 | 3.6089 | 0.93376 | 0.00020973
| 404.15 | 1500000 | 4263.4795 | 3613.604 | 934.6175 | 0.00021146 | 131 | 14.8038 | 4.2635 | 3.6136 | 0.93462 | 0.00021146
| 403.15 | 1500000 | 4261.4902 | 3618.3567 | 935.47 | 0.00021321 | 130 | 14.8038 | 4.2615 | 3.6184 | 0.93547 | 0.00021321
| 402.15 | 1500000 | 4259.5278 | 3623.1204 | 936.3181 | 0.000215 | 129 | 14.8038 | 4.2595 | 3.6231 | 0.93632 | 0.000215
| 401.15 | 1500000 | 4257.5928 | 3627.8948 | 937.1619 | 0.00021681 | 128 | 14.8038 | 4.2576 | 3.6279 | 0.93716 | 0.00021681
| 400.15 | 1500000 | 4255.6846 | 3632.6804 | 938.0013 | 0.00021865 | 127 | 14.8038 | 4.2557 | 3.6327 | 0.938 | 0.00021865
| 399.15 | 1500000 | 4253.8032 | 3637.4766 | 938.8364 | 0.00022051 | 126 | 14.8038 | 4.2538 | 3.6375 | 0.93884 | 0.00022051
| 398.15 | 1500000 | 4251.9478 | 3642.2834 | 939.6671 | 0.00022241 | 125 | 14.8038 | 4.2519 | 3.6423 | 0.93967 | 0.00022241
| 397.15 | 1500000 | 4250.1187 | 3647.1011 | 940.4935 | 0.00022435 | 124 | 14.8038 | 4.2501 | 3.6471 | 0.94049 | 0.00022435
| 396.15 | 1500000 | 4248.3149 | 3651.929 | 941.3156 | 0.00022631 | 123 | 14.8038 | 4.2483 | 3.6519 | 0.94132 | 0.00022631
| 395.15 | 1500000 | 4246.5366 | 3656.7676 | 942.1332 | 0.0002283 | 122 | 14.8038 | 4.2465 | 3.6568 | 0.94213 | 0.0002283
| 394.15 | 1500000 | 4244.7837 | 3661.6165 | 942.9465 | 0.00023033 | 121 | 14.8038 | 4.2448 | 3.6616 | 0.94295 | 0.00023033
| 393.15 | 1500000 | 4243.0562 | 3666.4756 | 943.7555 | 0.00023239 | 120 | 14.8038 | 4.2431 | 3.6665 | 0.94376 | 0.00023239
| 392.15 | 1500000 | 4241.3525 | 3671.3447 | 944.5601 | 0.00023449 | 119 | 14.8038 | 4.2414 | 3.6713 | 0.94456 | 0.00023449
| 391.15 | 1500000 | 4239.6743 | 3676.2241 | 945.3603 | 0.00023662 | 118 | 14.8038 | 4.2397 | 3.6762 | 0.94536 | 0.00023662
| 390.15 | 1500000 | 4238.0195 | 3681.1135 | 946.1561 | 0.00023879 | 117 | 14.8038 | 4.238 | 3.6811 | 0.94616 | 0.00023879
| 389.15 | 1500000 | 4236.3896 | 3686.0129 | 946.9476 | 0.000241 | 116 | 14.8038 | 4.2364 | 3.686 | 0.94695 | 0.000241
| 388.15 | 1500000 | 4234.7832 | 3690.9219 | 947.7347 | 0.00024324 | 115 | 14.8038 | 4.2348 | 3.6909 | 0.94773 | 0.00024324
| 387.15 | 1500000 | 4233.2002 | 3695.8406 | 948.5174 | 0.00024552 | 114 | 14.8038 | 4.2332 | 3.6958 | 0.94852 | 0.00024552
| 386.15 | 1500000 | 4231.6411 | 3700.769 | 949.2957 | 0.00024784 | 113 | 14.8038 | 4.2316 | 3.7008 | 0.9493 | 0.00024784
| 385.15 | 1500000 | 4230.105 | 3705.7068 | 950.0695 | 0.00025021 | 112 | 14.8038 | 4.2301 | 3.7057 | 0.95007 | 0.00025021
| 384.15 | 1500000 | 4228.5923 | 3710.6538 | 950.839 | 0.00025261 | 111 | 14.8038 | 4.2286 | 3.7107 | 0.95084 | 0.00025261
| 383.15 | 1500000 | 4227.1025 | 3715.6101 | 951.6041 | 0.00025506 | 110 | 14.8038 | 4.2271 | 3.7156 | 0.9516 | 0.00025506
| 382.15 | 1500000 | 4225.6353 | 3720.5757 | 952.3646 | 0.00025755 | 109 | 14.8038 | 4.2256 | 3.7206 | 0.95236 | 0.00025755
| 381.15 | 1500000 | 4224.1909 | 3725.55 | 953.1208 | 0.00026009 | 108 | 14.8038 | 4.2242 | 3.7256 | 0.95312 | 0.00026009
| 380.15 | 1500000 | 4222.7686 | 3730.5334 | 953.8725 | 0.00026267 | 107 | 14.8038 | 4.2228 | 3.7305 | 0.95387 | 0.00026267
| 379.15 | 1500000 | 4221.3691 | 3735.5256 | 954.6198 | 0.0002653 | 106 | 14.8038 | 4.2214 | 3.7355 | 0.95462 | 0.0002653
| 378.15 | 1500000 | 4219.9912 | 3740.5261 | 955.3625 | 0.00026797 | 105 | 14.8038 | 4.22 | 3.7405 | 0.95536 | 0.00026797
| 377.15 | 1500000 | 4218.6357 | 3745.5352 | 956.1008 | 0.0002707 | 104 | 14.8038 | 4.2186 | 3.7455 | 0.9561 | 0.0002707
| 376.15 | 1500000 | 4217.3022 | 3750.5525 | 956.8345 | 0.00027347 | 103 | 14.8038 | 4.2173 | 3.7506 | 0.95683 | 0.00027347
| 375.15 | 1500000 | 4215.9902 | 3755.5781 | 957.5638 | 0.0002763 | 102 | 14.8038 | 4.216 | 3.7556 | 0.95756 | 0.0002763
| 374.15 | 1500000 | 4214.7002 | 3760.6116 | 958.2885 | 0.00027918 | 101 | 14.8038 | 4.2147 | 3.7606 | 0.95829 | 0.00027918
| 373.15 | 1500000 | 4213.4316 | 3765.6526 | 959.0087 | 0.00028212 | 100 | 14.8038 | 4.2134 | 3.7657 | 0.95901 | 0.00028212
| 372.15 | 1500000 | 4212.1846 | 3770.7014 | 959.7242 | 0.00028511 | 99 | 14.8038 | 4.2122 | 3.7707 | 0.95972 | 0.00028511
| 371.15 | 1500000 | 4210.9585 | 3775.7578 | 960.4352 | 0.00028816 | 98 | 14.8038 | 4.211 | 3.7758 | 0.96044 | 0.00028816
| 370.15 | 1500000 | 4209.7539 | 3780.8213 | 961.1417 | 0.00029127 | 97 | 14.8038 | 4.2098 | 3.7808 | 0.96114 | 0.00029127
| 369.15 | 1500000 | 4208.5703 | 3785.8918 | 961.8434 | 0.00029443 | 96 | 14.8038 | 4.2086 | 3.7859 | 0.96184 | 0.00029443
| 368.15 | 1500000 | 4207.4082 | 3790.9692 | 962.5406 | 0.00029766 | 95 | 14.8038 | 4.2074 | 3.791 | 0.96254 | 0.00029766
| 367.15 | 1500000 | 4206.2666 | 3796.053 | 963.2332 | 0.00030095 | 94 | 14.8038 | 4.2063 | 3.7961 | 0.96323 | 0.00030095
| 366.15 | 1500000 | 4205.146 | 3801.1433 | 963.921 | 0.00030431 | 93 | 14.8038 | 4.2051 | 3.8011 | 0.96392 | 0.00030431
| 365.15 | 1500000 | 4204.0464 | 3806.24 | 964.6041 | 0.00030773 | 92 | 14.8038 | 4.204 | 3.8062 | 0.9646 | 0.00030773
| 364.15 | 1500000 | 4202.9678 | 3811.3423 | 965.2826 | 0.00031122 | 91 | 14.8038 | 4.203 | 3.8113 | 0.96528 | 0.00031122
| 363.15 | 1500000 | 4201.9097 | 3816.4502 | 965.9563 | 0.00031479 | 90 | 14.8038 | 4.2019 | 3.8165 | 0.96596 | 0.00031479
| 362.15 | 1500000 | 4200.8721 | 3821.5635 | 966.6252 | 0.00031842 | 89 | 14.8038 | 4.2009 | 3.8216 | 0.96663 | 0.00031842
| 361.15 | 1500000 | 4199.855 | 3826.6821 | 967.2894 | 0.00032213 | 88 | 14.8038 | 4.1999 | 3.8267 | 0.96729 | 0.00032213
| 360.15 | 1500000 | 4198.8589 | 3831.8052 | 967.9487 | 0.00032591 | 87 | 14.8038 | 4.1989 | 3.8318 | 0.96795 | 0.00032591
| 359.15 | 1500000 | 4197.8828 | 3836.9329 | 968.6032 | 0.00032978 | 86 | 14.8038 | 4.1979 | 3.8369 | 0.9686 | 0.00032978
| 358.15 | 1500000 | 4196.9277 | 3842.0649 | 969.2529 | 0.00033372 | 85 | 14.8038 | 4.1969 | 3.8421 | 0.96925 | 0.00033372
| 357.15 | 1500000 | 4195.9927 | 3847.2004 | 969.8976 | 0.00033774 | 84 | 14.8038 | 4.196 | 3.8472 | 0.9699 | 0.00033774
| 356.15 | 1500000 | 4195.0781 | 3852.3398 | 970.5375 | 0.00034185 | 83 | 14.8038 | 4.1951 | 3.8523 | 0.97054 | 0.00034185
| 355.15 | 1500000 | 4194.1841 | 3857.4822 | 971.1724 | 0.00034605 | 82 | 14.8038 | 4.1942 | 3.8575 | 0.97117 | 0.00034605
| 354.15 | 1500000 | 4193.3105 | 3862.6272 | 971.8023 | 0.00035034 | 81 | 14.8038 | 4.1933 | 3.8626 | 0.9718 | 0.00035034
| 353.15 | 1500000 | 4192.4575 | 3867.7747 | 972.4272 | 0.00035472 | 80 | 14.8038 | 4.1925 | 3.8678 | 0.97243 | 0.00035472
| 352.15 | 1500000 | 4191.6245 | 3872.9241 | 973.0471 | 0.0003592 | 79 | 14.8038 | 4.1916 | 3.8729 | 0.97305 | 0.0003592
| 351.15 | 1500000 | 4190.8115 | 3878.075 | 973.6619 | 0.00036377 | 78 | 14.8038 | 4.1908 | 3.8781 | 0.97366 | 0.00036377
| 350.15 | 1500000 | 4190.019 | 3883.2271 | 974.2717 | 0.00036844 | 77 | 14.8038 | 4.19 | 3.8832 | 0.97427 | 0.00036844
| 349.15 | 1500000 | 4189.2471 | 3888.3796 | 974.8762 | 0.00037322 | 76 | 14.8038 | 4.1892 | 3.8884 | 0.97488 | 0.00037322
| 348.15 | 1500000 | 4188.4956 | 3893.5325 | 975.4756 | 0.00037811 | 75 | 14.8038 | 4.1885 | 3.8935 | 0.97548 | 0.00037811
| 347.15 | 1500000 | 4187.7642 | 3898.6851 | 976.0699 | 0.0003831 | 74 | 14.8038 | 4.1878 | 3.8987 | 0.97607 | 0.0003831
| 346.15 | 1500000 | 4187.0527 | 3903.8367 | 976.6589 | 0.00038821 | 73 | 14.8038 | 4.1871 | 3.9038 | 0.97666 | 0.00038821
| 345.15 | 1500000 | 4186.3618 | 3908.9868 | 977.2426 | 0.00039343 | 72 | 14.8038 | 4.1864 | 3.909 | 0.97724 | 0.00039343
| 344.15 | 1500000 | 4185.6914 | 3914.1353 | 977.8209 | 0.00039878 | 71 | 14.8038 | 4.1857 | 3.9141 | 0.97782 | 0.00039878
| 343.15 | 1500000 | 4185.041 | 3919.281 | 978.3939 | 0.00040425 | 70 | 14.8038 | 4.185 | 3.9193 | 0.97839 | 0.00040425
| 342.15 | 1500000 | 4184.4111 | 3924.4236 | 978.9615 | 0.00040985 | 69 | 14.8038 | 4.1844 | 3.9244 | 0.97896 | 0.00040985
| 341.15 | 1500000 | 4183.8013 | 3929.5625 | 979.5237 | 0.00041558 | 68 | 14.8038 | 4.1838 | 3.9296 | 0.97952 | 0.00041558
| 340.15 | 1500000 | 4183.2119 | 3934.6968 | 980.0804 | 0.00042144 | 67 | 14.8038 | 4.1832 | 3.9347 | 0.98008 | 0.00042144
| 339.15 | 1500000 | 4182.6431 | 3939.8262 | 980.6315 | 0.00042745 | 66 | 14.8038 | 4.1826 | 3.9398 | 0.98063 | 0.00042745
| 338.15 | 1500000 | 4182.0947 | 3944.95 | 981.1771 | 0.0004336 | 65 | 14.8038 | 4.1821 | 3.9449 | 0.98118 | 0.0004336
| 337.15 | 1500000 | 4181.5664 | 3950.0669 | 981.717 | 0.0004399 | 64 | 14.8038 | 4.1816 | 3.9501 | 0.98172 | 0.0004399
| 336.15 | 1500000 | 4181.0586 | 3955.1768 | 982.2513 | 0.00044636 | 63 | 14.8038 | 4.1811 | 3.9552 | 0.98225 | 0.00044636
| 335.15 | 1500000 | 4180.5713 | 3960.2786 | 982.7798 | 0.00045298 | 62 | 14.8038 | 4.1806 | 3.9603 | 0.98278 | 0.00045298
| 334.15 | 1500000 | 4180.1045 | 3965.3716 | 983.3026 | 0.00045976 | 61 | 14.8038 | 4.1801 | 3.9654 | 0.9833 | 0.00045976
| 333.15 | 1500000 | 4179.6577 | 3970.4548 | 983.8195 | 0.00046671 | 60 | 14.8038 | 4.1797 | 3.9705 | 0.98382 | 0.00046671
| 332.15 | 1500000 | 4179.2319 | 3975.5278 | 984.3305 | 0.00047385 | 59 | 14.8038 | 4.1792 | 3.9755 | 0.98433 | 0.00047385
| 331.15 | 1500000 | 4178.8267 | 3980.5891 | 984.8356 | 0.00048116 | 58 | 14.8038 | 4.1788 | 3.9806 | 0.98484 | 0.00048116
| 330.15 | 1500000 | 4178.4419 | 3985.6382 | 985.3347 | 0.00048866 | 57 | 14.8038 | 4.1784 | 3.9856 | 0.98533 | 0.00048866
| 329.15 | 1500000 | 4178.0776 | 3990.6738 | 985.8277 | 0.00049636 | 56 | 14.8038 | 4.1781 | 3.9907 | 0.98583 | 0.00049636
| 328.15 | 1500000 | 4177.7344 | 3995.6953 | 986.3146 | 0.00050427 | 55 | 14.8038 | 4.1777 | 3.9957 | 0.98631 | 0.00050427
| 327.15 | 1500000 | 4177.4116 | 4000.7014 | 986.7953 | 0.00051238 | 54 | 14.8038 | 4.1774 | 4.0007 | 0.9868 | 0.00051238
| 326.15 | 1500000 | 4177.1094 | 4005.6912 | 987.2697 | 0.00052071 | 53 | 14.8038 | 4.1771 | 4.0057 | 0.98727 | 0.00052071
| 325.15 | 1500000 | 4176.8286 | 4010.6636 | 987.7379 | 0.00052927 | 52 | 14.8038 | 4.1768 | 4.0107 | 0.98774 | 0.00052927
| 324.15 | 1500000 | 4176.5684 | 4015.6174 | 988.1996 | 0.00053806 | 51 | 14.8038 | 4.1766 | 4.0156 | 0.9882 | 0.00053806
| 323.15 | 1500000 | 4176.3291 | 4020.5515 | 988.6549 | 0.00054709 | 50 | 14.8038 | 4.1763 | 4.0206 | 0.98865 | 0.00054709
| 322.15 | 1500000 | 4176.1108 | 4025.4648 | 989.1037 | 0.00055638 | 49 | 14.8038 | 4.1761 | 4.0255 | 0.9891 | 0.00055638
| 321.15 | 1500000 | 4175.9141 | 4030.356 | 989.5458 | 0.00056593 | 48 | 14.8038 | 4.1759 | 4.0304 | 0.98955 | 0.00056593
| 320.15 | 1500000 | 4175.7383 | 4035.2239 | 989.9813 | 0.00057575 | 47 | 14.8038 | 4.1757 | 4.0352 | 0.98998 | 0.00057575
| 319.15 | 1500000 | 4175.584 | 4040.0671 | 990.41 | 0.00058586 | 46 | 14.8038 | 4.1756 | 4.0401 | 0.99041 | 0.00058586
| 318.15 | 1500000 | 4175.4512 | 4044.8845 | 990.8319 | 0.00059626 | 45 | 14.8038 | 4.1755 | 4.0449 | 0.99083 | 0.00059626
| 317.15 | 1500000 | 4175.3403 | 4049.6746 | 991.2468 | 0.00060696 | 44 | 14.8038 | 4.1753 | 4.0497 | 0.99125 | 0.00060696
| 316.15 | 1500000 | 4175.2515 | 4054.436 | 991.6547 | 0.00061798 | 43 | 14.8038 | 4.1753 | 4.0544 | 0.99165 | 0.00061798
| 315.15 | 1500000 | 4175.1846 | 4059.1675 | 992.0555 | 0.00062934 | 42 | 14.8038 | 4.1752 | 4.0592 | 0.99206 | 0.00062934
| 314.15 | 1500000 | 4175.1396 | 4063.8672 | 992.4491 | 0.00064103 | 41 | 14.8038 | 4.1751 | 4.0639 | 0.99245 | 0.00064103
| 313.15 | 1500000 | 4175.1182 | 4068.5342 | 992.8354 | 0.00065309 | 40 | 14.8038 | 4.1751 | 4.0685 | 0.99284 | 0.00065309
| 312.15 | 1500000 | 4175.1191 | 4073.1665 | 993.2143 | 0.00066552 | 39 | 14.8038 | 4.1751 | 4.0732 | 0.99321 | 0.00066552
| 311.15 | 1500000 | 4175.144 | 4077.7629 | 993.5857 | 0.00067834 | 38 | 14.8038 | 4.1751 | 4.0778 | 0.99359 | 0.00067834
| 310.15 | 1500000 | 4175.1919 | 4082.3215 | 993.9495 | 0.00069157 | 37 | 14.8038 | 4.1752 | 4.0823 | 0.99395 | 0.00069157
| 309.15 | 1500000 | 4175.2646 | 4086.8413 | 994.3055 | 0.00070523 | 36 | 14.8038 | 4.1753 | 4.0868 | 0.99431 | 0.00070523
| 308.15 | 1500000 | 4175.3618 | 4091.3198 | 994.6538 | 0.00071932 | 35 | 14.8038 | 4.1754 | 4.0913 | 0.99465 | 0.00071932
| 307.15 | 1500000 | 4175.4849 | 4095.7563 | 994.9941 | 0.00073389 | 34 | 14.8038 | 4.1755 | 4.0958 | 0.99499 | 0.00073389
| 306.15 | 1500000 | 4175.6333 | 4100.1484 | 995.3262 | 0.00074893 | 33 | 14.8038 | 4.1756 | 4.1001 | 0.99533 | 0.00074893
| 305.15 | 1500000 | 4175.8091 | 4104.4946 | 995.6503 | 0.00076449 | 32 | 14.8038 | 4.1758 | 4.1045 | 0.99565 | 0.00076449
| 304.15 | 1500000 | 4176.0122 | 4108.7939 | 995.9659 | 0.00078057 | 31 | 14.8038 | 4.176 | 4.1088 | 0.99597 | 0.00078057
| 303.15 | 1500000 | 4176.2441 | 4113.0435 | 996.2731 | 0.00079721 | 30 | 14.8038 | 4.1762 | 4.113 | 0.99627 | 0.00079721
| 302.15 | 1500000 | 4176.5054 | 4117.2422 | 996.5717 | 0.00081444 | 29 | 14.8038 | 4.1765 | 4.1172 | 0.99657 | 0.00081444
| 301.15 | 1500000 | 4176.7979 | 4121.3887 | 996.8615 | 0.00083227 | 28 | 14.8038 | 4.1768 | 4.1214 | 0.99686 | 0.00083227
| 300.15 | 1500000 | 4177.123 | 4125.4805 | 997.1425 | 0.00085075 | 27 | 14.8038 | 4.1771 | 4.1255 | 0.99714 | 0.00085075
| 299.15 | 1500000 | 4177.4819 | 4129.5161 | 997.4143 | 0.0008699 | 26 | 14.8038 | 4.1775 | 4.1295 | 0.99741 | 0.0008699
| 298.15 | 1500000 | 4177.8765 | 4133.4941 | 997.6769 | 0.00088976 | 25 | 14.8038 | 4.1779 | 4.1335 | 0.99768 | 0.00088976
| 297.15 | 1500000 | 4178.3086 | 4137.4131 | 997.9301 | 0.00091036 | 24 | 14.8038 | 4.1783 | 4.1374 | 0.99793 | 0.00091036
| 296.15 | 1500000 | 4178.7808 | 4141.2705 | 998.1736 | 0.00093174 | 23 | 14.8038 | 4.1788 | 4.1413 | 0.99817 | 0.00093174
| 295.15 | 1500000 | 4179.2949 | 4145.0654 | 998.4075 | 0.00095395 | 22 | 14.8038 | 4.1793 | 4.1451 | 0.99841 | 0.00095395
| 294.15 | 1500000 | 4179.8545 | 4148.7959 | 998.6313 | 0.00097702 | 21 | 14.8038 | 4.1799 | 4.1488 | 0.99863 | 0.00097702
| 293.15 | 1500000 | 4180.4619 | 4152.4604 | 998.845 | 0.001001 | 20 | 14.8038 | 4.1805 | 4.1525 | 0.99884 | 0.001001
| 292.15 | 1500000 | 4181.1211 | 4156.0576 | 999.0482 | 0.001026 | 19 | 14.8038 | 4.1811 | 4.1561 | 0.99905 | 0.001026
| 291.15 | 1500000 | 4181.8354 | 4159.5859 | 999.2409 | 0.0010519 | 18 | 14.8038 | 4.1818 | 4.1596 | 0.99924 | 0.0010519
| 290.15 | 1500000 | 4182.6099 | 4163.0444 | 999.4227 | 0.001079 | 17 | 14.8038 | 4.1826 | 4.163 | 0.99942 | 0.001079
| 289.15 | 1500000 | 4183.4487 | 4166.4312 | 999.5933 | 0.0011072 | 16 | 14.8038 | 4.1834 | 4.1664 | 0.99959 | 0.0011072
| 288.15 | 1500000 | 4184.3569 | 4169.7456 | 999.7526 | 0.0011366 | 15 | 14.8038 | 4.1844 | 4.1697 | 0.99975 | 0.0011366
| 287.15 | 1500000 | 4185.3413 | 4172.9858 | 999.9003 | 0.0011672 | 14 | 14.8038 | 4.1853 | 4.173 | 0.9999 | 0.0011672
| 286.15 | 1500000 | 4186.4077 | 4176.1519 | 1000.0361 | 0.0011993 | 13 | 14.8038 | 4.1864 | 4.1762 | 1 | 0.0011993
| 285.15 | 1500000 | 4187.5635 | 4179.2422 | 1000.1596 | 0.0012327 | 12 | 14.8038 | 4.1876 | 4.1792 | 1.0002 | 0.0012327
| 284.15 | 1500000 | 4188.8174 | 4182.2563 | 1000.2706 | 0.0012677 | 11 | 14.8038 | 4.1888 | 4.1823 | 1.0003 | 0.0012677
| 283.15 | 1500000 | 4190.1772 | 4185.1943 | 1000.3688 | 0.0013044 | 10 | 14.8038 | 4.1902 | 4.1852 | 1.0004 | 0.0013044
| 282.15 | 1500000 | 4191.6543 | 4188.0552 | 1000.4537 | 0.0013427 | 9 | 14.8038 | 4.1917 | 4.1881 | 1.0005 | 0.0013427
| 281.15 | 1500000 | 4193.2593 | 4190.8389 | 1000.525 | 0.0013829 | 8 | 14.8038 | 4.1933 | 4.1908 | 1.0005 | 0.0013829
| 280.15 | 1500000 | 4195.0039 | 4193.5454 | 1000.5824 | 0.0014251 | 7 | 14.8038 | 4.195 | 4.1935 | 1.0006 | 0.0014251
| 279.15 | 1500000 | 4196.9023 | 4196.1758 | 1000.6254 | 0.0014693 | 6 | 14.8038 | 4.1969 | 4.1962 | 1.0006 | 0.0014693
| 278.15 | 1500000 | 4198.9697 | 4198.73 | 1000.6535 | 0.0015158 | 5 | 14.8038 | 4.199 | 4.1987 | 1.0007 | 0.0015158
| 277.15 | 1500000 | 4201.2227 | 4201.2085 | 1000.6664 | 0.0015647 | 4 | 14.8038 | 4.2012 | 4.2012 | 1.0007 | 0.0015647
| 276.15 | 1500000 | 4203.6797 | 4203.6128 | 1000.6635 | 0.0016162 | 3 | 14.8038 | 4.2037 | 4.2036 | 1.0007 | 0.0016162
| 275.15 | 1500000 | 4206.3613 | 4205.9443 | 1000.6443 | 0.0016704 | 2 | 14.8038 | 4.2064 | 4.2059 | 1.0006 | 0.0016704
| 274.15 | 1500000 | 4209.2905 | 4208.2046 | 1000.6082 | 0.0017276 | 0.99999 | 14.8038 | 4.2093 | 4.2082 | 1.0006 | 0.0017276
| 273.15 | 1500000 | 4212.4917 | 4210.3955 | 1000.5547 | 0.001788 | -6.1035e-06 | 14.8038 | 4.2125 | 4.2104 | 1.0006 | 0.001788
| 473.15 | 1400000 | 2780.7251 | 1947.9 | 6.9925 | 1.5765e-05 | 200 | 13.8169 | 2.7807 | 1.9479 | 0.0069925 | 1.5765e-05
| 472.15 | 1400000 | 2804.1023 | 1962.2478 | 7.0144 | 1.5721e-05 | 199 | 13.8169 | 2.8041 | 1.9622 | 0.0070144 | 1.5721e-05
| 471.15 | 1400000 | 2829.3369 | 1977.84 | 7.0366 | 1.5676e-05 | 198 | 13.8169 | 2.8293 | 1.9778 | 0.0070366 | 1.5676e-05
| 470.15 | 1400000 | 2856.6567 | 1994.8295 | 7.0591 | 1.5631e-05 | 197 | 13.8169 | 2.8567 | 1.9948 | 0.0070591 | 1.5631e-05
| 469.15 | 1400000 | 2886.3206 | 2013.3895 | 7.0819 | 1.5586e-05 | 196 | 13.8169 | 2.8863 | 2.0134 | 0.0070819 | 1.5586e-05
| 468.15 | 1400000 | 4469.5791 | 3336.2014 | 870.4404 | 0.00013795 | 195 | 13.8169 | 4.4696 | 3.3362 | 0.87044 | 0.00013795
| 467.15 | 1400000 | 4464.7319 | 3340.0693 | 871.6012 | 0.00013871 | 194 | 13.8169 | 4.4647 | 3.3401 | 0.8716 | 0.00013871
| 466.15 | 1400000 | 4459.9556 | 3343.9543 | 872.7563 | 0.00013947 | 193 | 13.8169 | 4.46 | 3.344 | 0.87276 | 0.00013947
| 465.15 | 1400000 | 4455.2485 | 3347.8562 | 873.9056 | 0.00014025 | 192 | 13.8169 | 4.4552 | 3.3479 | 0.87391 | 0.00014025
| 464.15 | 1400000 | 4450.6099 | 3351.7751 | 875.0494 | 0.00014103 | 191 | 13.8169 | 4.4506 | 3.3518 | 0.87505 | 0.00014103
| 463.15 | 1400000 | 4446.0376 | 3355.7107 | 876.1876 | 0.00014182 | 190 | 13.8169 | 4.446 | 3.3557 | 0.87619 | 0.00014182
| 462.15 | 1400000 | 4441.5317 | 3359.6628 | 877.3202 | 0.00014262 | 189 | 13.8169 | 4.4415 | 3.3597 | 0.87732 | 0.00014262
| 461.15 | 1400000 | 4437.0908 | 3363.6313 | 878.4473 | 0.00014343 | 188 | 13.8169 | 4.4371 | 3.3636 | 0.87845 | 0.00014343
| 460.15 | 1400000 | 4432.7129 | 3367.6165 | 879.569 | 0.00014425 | 187 | 13.8169 | 4.4327 | 3.3676 | 0.87957 | 0.00014425
| 459.15 | 1400000 | 4428.3979 | 3371.6179 | 880.6853 | 0.00014507 | 186 | 13.8169 | 4.4284 | 3.3716 | 0.88069 | 0.00014507
| 458.15 | 1400000 | 4424.1445 | 3375.6353 | 881.7962 | 0.00014591 | 185 | 13.8169 | 4.4241 | 3.3756 | 0.8818 | 0.00014591
| 457.15 | 1400000 | 4419.9512 | 3379.6689 | 882.9017 | 0.00014675 | 184 | 13.8169 | 4.42 | 3.3797 | 0.8829 | 0.00014675
| 456.15 | 1400000 | 4415.8179 | 3383.7183 | 884.002 | 0.00014761 | 183 | 13.8169 | 4.4158 | 3.3837 | 0.884 | 0.00014761
| 455.15 | 1400000 | 4411.7427 | 3387.7837 | 885.097 | 0.00014848 | 182 | 13.8169 | 4.4117 | 3.3878 | 0.8851 | 0.00014848
| 454.15 | 1400000 | 4407.7246 | 3391.8647 | 886.1868 | 0.00014935 | 181 | 13.8169 | 4.4077 | 3.3919 | 0.88619 | 0.00014935
| 453.15 | 1400000 | 4403.7637 | 3395.9612 | 887.2713 | 0.00015024 | 180 | 13.8169 | 4.4038 | 3.396 | 0.88727 | 0.00015024
| 452.15 | 1400000 | 4399.8584 | 3400.0732 | 888.3507 | 0.00015113 | 179 | 13.8169 | 4.3999 | 3.4001 | 0.88835 | 0.00015113
| 451.15 | 1400000 | 4396.0078 | 3404.2007 | 889.425 | 0.00015204 | 178 | 13.8169 | 4.396 | 3.4042 | 0.88942 | 0.00015204
| 450.15 | 1400000 | 4392.2109 | 3408.3435 | 890.4941 | 0.00015296 | 177 | 13.8169 | 4.3922 | 3.4083 | 0.89049 | 0.00015296
| 449.15 | 1400000 | 4388.4668 | 3412.5012 | 891.5583 | 0.00015389 | 176 | 13.8169 | 4.3885 | 3.4125 | 0.89156 | 0.00015389
| 448.15 | 1400000 | 4384.7749 | 3416.6743 | 892.6173 | 0.00015483 | 175 | 13.8169 | 4.3848 | 3.4167 | 0.89262 | 0.00015483
| 447.15 | 1400000 | 4381.1348 | 3420.8621 | 893.6714 | 0.00015578 | 174 | 13.8169 | 4.3811 | 3.4209 | 0.89367 | 0.00015578
| 446.15 | 1400000 | 4377.5449 | 3425.0647 | 894.7205 | 0.00015674 | 173 | 13.8169 | 4.3775 | 3.4251 | 0.89472 | 0.00015674
| 445.15 | 1400000 | 4374.0044 | 3429.2822 | 895.7646 | 0.00015772 | 172 | 13.8169 | 4.374 | 3.4293 | 0.89576 | 0.00015772
| 444.15 | 1400000 | 4370.5132 | 3433.5142 | 896.8038 | 0.0001587 | 171 | 13.8169 | 4.3705 | 3.4335 | 0.8968 | 0.0001587
| 443.15 | 1400000 | 4367.0703 | 3437.7607 | 897.8382 | 0.0001597 | 170 | 13.8169 | 4.3671 | 3.4378 | 0.89784 | 0.0001597
| 442.15 | 1400000 | 4363.6743 | 3442.0217 | 898.8676 | 0.00016072 | 169 | 13.8169 | 4.3637 | 3.442 | 0.89887 | 0.00016072
| 441.15 | 1400000 | 4360.3257 | 3446.2969 | 899.8922 | 0.00016174 | 168 | 13.8169 | 4.3603 | 3.4463 | 0.89989 | 0.00016174
| 440.15 | 1400000 | 4357.0225 | 3450.5864 | 900.912 | 0.00016278 | 167 | 13.8169 | 4.357 | 3.4506 | 0.90091 | 0.00016278
| 439.15 | 1400000 | 4353.7646 | 3454.8901 | 901.927 | 0.00016383 | 166 | 13.8169 | 4.3538 | 3.4549 | 0.90193 | 0.00016383
| 438.15 | 1400000 | 4350.5518 | 3459.2078 | 902.9372 | 0.0001649 | 165 | 13.8169 | 4.3506 | 3.4592 | 0.90294 | 0.0001649
| 437.15 | 1400000 | 4347.3823 | 3463.5393 | 903.9427 | 0.00016598 | 164 | 13.8169 | 4.3474 | 3.4635 | 0.90394 | 0.00016598
| 436.15 | 1400000 | 4344.2563 | 3467.8845 | 904.9434 | 0.00016707 | 163 | 13.8169 | 4.3443 | 3.4679 | 0.90494 | 0.00016707
| 435.15 | 1400000 | 4341.1729 | 3472.2437 | 905.9394 | 0.00016818 | 162 | 13.8169 | 4.3412 | 3.4722 | 0.90594 | 0.00016818
| 434.15 | 1400000 | 4338.1313 | 3476.6165 | 906.9307 | 0.0001693 | 161 | 13.8169 | 4.3381 | 3.4766 | 0.90693 | 0.0001693
| 433.15 | 1400000 | 4335.1313 | 3481.0027 | 907.9174 | 0.00017044 | 160 | 13.8169 | 4.3351 | 3.481 | 0.90792 | 0.00017044
| 432.15 | 1400000 | 4332.1724 | 3485.4026 | 908.8994 | 0.00017159 | 159 | 13.8169 | 4.3322 | 3.4854 | 0.9089 | 0.00017159
| 431.15 | 1400000 | 4329.2529 | 3489.8157 | 909.8768 | 0.00017276 | 158 | 13.8169 | 4.3293 | 3.4898 | 0.90988 | 0.00017276
| 430.15 | 1400000 | 4326.3735 | 3494.2419 | 910.8495 | 0.00017394 | 157 | 13.8169 | 4.3264 | 3.4942 | 0.91085 | 0.00017394
| 429.15 | 1400000 | 4323.5332 | 3498.6816 | 911.8177 | 0.00017514 | 156 | 13.8169 | 4.3235 | 3.4987 | 0.91182 | 0.00017514
| 428.15 | 1400000 | 4320.731 | 3503.1343 | 912.7813 | 0.00017636 | 155 | 13.8169 | 4.3207 | 3.5031 | 0.91278 | 0.00017636
| 427.15 | 1400000 | 4317.9668 | 3507.5999 | 913.7403 | 0.00017759 | 154 | 13.8169 | 4.318 | 3.5076 | 0.91374 | 0.00017759
| 426.15 | 1400000 | 4315.2402 | 3512.0784 | 914.6948 | 0.00017884 | 153 | 13.8169 | 4.3152 | 3.5121 | 0.91469 | 0.00017884
| 425.15 | 1400000 | 4312.5503 | 3516.5698 | 915.6447 | 0.00018011 | 152 | 13.8169 | 4.3126 | 3.5166 | 0.91564 | 0.00018011
| 424.15 | 1400000 | 4309.8965 | 3521.074 | 916.5901 | 0.00018139 | 151 | 13.8169 | 4.3099 | 3.5211 | 0.91659 | 0.00018139
| 423.15 | 1400000 | 4307.2788 | 3525.5908 | 917.531 | 0.00018269 | 150 | 13.8169 | 4.3073 | 3.5256 | 0.91753 | 0.00018269
| 422.15 | 1400000 | 4304.6963 | 3530.1201 | 918.4674 | 0.00018402 | 149 | 13.8169 | 4.3047 | 3.5301 | 0.91847 | 0.00018402
| 421.15 | 1400000 | 4302.1489 | 3534.6621 | 919.3994 | 0.00018536 | 148 | 13.8169 | 4.3021 | 3.5347 | 0.9194 | 0.00018536
| 420.15 | 1400000 | 4299.6357 | 3539.2166 | 920.3268 | 0.00018672 | 147 | 13.8169 | 4.2996 | 3.5392 | 0.92033 | 0.00018672
| 419.15 | 1400000 | 4297.1562 | 3543.7832 | 921.2498 | 0.0001881 | 146 | 13.8169 | 4.2972 | 3.5438 | 0.92125 | 0.0001881
| 418.15 | 1400000 | 4294.7104 | 3548.3621 | 922.1683 | 0.00018949 | 145 | 13.8169 | 4.2947 | 3.5484 | 0.92217 | 0.00018949
| 417.15 | 1400000 | 4292.2979 | 3552.9531 | 923.0825 | 0.00019091 | 144 | 13.8169 | 4.2923 | 3.553 | 0.92308 | 0.00019091
| 416.15 | 1400000 | 4289.9175 | 3557.5564 | 923.9921 | 0.00019236 | 143 | 13.8169 | 4.2899 | 3.5576 | 0.92399 | 0.00019236
| 415.15 | 1400000 | 4287.5698 | 3562.1716 | 924.8974 | 0.00019382 | 142 | 13.8169 | 4.2876 | 3.5622 | 0.9249 | 0.00019382
| 414.15 | 1400000 | 4285.2534 | 3566.7988 | 925.7982 | 0.0001953 | 141 | 13.8169 | 4.2853 | 3.5668 | 0.9258 | 0.0001953
| 413.15 | 1400000 | 4282.9688 | 3571.438 | 926.6947 | 0.00019681 | 140 | 13.8169 | 4.283 | 3.5714 | 0.92669 | 0.00019681
| 412.15 | 1400000 | 4280.7148 | 3576.0889 | 927.5867 | 0.00019833 | 139 | 13.8169 | 4.2807 | 3.5761 | 0.92759 | 0.00019833
| 411.15 | 1400000 | 4278.4912 | 3580.7515 | 928.4744 | 0.00019989 | 138 | 13.8169 | 4.2785 | 3.5808 | 0.92847 | 0.00019989
| 410.15 | 1400000 | 4276.2983 | 3585.4258 | 929.3577 | 0.00020146 | 137 | 13.8169 | 4.2763 | 3.5854 | 0.92936 | 0.00020146
| 409.15 | 1400000 | 4274.1348 | 3590.1116 | 930.2365 | 0.00020306 | 136 | 13.8169 | 4.2741 | 3.5901 | 0.93024 | 0.00020306
| 408.15 | 1400000 | 4272.001 | 3594.8088 | 931.111 | 0.00020468 | 135 | 13.8169 | 4.272 | 3.5948 | 0.93111 | 0.00020468
| 407.15 | 1400000 | 4269.8965 | 3599.5176 | 931.9812 | 0.00020633 | 134 | 13.8169 | 4.2699 | 3.5995 | 0.93198 | 0.00020633
| 406.15 | 1400000 | 4267.8203 | 3604.2375 | 932.847 | 0.00020801 | 133 | 13.8169 | 4.2678 | 3.6042 | 0.93285 | 0.00020801
| 405.15 | 1400000 | 4265.7729 | 3608.969 | 933.7084 | 0.00020971 | 132 | 13.8169 | 4.2658 | 3.609 | 0.93371 | 0.00020971
| 404.15 | 1400000 | 4263.7534 | 3613.7114 | 934.5654 | 0.00021143 | 131 | 13.8169 | 4.2638 | 3.6137 | 0.93457 | 0.00021143
| 403.15 | 1400000 | 4261.7617 | 3618.4651 | 935.4182 | 0.00021319 | 130 | 13.8169 | 4.2618 | 3.6185 | 0.93542 | 0.00021319
| 402.15 | 1400000 | 4259.7979 | 3623.2297 | 936.2665 | 0.00021497 | 129 | 13.8169 | 4.2598 | 3.6232 | 0.93627 | 0.00021497
| 401.15 | 1400000 | 4257.8608 | 3628.0054 | 937.1105 | 0.00021678 | 128 | 13.8169 | 4.2579 | 3.628 | 0.93711 | 0.00021678
| 400.15 | 1400000 | 4255.9507 | 3632.7917 | 937.9501 | 0.00021862 | 127 | 13.8169 | 4.256 | 3.6328 | 0.93795 | 0.00021862
| 399.15 | 1400000 | 4254.0674 | 3637.5891 | 938.7854 | 0.00022049 | 126 | 13.8169 | 4.2541 | 3.6376 | 0.93879 | 0.00022049
| 398.15 | 1400000 | 4252.21 | 3642.397 | 939.6163 | 0.00022239 | 125 | 13.8169 | 4.2522 | 3.6424 | 0.93962 | 0.00022239
| 397.15 | 1400000 | 4250.3789 | 3647.2156 | 940.4429 | 0.00022432 | 124 | 13.8169 | 4.2504 | 3.6472 | 0.94044 | 0.00022432
| 396.15 | 1400000 | 4248.5737 | 3652.0447 | 941.2651 | 0.00022628 | 123 | 13.8169 | 4.2486 | 3.652 | 0.94127 | 0.00022628
| 395.15 | 1400000 | 4246.7939 | 3656.8843 | 942.083 | 0.00022828 | 122 | 13.8169 | 4.2468 | 3.6569 | 0.94208 | 0.00022828
| 394.15 | 1400000 | 4245.0391 | 3661.7344 | 942.8965 | 0.0002303 | 121 | 13.8169 | 4.245 | 3.6617 | 0.9429 | 0.0002303
| 393.15 | 1400000 | 4243.3096 | 3666.5947 | 943.7056 | 0.00023237 | 120 | 13.8169 | 4.2433 | 3.6666 | 0.94371 | 0.00023237
| 392.15 | 1400000 | 4241.605 | 3671.4651 | 944.5104 | 0.00023446 | 119 | 13.8169 | 4.2416 | 3.6715 | 0.94451 | 0.00023446
| 391.15 | 1400000 | 4239.9248 | 3676.3457 | 945.3109 | 0.0002366 | 118 | 13.8169 | 4.2399 | 3.6763 | 0.94531 | 0.0002366
| 390.15 | 1400000 | 4238.2686 | 3681.2363 | 946.1069 | 0.00023876 | 117 | 13.8169 | 4.2383 | 3.6812 | 0.94611 | 0.00023876
| 389.15 | 1400000 | 4236.6372 | 3686.1367 | 946.8985 | 0.00024097 | 116 | 13.8169 | 4.2366 | 3.6861 | 0.9469 | 0.00024097
| 388.15 | 1400000 | 4235.0293 | 3691.0471 | 947.6857 | 0.00024321 | 115 | 13.8169 | 4.235 | 3.691 | 0.94769 | 0.00024321
| 387.15 | 1400000 | 4233.4448 | 3695.967 | 948.4686 | 0.0002455 | 114 | 13.8169 | 4.2334 | 3.696 | 0.94847 | 0.0002455
| 386.15 | 1400000 | 4231.8843 | 3700.8967 | 949.2471 | 0.00024782 | 113 | 13.8169 | 4.2319 | 3.7009 | 0.94925 | 0.00024782
| 385.15 | 1400000 | 4230.3472 | 3705.8357 | 950.0211 | 0.00025018 | 112 | 13.8169 | 4.2303 | 3.7058 | 0.95002 | 0.00025018
| 384.15 | 1400000 | 4228.833 | 3710.7842 | 950.7907 | 0.00025259 | 111 | 13.8169 | 4.2288 | 3.7108 | 0.95079 | 0.00025259
| 383.15 | 1400000 | 4227.3418 | 3715.7419 | 951.5559 | 0.00025503 | 110 | 13.8169 | 4.2273 | 3.7157 | 0.95156 | 0.00025503
| 382.15 | 1400000 | 4225.8735 | 3720.7087 | 952.3167 | 0.00025752 | 109 | 13.8169 | 4.2259 | 3.7207 | 0.95232 | 0.00025752
| 381.15 | 1400000 | 4224.4277 | 3725.6846 | 953.073 | 0.00026006 | 108 | 13.8169 | 4.2244 | 3.7257 | 0.95307 | 0.00026006
| 380.15 | 1400000 | 4223.0049 | 3730.6692 | 953.8248 | 0.00026264 | 107 | 13.8169 | 4.223 | 3.7307 | 0.95382 | 0.00026264
| 379.15 | 1400000 | 4221.604 | 3735.6628 | 954.5722 | 0.00026527 | 106 | 13.8169 | 4.2216 | 3.7357 | 0.95457 | 0.00026527
| 378.15 | 1400000 | 4220.2251 | 3740.6648 | 955.3151 | 0.00026795 | 105 | 13.8169 | 4.2202 | 3.7407 | 0.95532 | 0.00026795
| 377.15 | 1400000 | 4218.8687 | 3745.6753 | 956.0535 | 0.00027067 | 104 | 13.8169 | 4.2189 | 3.7457 | 0.95605 | 0.00027067
| 376.15 | 1400000 | 4217.5342 | 3750.6941 | 956.7874 | 0.00027345 | 103 | 13.8169 | 4.2175 | 3.7507 | 0.95679 | 0.00027345
| 375.15 | 1400000 | 4216.2212 | 3755.7212 | 957.5168 | 0.00027628 | 102 | 13.8169 | 4.2162 | 3.7557 | 0.95752 | 0.00027628
| 374.15 | 1400000 | 4214.9302 | 3760.7561 | 958.2416 | 0.00027916 | 101 | 13.8169 | 4.2149 | 3.7608 | 0.95824 | 0.00027916
| 373.15 | 1400000 | 4213.6606 | 3765.7988 | 958.9619 | 0.00028209 | 100 | 13.8169 | 4.2137 | 3.7658 | 0.95896 | 0.00028209
| 372.15 | 1400000 | 4212.4126 | 3770.8494 | 959.6777 | 0.00028508 | 99 | 13.8169 | 4.2124 | 3.7708 | 0.95968 | 0.00028508
| 371.15 | 1400000 | 4211.1855 | 3775.9072 | 960.3888 | 0.00028813 | 98 | 13.8169 | 4.2112 | 3.7759 | 0.96039 | 0.00028813
| 370.15 | 1400000 | 4209.9805 | 3780.9722 | 961.0953 | 0.00029124 | 97 | 13.8169 | 4.21 | 3.781 | 0.9611 | 0.00029124
| 369.15 | 1400000 | 4208.7959 | 3786.0444 | 961.7973 | 0.00029441 | 96 | 13.8169 | 4.2088 | 3.786 | 0.9618 | 0.00029441
| 368.15 | 1400000 | 4207.6328 | 3791.1233 | 962.4946 | 0.00029763 | 95 | 13.8169 | 4.2076 | 3.7911 | 0.96249 | 0.00029763
| 367.15 | 1400000 | 4206.4907 | 3796.209 | 963.1872 | 0.00030093 | 94 | 13.8169 | 4.2065 | 3.7962 | 0.96319 | 0.00030093
| 366.15 | 1400000 | 4205.3696 | 3801.301 | 963.8752 | 0.00030428 | 93 | 13.8169 | 4.2054 | 3.8013 | 0.96388 | 0.00030428
| 365.15 | 1400000 | 4204.2695 | 3806.3992 | 964.5584 | 0.00030771 | 92 | 13.8169 | 4.2043 | 3.8064 | 0.96456 | 0.00030771
| 364.15 | 1400000 | 4203.1899 | 3811.5032 | 965.2369 | 0.0003112 | 91 | 13.8169 | 4.2032 | 3.8115 | 0.96524 | 0.0003112
| 363.15 | 1400000 | 4202.1309 | 3816.613 | 965.9108 | 0.00031476 | 90 | 13.8169 | 4.2021 | 3.8166 | 0.96591 | 0.00031476
| 362.15 | 1400000 | 4201.0933 | 3821.7283 | 966.5798 | 0.00031839 | 89 | 13.8169 | 4.2011 | 3.8217 | 0.96658 | 0.00031839
| 361.15 | 1400000 | 4200.0757 | 3826.8484 | 967.2441 | 0.0003221 | 88 | 13.8169 | 4.2001 | 3.8268 | 0.96724 | 0.0003221
| 360.15 | 1400000 | 4199.0791 | 3831.9734 | 967.9035 | 0.00032589 | 87 | 13.8169 | 4.1991 | 3.832 | 0.9679 | 0.00032589
| 359.15 | 1400000 | 4198.1025 | 3837.103 | 968.5581 | 0.00032975 | 86 | 13.8169 | 4.1981 | 3.8371 | 0.96856 | 0.00032975
| 358.15 | 1400000 | 4197.147 | 3842.2368 | 969.2078 | 0.00033369 | 85 | 13.8169 | 4.1971 | 3.8422 | 0.96921 | 0.00033369
| 357.15 | 1400000 | 4196.2119 | 3847.3745 | 969.8527 | 0.00033772 | 84 | 13.8169 | 4.1962 | 3.8474 | 0.96985 | 0.00033772
| 356.15 | 1400000 | 4195.2969 | 3852.5156 | 970.4926 | 0.00034183 | 83 | 13.8169 | 4.1953 | 3.8525 | 0.97049 | 0.00034183
| 355.15 | 1400000 | 4194.4028 | 3857.6599 | 971.1276 | 0.00034603 | 82 | 13.8169 | 4.1944 | 3.8577 | 0.97113 | 0.00034603
| 354.15 | 1400000 | 4193.5288 | 3862.8069 | 971.7576 | 0.00035031 | 81 | 13.8169 | 4.1935 | 3.8628 | 0.97176 | 0.00035031
| 353.15 | 1400000 | 4192.6753 | 3867.9563 | 972.3826 | 0.00035469 | 80 | 13.8169 | 4.1927 | 3.868 | 0.97238 | 0.00035469
| 352.15 | 1400000 | 4191.8418 | 3873.1077 | 973.0026 | 0.00035917 | 79 | 13.8169 | 4.1918 | 3.8731 | 0.973 | 0.00035917
| 351.15 | 1400000 | 4191.0293 | 3878.2607 | 973.6175 | 0.00036374 | 78 | 13.8169 | 4.191 | 3.8783 | 0.97362 | 0.00036374
| 350.15 | 1400000 | 4190.2368 | 3883.4148 | 974.2273 | 0.00036842 | 77 | 13.8169 | 4.1902 | 3.8834 | 0.97423 | 0.00036842
| 349.15 | 1400000 | 4189.4644 | 3888.5696 | 974.832 | 0.0003732 | 76 | 13.8169 | 4.1895 | 3.8886 | 0.97483 | 0.0003732
| 348.15 | 1400000 | 4188.7129 | 3893.7246 | 975.4315 | 0.00037808 | 75 | 13.8169 | 4.1887 | 3.8937 | 0.97543 | 0.00037808
| 347.15 | 1400000 | 4187.981 | 3898.8792 | 976.0258 | 0.00038308 | 74 | 13.8169 | 4.188 | 3.8989 | 0.97603 | 0.00038308
| 346.15 | 1400000 | 4187.27 | 3904.033 | 976.6148 | 0.00038818 | 73 | 13.8169 | 4.1873 | 3.904 | 0.97661 | 0.00038818
| 345.15 | 1400000 | 4186.5791 | 3909.1853 | 977.1985 | 0.00039341 | 72 | 13.8169 | 4.1866 | 3.9092 | 0.9772 | 0.00039341
| 344.15 | 1400000 | 4185.9087 | 3914.3359 | 977.777 | 0.00039875 | 71 | 13.8169 | 4.1859 | 3.9143 | 0.97778 | 0.00039875
| 343.15 | 1400000 | 4185.2588 | 3919.4839 | 978.35 | 0.00040422 | 70 | 13.8169 | 4.1853 | 3.9195 | 0.97835 | 0.00040422
| 342.15 | 1400000 | 4184.6289 | 3924.6289 | 978.9177 | 0.00040982 | 69 | 13.8169 | 4.1846 | 3.9246 | 0.97892 | 0.00040982
| 341.15 | 1400000 | 4184.0195 | 3929.77 | 979.4799 | 0.00041555 | 68 | 13.8169 | 4.184 | 3.9298 | 0.97948 | 0.00041555
| 340.15 | 1400000 | 4183.4302 | 3934.9067 | 980.0366 | 0.00042142 | 67 | 13.8169 | 4.1834 | 3.9349 | 0.98004 | 0.00042142
| 339.15 | 1400000 | 4182.8618 | 3940.0386 | 980.5878 | 0.00042743 | 66 | 13.8169 | 4.1829 | 3.94 | 0.98059 | 0.00042743
| 338.15 | 1400000 | 4182.3135 | 3945.1646 | 981.1334 | 0.00043358 | 65 | 13.8169 | 4.1823 | 3.9452 | 0.98113 | 0.00043358
| 337.15 | 1400000 | 4181.7856 | 3950.2839 | 981.6734 | 0.00043988 | 64 | 13.8169 | 4.1818 | 3.9503 | 0.98167 | 0.00043988
| 336.15 | 1400000 | 4181.2783 | 3955.3962 | 982.2077 | 0.00044634 | 63 | 13.8169 | 4.1813 | 3.9554 | 0.98221 | 0.00044634
| 335.15 | 1400000 | 4180.7915 | 3960.5005 | 982.7363 | 0.00045296 | 62 | 13.8169 | 4.1808 | 3.9605 | 0.98274 | 0.00045296
| 334.15 | 1400000 | 4180.3247 | 3965.5959 | 983.259 | 0.00045974 | 61 | 13.8169 | 4.1803 | 3.9656 | 0.98326 | 0.00045974
| 333.15 | 1400000 | 4179.8789 | 3970.6816 | 983.776 | 0.00046669 | 60 | 13.8169 | 4.1799 | 3.9707 | 0.98378 | 0.00046669
| 332.15 | 1400000 | 4179.4536 | 3975.7571 | 984.287 | 0.00047382 | 59 | 13.8169 | 4.1795 | 3.9758 | 0.98429 | 0.00047382
| 331.15 | 1400000 | 4179.0493 | 3980.821 | 984.7922 | 0.00048114 | 58 | 13.8169 | 4.179 | 3.9808 | 0.98479 | 0.00048114
| 330.15 | 1400000 | 4178.665 | 3985.8726 | 985.2913 | 0.00048864 | 57 | 13.8169 | 4.1787 | 3.9859 | 0.98529 | 0.00048864
| 329.15 | 1400000 | 4178.3018 | 3990.9109 | 985.7843 | 0.00049634 | 56 | 13.8169 | 4.1783 | 3.9909 | 0.98578 | 0.00049634
| 328.15 | 1400000 | 4177.959 | 3995.9351 | 986.2712 | 0.00050425 | 55 | 13.8169 | 4.178 | 3.9959 | 0.98627 | 0.00050425
| 327.15 | 1400000 | 4177.6372 | 4000.9438 | 986.7519 | 0.00051236 | 54 | 13.8169 | 4.1776 | 4.0009 | 0.98675 | 0.00051236
| 326.15 | 1400000 | 4177.3359 | 4005.9363 | 987.2264 | 0.00052069 | 53 | 13.8169 | 4.1773 | 4.0059 | 0.98723 | 0.00052069
| 325.15 | 1400000 | 4177.0562 | 4010.9114 | 987.6945 | 0.00052925 | 52 | 13.8169 | 4.1771 | 4.0109 | 0.98769 | 0.00052925
| 324.15 | 1400000 | 4176.7969 | 4015.8679 | 988.1562 | 0.00053804 | 51 | 13.8169 | 4.1768 | 4.0159 | 0.98816 | 0.00053804
| 323.15 | 1400000 | 4176.5586 | 4020.8049 | 988.6116 | 0.00054708 | 50 | 13.8169 | 4.1766 | 4.0208 | 0.98861 | 0.00054708
| 322.15 | 1400000 | 4176.3418 | 4025.7209 | 989.0603 | 0.00055637 | 49 | 13.8169 | 4.1763 | 4.0257 | 0.98906 | 0.00055637
| 321.15 | 1400000 | 4176.146 | 4030.615 | 989.5024 | 0.00056592 | 48 | 13.8169 | 4.1761 | 4.0306 | 0.9895 | 0.00056592
| 320.15 | 1400000 | 4175.9717 | 4035.4858 | 989.9379 | 0.00057574 | 47 | 13.8169 | 4.176 | 4.0355 | 0.98994 | 0.00057574
| 319.15 | 1400000 | 4175.8188 | 4040.3318 | 990.3666 | 0.00058584 | 46 | 13.8169 | 4.1758 | 4.0403 | 0.99037 | 0.00058584
| 318.15 | 1400000 | 4175.6875 | 4045.1521 | 990.7885 | 0.00059624 | 45 | 13.8169 | 4.1757 | 4.0452 | 0.99079 | 0.00059624
| 317.15 | 1400000 | 4175.5781 | 4049.9453 | 991.2033 | 0.00060695 | 44 | 13.8169 | 4.1756 | 4.0499 | 0.9912 | 0.00060695
| 316.15 | 1400000 | 4175.4907 | 4054.7097 | 991.6112 | 0.00061797 | 43 | 13.8169 | 4.1755 | 4.0547 | 0.99161 | 0.00061797
| 315.15 | 1400000 | 4175.4253 | 4059.4441 | 992.012 | 0.00062933 | 42 | 13.8169 | 4.1754 | 4.0594 | 0.99201 | 0.00062933
| 314.15 | 1400000 | 4175.3823 | 4064.147 | 992.4055 | 0.00064102 | 41 | 13.8169 | 4.1754 | 4.0641 | 0.99241 | 0.00064102
| 313.15 | 1400000 | 4175.3628 | 4068.8169 | 992.7917 | 0.00065308 | 40 | 13.8169 | 4.1754 | 4.0688 | 0.99279 | 0.00065308
| 312.15 | 1400000 | 4175.3657 | 4073.4524 | 993.1706 | 0.00066552 | 39 | 13.8169 | 4.1754 | 4.0735 | 0.99317 | 0.00066552
| 311.15 | 1400000 | 4175.3921 | 4078.052 | 993.5419 | 0.00067834 | 38 | 13.8169 | 4.1754 | 4.0781 | 0.99354 | 0.00067834
| 310.15 | 1400000 | 4175.4429 | 4082.614 | 993.9057 | 0.00069157 | 37 | 13.8169 | 4.1754 | 4.0826 | 0.99391 | 0.00069157
| 309.15 | 1400000 | 4175.5176 | 4087.1367 | 994.2617 | 0.00070522 | 36 | 13.8169 | 4.1755 | 4.0871 | 0.99426 | 0.00070522
| 308.15 | 1400000 | 4175.6172 | 4091.6187 | 994.6099 | 0.00071932 | 35 | 13.8169 | 4.1756 | 4.0916 | 0.99461 | 0.00071932
| 307.15 | 1400000 | 4175.7422 | 4096.0586 | 994.9501 | 0.00073389 | 34 | 13.8169 | 4.1757 | 4.0961 | 0.99495 | 0.00073389
| 306.15 | 1400000 | 4175.8936 | 4100.4541 | 995.2822 | 0.00074894 | 33 | 13.8169 | 4.1759 | 4.1005 | 0.99528 | 0.00074894
| 305.15 | 1400000 | 4176.0718 | 4104.8037 | 995.6061 | 0.00076449 | 32 | 13.8169 | 4.1761 | 4.1048 | 0.99561 | 0.00076449
| 304.15 | 1400000 | 4176.2778 | 4109.106 | 995.9217 | 0.00078058 | 31 | 13.8169 | 4.1763 | 4.1091 | 0.99592 | 0.00078058
| 303.15 | 1400000 | 4176.5127 | 4113.3594 | 996.2288 | 0.00079722 | 30 | 13.8169 | 4.1765 | 4.1134 | 0.99623 | 0.00079722
| 302.15 | 1400000 | 4176.7773 | 4117.562 | 996.5273 | 0.00081445 | 29 | 13.8169 | 4.1768 | 4.1176 | 0.99653 | 0.00081445
| 301.15 | 1400000 | 4177.0732 | 4121.7119 | 996.817 | 0.00083229 | 28 | 13.8169 | 4.1771 | 4.1217 | 0.99682 | 0.00083229
| 300.15 | 1400000 | 4177.4019 | 4125.8071 | 997.0978 | 0.00085077 | 27 | 13.8169 | 4.1774 | 4.1258 | 0.9971 | 0.00085077
| 299.15 | 1400000 | 4177.7642 | 4129.8467 | 997.3695 | 0.00086992 | 26 | 13.8169 | 4.1778 | 4.1298 | 0.99737 | 0.00086992
| 298.15 | 1400000 | 4178.1626 | 4133.8286 | 997.632 | 0.00088978 | 25 | 13.8169 | 4.1782 | 4.1338 | 0.99763 | 0.00088978
| 297.15 | 1400000 | 4178.5986 | 4137.751 | 997.8851 | 0.00091038 | 24 | 13.8169 | 4.1786 | 4.1378 | 0.99789 | 0.00091038
| 296.15 | 1400000 | 4179.0747 | 4141.6128 | 998.1285 | 0.00093177 | 23 | 13.8169 | 4.1791 | 4.1416 | 0.99813 | 0.00093177
| 295.15 | 1400000 | 4179.5938 | 4145.4116 | 998.3622 | 0.00095398 | 22 | 13.8169 | 4.1796 | 4.1454 | 0.99836 | 0.00095398
| 294.15 | 1400000 | 4180.1577 | 4149.146 | 998.5859 | 0.00097706 | 21 | 13.8169 | 4.1802 | 4.1491 | 0.99859 | 0.00097706
| 293.15 | 1400000 | 4180.77 | 4152.8149 | 998.7994 | 0.0010011 | 20 | 13.8169 | 4.1808 | 4.1528 | 0.9988 | 0.0010011
| 292.15 | 1400000 | 4181.4346 | 4156.4165 | 999.0024 | 0.001026 | 19 | 13.8169 | 4.1814 | 4.1564 | 0.999 | 0.001026
| 291.15 | 1400000 | 4182.1543 | 4159.9492 | 999.1949 | 0.001052 | 18 | 13.8169 | 4.1822 | 4.1599 | 0.99919 | 0.001052
| 290.15 | 1400000 | 4182.9346 | 4163.4116 | 999.3765 | 0.001079 | 17 | 13.8169 | 4.1829 | 4.1634 | 0.99938 | 0.001079
| 289.15 | 1400000 | 4183.7793 | 4166.8032 | 999.547 | 0.0011072 | 16 | 13.8169 | 4.1838 | 4.1668 | 0.99955 | 0.0011072
| 288.15 | 1400000 | 4184.6938 | 4170.1221 | 999.7061 | 0.0011366 | 15 | 13.8169 | 4.1847 | 4.1701 | 0.99971 | 0.0011366
| 287.15 | 1400000 | 4185.6846 | 4173.3672 | 999.8536 | 0.0011673 | 14 | 13.8169 | 4.1857 | 4.1734 | 0.99985 | 0.0011673
| 286.15 | 1400000 | 4186.7583 | 4176.5381 | 999.9891 | 0.0011994 | 13 | 13.8169 | 4.1868 | 4.1765 | 0.99999 | 0.0011994
| 285.15 | 1400000 | 4187.9219 | 4179.6338 | 1000.1125 | 0.0012328 | 12 | 13.8169 | 4.1879 | 4.1796 | 1.0001 | 0.0012328
| 284.15 | 1400000 | 4189.1831 | 4182.6533 | 1000.2233 | 0.0012678 | 11 | 13.8169 | 4.1892 | 4.1827 | 1.0002 | 0.0012678
| 283.15 | 1400000 | 4190.5522 | 4185.5962 | 1000.3212 | 0.0013045 | 10 | 13.8169 | 4.1906 | 4.1856 | 1.0003 | 0.0013045
| 282.15 | 1400000 | 4192.0381 | 4188.4629 | 1000.4058 | 0.0013428 | 9 | 13.8169 | 4.192 | 4.1885 | 1.0004 | 0.0013428
| 281.15 | 1400000 | 4193.6519 | 4191.2524 | 1000.4769 | 0.001383 | 8 | 13.8169 | 4.1937 | 4.1913 | 1.0005 | 0.001383
| 280.15 | 1400000 | 4195.4067 | 4193.9648 | 1000.534 | 0.0014252 | 7 | 13.8169 | 4.1954 | 4.194 | 1.0005 | 0.0014252
| 279.15 | 1400000 | 4197.3159 | 4196.6011 | 1000.5767 | 0.0014695 | 6 | 13.8169 | 4.1973 | 4.1966 | 1.0006 | 0.0014695
| 278.15 | 1400000 | 4199.3945 | 4199.1616 | 1000.6045 | 0.001516 | 5 | 13.8169 | 4.1994 | 4.1992 | 1.0006 | 0.001516
| 277.15 | 1400000 | 4201.6597 | 4201.647 | 1000.6171 | 0.0015649 | 4 | 13.8169 | 4.2017 | 4.2016 | 1.0006 | 0.0015649
| 276.15 | 1400000 | 4204.1294 | 4204.0586 | 1000.6138 | 0.0016164 | 3 | 13.8169 | 4.2041 | 4.2041 | 1.0006 | 0.0016164
| 275.15 | 1400000 | 4206.8247 | 4206.397 | 1000.5942 | 0.0016706 | 2 | 13.8169 | 4.2068 | 4.2064 | 1.0006 | 0.0016706
| 274.15 | 1400000 | 4209.7681 | 4208.665 | 1000.5579 | 0.0017279 | 0.99999 | 13.8169 | 4.2098 | 4.2087 | 1.0006 | 0.0017279
| 273.15 | 1400000 | 4212.9849 | 4210.8638 | 1000.504 | 0.0017883 | -6.1035e-06 | 13.8169 | 4.213 | 4.2109 | 1.0005 | 0.0017883
| 473.15 | 1300000 | 2673.3928 | 1887.4995 | 6.4445 | 1.5798e-05 | 200 | 12.83 | 2.6734 | 1.8875 | 0.0064445 | 1.5798e-05
| 472.15 | 1300000 | 2690.8784 | 1898.0713 | 6.464 | 1.5753e-05 | 199 | 12.83 | 2.6909 | 1.8981 | 0.006464 | 1.5753e-05
| 471.15 | 1300000 | 2709.5681 | 1909.4528 | 6.4837 | 1.5709e-05 | 198 | 12.83 | 2.7096 | 1.9095 | 0.0064837 | 1.5709e-05
| 470.15 | 1300000 | 2729.6025 | 1921.7407 | 6.5036 | 1.5665e-05 | 197 | 12.83 | 2.7296 | 1.9217 | 0.0065036 | 1.5665e-05
| 469.15 | 1300000 | 2751.1414 | 1935.0444 | 6.5237 | 1.562e-05 | 196 | 12.83 | 2.7511 | 1.935 | 0.0065237 | 1.562e-05
| 468.15 | 1300000 | 2774.3665 | 1949.4879 | 6.544 | 1.5576e-05 | 195 | 12.83 | 2.7744 | 1.9495 | 0.006544 | 1.5576e-05
| 467.15 | 1300000 | 2799.4836 | 1965.2112 | 6.5646 | 1.5532e-05 | 194 | 12.83 | 2.7995 | 1.9652 | 0.0065646 | 1.5532e-05
| 466.15 | 1300000 | 2826.7275 | 1982.3732 | 6.5855 | 1.5487e-05 | 193 | 12.83 | 2.8267 | 1.9824 | 0.0065855 | 1.5487e-05
| 465.15 | 1300000 | 2856.3647 | 2001.1533 | 6.6066 | 1.5443e-05 | 192 | 12.83 | 2.8564 | 2.0012 | 0.0066066 | 1.5443e-05
| 464.15 | 1300000 | 4451.1284 | 3351.8525 | 874.9775 | 0.00014101 | 191 | 12.83 | 4.4511 | 3.3519 | 0.87498 | 0.00014101
| 463.15 | 1300000 | 4446.5498 | 3355.7883 | 876.1162 | 0.0001418 | 190 | 12.83 | 4.4465 | 3.3558 | 0.87612 | 0.0001418
| 462.15 | 1300000 | 4442.0371 | 3359.7405 | 877.2493 | 0.0001426 | 189 | 12.83 | 4.442 | 3.3597 | 0.87725 | 0.0001426
| 461.15 | 1300000 | 4437.5889 | 3363.7092 | 878.377 | 0.0001434 | 188 | 12.83 | 4.4376 | 3.3637 | 0.87838 | 0.0001434
| 460.15 | 1300000 | 4433.2046 | 3367.6946 | 879.4991 | 0.00014422 | 187 | 12.83 | 4.4332 | 3.3677 | 0.8795 | 0.00014422
| 459.15 | 1300000 | 4428.8833 | 3371.696 | 880.6158 | 0.00014505 | 186 | 12.83 | 4.4289 | 3.3717 | 0.88062 | 0.00014505
| 458.15 | 1300000 | 4424.6235 | 3375.7136 | 881.7272 | 0.00014588 | 185 | 12.83 | 4.4246 | 3.3757 | 0.88173 | 0.00014588
| 457.15 | 1300000 | 4420.4238 | 3379.7473 | 882.8331 | 0.00014673 | 184 | 12.83 | 4.4204 | 3.3797 | 0.88283 | 0.00014673
| 456.15 | 1300000 | 4416.2842 | 3383.7969 | 883.9338 | 0.00014759 | 183 | 12.83 | 4.4163 | 3.3838 | 0.88393 | 0.00014759
| 455.15 | 1300000 | 4412.2031 | 3387.8625 | 885.0292 | 0.00014845 | 182 | 12.83 | 4.4122 | 3.3879 | 0.88503 | 0.00014845
| 454.15 | 1300000 | 4408.1797 | 3391.9436 | 886.1194 | 0.00014933 | 181 | 12.83 | 4.4082 | 3.3919 | 0.88612 | 0.00014933
| 453.15 | 1300000 | 4404.2129 | 3396.0405 | 887.2044 | 0.00015021 | 180 | 12.83 | 4.4042 | 3.396 | 0.8872 | 0.00015021
| 452.15 | 1300000 | 4400.3022 | 3400.1528 | 888.2842 | 0.00015111 | 179 | 12.83 | 4.4003 | 3.4002 | 0.88828 | 0.00015111
| 451.15 | 1300000 | 4396.4458 | 3404.2805 | 889.3589 | 0.00015202 | 178 | 12.83 | 4.3964 | 3.4043 | 0.88936 | 0.00015202
| 450.15 | 1300000 | 4392.6436 | 3408.4233 | 890.4285 | 0.00015293 | 177 | 12.83 | 4.3926 | 3.4084 | 0.89043 | 0.00015293
| 449.15 | 1300000 | 4388.8945 | 3412.5815 | 891.493 | 0.00015386 | 176 | 12.83 | 4.3889 | 3.4126 | 0.89149 | 0.00015386
| 448.15 | 1300000 | 4385.1978 | 3416.7546 | 892.5525 | 0.0001548 | 175 | 12.83 | 4.3852 | 3.4168 | 0.89255 | 0.0001548
| 447.15 | 1300000 | 4381.5522 | 3420.9429 | 893.6069 | 0.00015575 | 174 | 12.83 | 4.3816 | 3.4209 | 0.89361 | 0.00015575
| 446.15 | 1300000 | 4377.9575 | 3425.1458 | 894.6564 | 0.00015672 | 173 | 12.83 | 4.378 | 3.4251 | 0.89466 | 0.00015672
| 445.15 | 1300000 | 4374.4121 | 3429.3635 | 895.7009 | 0.00015769 | 172 | 12.83 | 4.3744 | 3.4294 | 0.8957 | 0.00015769
| 444.15 | 1300000 | 4370.9165 | 3433.5959 | 896.7405 | 0.00015868 | 171 | 12.83 | 4.3709 | 3.4336 | 0.89674 | 0.00015868
| 443.15 | 1300000 | 4367.4688 | 3437.8428 | 897.7751 | 0.00015968 | 170 | 12.83 | 4.3675 | 3.4378 | 0.89778 | 0.00015968
| 442.15 | 1300000 | 4364.0684 | 3442.104 | 898.805 | 0.00016069 | 169 | 12.83 | 4.3641 | 3.4421 | 0.8988 | 0.00016069
| 441.15 | 1300000 | 4360.7148 | 3446.3796 | 899.83 | 0.00016172 | 168 | 12.83 | 4.3607 | 3.4464 | 0.89983 | 0.00016172
| 440.15 | 1300000 | 4357.4072 | 3450.6697 | 900.85 | 0.00016276 | 167 | 12.83 | 4.3574 | 3.4507 | 0.90085 | 0.00016276
| 439.15 | 1300000 | 4354.1455 | 3454.9736 | 901.8654 | 0.00016381 | 166 | 12.83 | 4.3541 | 3.455 | 0.90187 | 0.00016381
| 438.15 | 1300000 | 4350.9282 | 3459.2917 | 902.876 | 0.00016487 | 165 | 12.83 | 4.3509 | 3.4593 | 0.90288 | 0.00016487
| 437.15 | 1300000 | 4347.7549 | 3463.6238 | 903.8817 | 0.00016595 | 164 | 12.83 | 4.3478 | 3.4636 | 0.90388 | 0.00016595
| 436.15 | 1300000 | 4344.6245 | 3467.9695 | 904.8828 | 0.00016704 | 163 | 12.83 | 4.3446 | 3.468 | 0.90488 | 0.00016704
| 435.15 | 1300000 | 4341.5371 | 3472.3291 | 905.8792 | 0.00016815 | 162 | 12.83 | 4.3415 | 3.4723 | 0.90588 | 0.00016815
| 434.15 | 1300000 | 4338.4922 | 3476.7024 | 906.8708 | 0.00016927 | 161 | 12.83 | 4.3385 | 3.4767 | 0.90687 | 0.00016927
| 433.15 | 1300000 | 4335.4883 | 3481.0891 | 907.8578 | 0.00017041 | 160 | 12.83 | 4.3355 | 3.4811 | 0.90786 | 0.00017041
| 432.15 | 1300000 | 4332.5254 | 3485.4895 | 908.8401 | 0.00017156 | 159 | 12.83 | 4.3325 | 3.4855 | 0.90884 | 0.00017156
| 431.15 | 1300000 | 4329.6025 | 3489.9031 | 909.8178 | 0.00017273 | 158 | 12.83 | 4.3296 | 3.4899 | 0.90982 | 0.00017273
| 430.15 | 1300000 | 4326.7192 | 3494.3298 | 910.7908 | 0.00017391 | 157 | 12.83 | 4.3267 | 3.4943 | 0.91079 | 0.00017391
| 429.15 | 1300000 | 4323.8755 | 3498.77 | 911.7593 | 0.00017511 | 156 | 12.83 | 4.3239 | 3.4988 | 0.91176 | 0.00017511
| 428.15 | 1300000 | 4321.0698 | 3503.2231 | 912.7232 | 0.00017633 | 155 | 12.83 | 4.3211 | 3.5032 | 0.91272 | 0.00017633
| 427.15 | 1300000 | 4318.3022 | 3507.6895 | 913.6825 | 0.00017756 | 154 | 12.83 | 4.3183 | 3.5077 | 0.91368 | 0.00017756
| 426.15 | 1300000 | 4315.5723 | 3512.1687 | 914.6373 | 0.00017881 | 153 | 12.83 | 4.3156 | 3.5122 | 0.91464 | 0.00017881
| 425.15 | 1300000 | 4312.8789 | 3516.6606 | 915.5875 | 0.00018008 | 152 | 12.83 | 4.3129 | 3.5167 | 0.91559 | 0.00018008
| 424.15 | 1300000 | 4310.2222 | 3521.1655 | 916.5332 | 0.00018137 | 151 | 12.83 | 4.3102 | 3.5212 | 0.91653 | 0.00018137
| 423.15 | 1300000 | 4307.6016 | 3525.6829 | 917.4744 | 0.00018267 | 150 | 12.83 | 4.3076 | 3.5257 | 0.91747 | 0.00018267
| 422.15 | 1300000 | 4305.0156 | 3530.2131 | 918.411 | 0.00018399 | 149 | 12.83 | 4.305 | 3.5302 | 0.91841 | 0.00018399
| 421.15 | 1300000 | 4302.4653 | 3534.7556 | 919.3433 | 0.00018533 | 148 | 12.83 | 4.3025 | 3.5348 | 0.91934 | 0.00018533
| 420.15 | 1300000 | 4299.9492 | 3539.3105 | 920.2709 | 0.00018669 | 147 | 12.83 | 4.2999 | 3.5393 | 0.92027 | 0.00018669
| 419.15 | 1300000 | 4297.4668 | 3543.8779 | 921.1942 | 0.00018807 | 146 | 12.83 | 4.2975 | 3.5439 | 0.92119 | 0.00018807
| 418.15 | 1300000 | 4295.0186 | 3548.4578 | 922.113 | 0.00018947 | 145 | 12.83 | 4.295 | 3.5485 | 0.92211 | 0.00018947
| 417.15 | 1300000 | 4292.603 | 3553.0496 | 923.0274 | 0.00019089 | 144 | 12.83 | 4.2926 | 3.553 | 0.92303 | 0.00019089
| 416.15 | 1300000 | 4290.2202 | 3557.6536 | 923.9373 | 0.00019233 | 143 | 12.83 | 4.2902 | 3.5577 | 0.92394 | 0.00019233
| 415.15 | 1300000 | 4287.8696 | 3562.2695 | 924.8428 | 0.00019379 | 142 | 12.83 | 4.2879 | 3.5623 | 0.92484 | 0.00019379
| 414.15 | 1300000 | 4285.5508 | 3566.8975 | 925.7439 | 0.00019528 | 141 | 12.83 | 4.2856 | 3.5669 | 0.92574 | 0.00019528
| 413.15 | 1300000 | 4283.2632 | 3571.5374 | 926.6406 | 0.00019678 | 140 | 12.83 | 4.2833 | 3.5715 | 0.92664 | 0.00019678
| 412.15 | 1300000 | 4281.0068 | 3576.1892 | 927.5329 | 0.00019831 | 139 | 12.83 | 4.281 | 3.5762 | 0.92753 | 0.00019831
| 411.15 | 1300000 | 4278.7812 | 3580.8525 | 928.4208 | 0.00019986 | 138 | 12.83 | 4.2788 | 3.5809 | 0.92842 | 0.00019986
| 410.15 | 1300000 | 4276.5854 | 3585.5276 | 929.3043 | 0.00020144 | 137 | 12.83 | 4.2766 | 3.5855 | 0.9293 | 0.00020144
| 409.15 | 1300000 | 4274.4199 | 3590.2144 | 930.1834 | 0.00020303 | 136 | 12.83 | 4.2744 | 3.5902 | 0.93018 | 0.00020303
| 408.15 | 1300000 | 4272.2837 | 3594.9126 | 931.0582 | 0.00020466 | 135 | 12.83 | 4.2723 | 3.5949 | 0.93106 | 0.00020466
| 407.15 | 1300000 | 4270.1768 | 3599.6221 | 931.9285 | 0.00020631 | 134 | 12.83 | 4.2702 | 3.5996 | 0.93193 | 0.00020631
| 406.15 | 1300000 | 4268.0986 | 3604.3433 | 932.7945 | 0.00020798 | 133 | 12.83 | 4.2681 | 3.6043 | 0.93279 | 0.00020798
| 405.15 | 1300000 | 4266.0488 | 3609.0754 | 933.6561 | 0.00020968 | 132 | 12.83 | 4.266 | 3.6091 | 0.93366 | 0.00020968
| 404.15 | 1300000 | 4264.0273 | 3613.8188 | 934.5134 | 0.00021141 | 131 | 12.83 | 4.264 | 3.6138 | 0.93451 | 0.00021141
| 403.15 | 1300000 | 4262.0337 | 3618.5735 | 935.3663 | 0.00021316 | 130 | 12.83 | 4.262 | 3.6186 | 0.93537 | 0.00021316
| 402.15 | 1300000 | 4260.0679 | 3623.3391 | 936.2149 | 0.00021494 | 129 | 12.83 | 4.2601 | 3.6233 | 0.93621 | 0.00021494
| 401.15 | 1300000 | 4258.1289 | 3628.1157 | 937.0591 | 0.00021675 | 128 | 12.83 | 4.2581 | 3.6281 | 0.93706 | 0.00021675
| 400.15 | 1300000 | 4256.2168 | 3632.9033 | 937.8989 | 0.00021859 | 127 | 12.83 | 4.2562 | 3.6329 | 0.9379 | 0.00021859
| 399.15 | 1300000 | 4254.3315 | 3637.7014 | 938.7344 | 0.00022046 | 126 | 12.83 | 4.2543 | 3.6377 | 0.93873 | 0.00022046
| 398.15 | 1300000 | 4252.4727 | 3642.5105 | 939.5656 | 0.00022236 | 125 | 12.83 | 4.2525 | 3.6425 | 0.93957 | 0.00022236
| 397.15 | 1300000 | 4250.6396 | 3647.3303 | 940.3923 | 0.00022429 | 124 | 12.83 | 4.2506 | 3.6473 | 0.94039 | 0.00022429
| 396.15 | 1300000 | 4248.8325 | 3652.1604 | 941.2147 | 0.00022626 | 123 | 12.83 | 4.2488 | 3.6522 | 0.94121 | 0.00022626
| 395.15 | 1300000 | 4247.0508 | 3657.0012 | 942.0328 | 0.00022825 | 122 | 12.83 | 4.2471 | 3.657 | 0.94203 | 0.00022825
| 394.15 | 1300000 | 4245.2944 | 3661.8523 | 942.8465 | 0.00023028 | 121 | 12.83 | 4.2453 | 3.6619 | 0.94285 | 0.00023028
| 393.15 | 1300000 | 4243.5635 | 3666.7139 | 943.6558 | 0.00023234 | 120 | 12.83 | 4.2436 | 3.6667 | 0.94366 | 0.00023234
| 392.15 | 1300000 | 4241.8569 | 3671.5854 | 944.4608 | 0.00023444 | 119 | 12.83 | 4.2419 | 3.6716 | 0.94446 | 0.00023444
| 391.15 | 1300000 | 4240.1753 | 3676.4673 | 945.2614 | 0.00023657 | 118 | 12.83 | 4.2402 | 3.6765 | 0.94526 | 0.00023657
| 390.15 | 1300000 | 4238.5181 | 3681.3589 | 946.0576 | 0.00023874 | 117 | 12.83 | 4.2385 | 3.6814 | 0.94606 | 0.00023874
| 389.15 | 1300000 | 4236.8848 | 3686.2607 | 946.8494 | 0.00024094 | 116 | 12.83 | 4.2369 | 3.6863 | 0.94685 | 0.00024094
| 388.15 | 1300000 | 4235.2754 | 3691.1721 | 947.6368 | 0.00024319 | 115 | 12.83 | 4.2353 | 3.6912 | 0.94764 | 0.00024319
| 387.15 | 1300000 | 4233.6899 | 3696.0935 | 948.4198 | 0.00024547 | 114 | 12.83 | 4.2337 | 3.6961 | 0.94842 | 0.00024547
| 386.15 | 1300000 | 4232.1279 | 3701.0244 | 949.1984 | 0.00024779 | 113 | 12.83 | 4.2321 | 3.701 | 0.9492 | 0.00024779
| 385.15 | 1300000 | 4230.5894 | 3705.9648 | 949.9726 | 0.00025015 | 112 | 12.83 | 4.2306 | 3.706 | 0.94997 | 0.00025015
| 384.15 | 1300000 | 4229.0737 | 3710.9146 | 950.7424 | 0.00025256 | 111 | 12.83 | 4.2291 | 3.7109 | 0.95074 | 0.00025256
| 383.15 | 1300000 | 4227.5815 | 3715.8735 | 951.5078 | 0.00025501 | 110 | 12.83 | 4.2276 | 3.7159 | 0.95151 | 0.00025501
| 382.15 | 1300000 | 4226.1118 | 3720.8418 | 952.2687 | 0.0002575 | 109 | 12.83 | 4.2261 | 3.7208 | 0.95227 | 0.0002575
| 381.15 | 1300000 | 4224.665 | 3725.8191 | 953.0251 | 0.00026003 | 108 | 12.83 | 4.2247 | 3.7258 | 0.95303 | 0.00026003
| 380.15 | 1300000 | 4223.2407 | 3730.8052 | 953.7771 | 0.00026261 | 107 | 12.83 | 4.2232 | 3.7308 | 0.95378 | 0.00026261
| 379.15 | 1300000 | 4221.8389 | 3735.8 | 954.5247 | 0.00026524 | 106 | 12.83 | 4.2218 | 3.7358 | 0.95452 | 0.00026524
| 378.15 | 1300000 | 4220.459 | 3740.8035 | 955.2677 | 0.00026792 | 105 | 12.83 | 4.2205 | 3.7408 | 0.95527 | 0.00026792
| 377.15 | 1300000 | 4219.1016 | 3745.8154 | 956.0062 | 0.00027065 | 104 | 12.83 | 4.2191 | 3.7458 | 0.95601 | 0.00027065
| 376.15 | 1300000 | 4217.7656 | 3750.8359 | 956.7403 | 0.00027342 | 103 | 12.83 | 4.2178 | 3.7508 | 0.95674 | 0.00027342
| 375.15 | 1300000 | 4216.4521 | 3755.8643 | 957.4698 | 0.00027625 | 102 | 12.83 | 4.2165 | 3.7559 | 0.95747 | 0.00027625
| 374.15 | 1300000 | 4215.1597 | 3760.9009 | 958.1948 | 0.00027913 | 101 | 12.83 | 4.2152 | 3.7609 | 0.95819 | 0.00027913
| 373.15 | 1300000 | 4213.8896 | 3765.9451 | 958.9152 | 0.00028207 | 100 | 12.83 | 4.2139 | 3.7659 | 0.95892 | 0.00028207
| 372.15 | 1300000 | 4212.6406 | 3770.9971 | 959.6311 | 0.00028506 | 99 | 12.83 | 4.2126 | 3.771 | 0.95963 | 0.00028506
| 371.15 | 1300000 | 4211.4131 | 3776.0564 | 960.3423 | 0.0002881 | 98 | 12.83 | 4.2114 | 3.7761 | 0.96034 | 0.0002881
| 370.15 | 1300000 | 4210.2065 | 3781.1233 | 961.049 | 0.00029121 | 97 | 12.83 | 4.2102 | 3.7811 | 0.96105 | 0.00029121
| 369.15 | 1300000 | 4209.0215 | 3786.197 | 961.7511 | 0.00029438 | 96 | 12.83 | 4.209 | 3.7862 | 0.96175 | 0.00029438
| 368.15 | 1300000 | 4207.8579 | 3791.2776 | 962.4485 | 0.00029761 | 95 | 12.83 | 4.2079 | 3.7913 | 0.96245 | 0.00029761
| 367.15 | 1300000 | 4206.7148 | 3796.365 | 963.1412 | 0.0003009 | 94 | 12.83 | 4.2067 | 3.7964 | 0.96314 | 0.0003009
| 366.15 | 1300000 | 4205.5933 | 3801.4587 | 963.8293 | 0.00030426 | 93 | 12.83 | 4.2056 | 3.8015 | 0.96383 | 0.00030426
| 365.15 | 1300000 | 4204.4922 | 3806.5586 | 964.5127 | 0.00030768 | 92 | 12.83 | 4.2045 | 3.8066 | 0.96451 | 0.00030768
| 364.15 | 1300000 | 4203.4121 | 3811.6643 | 965.1913 | 0.00031117 | 91 | 12.83 | 4.2034 | 3.8117 | 0.96519 | 0.00031117
| 363.15 | 1300000 | 4202.353 | 3816.7759 | 965.8652 | 0.00031473 | 90 | 12.83 | 4.2024 | 3.8168 | 0.96587 | 0.00031473
| 362.15 | 1300000 | 4201.3145 | 3821.8928 | 966.5344 | 0.00031837 | 89 | 12.83 | 4.2013 | 3.8219 | 0.96653 | 0.00031837
| 361.15 | 1300000 | 4200.2964 | 3827.0149 | 967.1987 | 0.00032208 | 88 | 12.83 | 4.2003 | 3.827 | 0.9672 | 0.00032208
| 360.15 | 1300000 | 4199.2993 | 3832.1418 | 967.8583 | 0.00032586 | 87 | 12.83 | 4.1993 | 3.8321 | 0.96786 | 0.00032586
| 359.15 | 1300000 | 4198.3228 | 3837.2732 | 968.513 | 0.00032972 | 86 | 12.83 | 4.1983 | 3.8373 | 0.96851 | 0.00032972
| 358.15 | 1300000 | 4197.3662 | 3842.4089 | 969.1628 | 0.00033367 | 85 | 12.83 | 4.1974 | 3.8424 | 0.96916 | 0.00033367
| 357.15 | 1300000 | 4196.4307 | 3847.5483 | 969.8078 | 0.00033769 | 84 | 12.83 | 4.1964 | 3.8475 | 0.96981 | 0.00033769
| 356.15 | 1300000 | 4195.5156 | 3852.6914 | 970.4478 | 0.0003418 | 83 | 12.83 | 4.1955 | 3.8527 | 0.97045 | 0.0003418
| 355.15 | 1300000 | 4194.6211 | 3857.8376 | 971.0829 | 0.000346 | 82 | 12.83 | 4.1946 | 3.8578 | 0.97108 | 0.000346
| 354.15 | 1300000 | 4193.7471 | 3862.9866 | 971.713 | 0.00035029 | 81 | 12.83 | 4.1937 | 3.863 | 0.97171 | 0.00035029
| 353.15 | 1300000 | 4192.8931 | 3868.1382 | 972.3381 | 0.00035467 | 80 | 12.83 | 4.1929 | 3.8681 | 0.97234 | 0.00035467
| 352.15 | 1300000 | 4192.0596 | 3873.2915 | 972.9581 | 0.00035914 | 79 | 12.83 | 4.1921 | 3.8733 | 0.97296 | 0.00035914
| 351.15 | 1300000 | 4191.2466 | 3878.4465 | 973.5731 | 0.00036372 | 78 | 12.83 | 4.1912 | 3.8784 | 0.97357 | 0.00036372
| 350.15 | 1300000 | 4190.4541 | 3883.6028 | 974.183 | 0.00036839 | 77 | 12.83 | 4.1905 | 3.8836 | 0.97418 | 0.00036839
| 349.15 | 1300000 | 4189.6821 | 3888.7595 | 974.7877 | 0.00037317 | 76 | 12.83 | 4.1897 | 3.8888 | 0.97479 | 0.00037317
| 348.15 | 1300000 | 4188.9302 | 3893.9167 | 975.3873 | 0.00037805 | 75 | 12.83 | 4.1889 | 3.8939 | 0.97539 | 0.00037805
| 347.15 | 1300000 | 4188.1987 | 3899.0735 | 975.9816 | 0.00038305 | 74 | 12.83 | 4.1882 | 3.8991 | 0.97598 | 0.00038305
| 346.15 | 1300000 | 4187.4873 | 3904.2295 | 976.5707 | 0.00038816 | 73 | 12.83 | 4.1875 | 3.9042 | 0.97657 | 0.00038816
| 345.15 | 1300000 | 4186.7964 | 3909.384 | 977.1545 | 0.00039338 | 72 | 12.83 | 4.1868 | 3.9094 | 0.97715 | 0.00039338
| 344.15 | 1300000 | 4186.1265 | 3914.5366 | 977.733 | 0.00039873 | 71 | 12.83 | 4.1861 | 3.9145 | 0.97773 | 0.00039873
| 343.15 | 1300000 | 4185.4761 | 3919.687 | 978.3062 | 0.0004042 | 70 | 12.83 | 4.1855 | 3.9197 | 0.97831 | 0.0004042
| 342.15 | 1300000 | 4184.8467 | 3924.8342 | 978.8739 | 0.0004098 | 69 | 12.83 | 4.1848 | 3.9248 | 0.97887 | 0.0004098
| 341.15 | 1300000 | 4184.2373 | 3929.9775 | 979.4362 | 0.00041553 | 68 | 12.83 | 4.1842 | 3.93 | 0.97944 | 0.00041553
| 340.15 | 1300000 | 4183.6484 | 3935.1167 | 979.9929 | 0.00042139 | 67 | 12.83 | 4.1836 | 3.9351 | 0.97999 | 0.00042139
| 339.15 | 1300000 | 4183.0801 | 3940.2507 | 980.5441 | 0.0004274 | 66 | 12.83 | 4.1831 | 3.9403 | 0.98054 | 0.0004274
| 338.15 | 1300000 | 4182.5322 | 3945.3792 | 981.0898 | 0.00043355 | 65 | 12.83 | 4.1825 | 3.9454 | 0.98109 | 0.00043355
| 337.15 | 1300000 | 4182.0049 | 3950.501 | 981.6298 | 0.00043986 | 64 | 12.83 | 4.182 | 3.9505 | 0.98163 | 0.00043986
| 336.15 | 1300000 | 4181.498 | 3955.6157 | 982.1641 | 0.00044631 | 63 | 12.83 | 4.1815 | 3.9556 | 0.98216 | 0.00044631
| 335.15 | 1300000 | 4181.0117 | 3960.7224 | 982.6927 | 0.00045293 | 62 | 12.83 | 4.181 | 3.9607 | 0.98269 | 0.00045293
| 334.15 | 1300000 | 4180.5459 | 3965.8203 | 983.2155 | 0.00045972 | 61 | 12.83 | 4.1805 | 3.9658 | 0.98322 | 0.00045972
| 333.15 | 1300000 | 4180.1006 | 3970.9087 | 983.7325 | 0.00046667 | 60 | 12.83 | 4.1801 | 3.9709 | 0.98373 | 0.00046667
| 332.15 | 1300000 | 4179.6758 | 3975.9866 | 984.2436 | 0.0004738 | 59 | 12.83 | 4.1797 | 3.976 | 0.98424 | 0.0004738
| 331.15 | 1300000 | 4179.2715 | 3981.053 | 984.7487 | 0.00048112 | 58 | 12.83 | 4.1793 | 3.9811 | 0.98475 | 0.00048112
| 330.15 | 1300000 | 4178.8882 | 3986.1072 | 985.2479 | 0.00048862 | 57 | 12.83 | 4.1789 | 3.9861 | 0.98525 | 0.00048862
| 329.15 | 1300000 | 4178.5259 | 3991.1479 | 985.7409 | 0.00049632 | 56 | 12.83 | 4.1785 | 3.9911 | 0.98574 | 0.00049632
| 328.15 | 1300000 | 4178.1841 | 3996.1748 | 986.2278 | 0.00050423 | 55 | 12.83 | 4.1782 | 3.9962 | 0.98623 | 0.00050423
| 327.15 | 1300000 | 4177.8628 | 4001.1863 | 986.7086 | 0.00051234 | 54 | 12.83 | 4.1779 | 4.0012 | 0.98671 | 0.00051234
| 326.15 | 1300000 | 4177.563 | 4006.1814 | 987.183 | 0.00052067 | 53 | 12.83 | 4.1776 | 4.0062 | 0.98718 | 0.00052067
| 325.15 | 1300000 | 4177.2837 | 4011.1592 | 987.6511 | 0.00052923 | 52 | 12.83 | 4.1773 | 4.0112 | 0.98765 | 0.00052923
| 324.15 | 1300000 | 4177.0254 | 4016.1187 | 988.1129 | 0.00053802 | 51 | 12.83 | 4.177 | 4.0161 | 0.98811 | 0.00053802
| 323.15 | 1300000 | 4176.7886 | 4021.0583 | 988.5682 | 0.00054706 | 50 | 12.83 | 4.1768 | 4.0211 | 0.98857 | 0.00054706
| 322.15 | 1300000 | 4176.5728 | 4025.9771 | 989.0169 | 0.00055635 | 49 | 12.83 | 4.1766 | 4.026 | 0.98902 | 0.00055635
| 321.15 | 1300000 | 4176.3779 | 4030.874 | 989.459 | 0.0005659 | 48 | 12.83 | 4.1764 | 4.0309 | 0.98946 | 0.0005659
| 320.15 | 1300000 | 4176.2051 | 4035.7476 | 989.8945 | 0.00057572 | 47 | 12.83 | 4.1762 | 4.0357 | 0.98989 | 0.00057572
| 319.15 | 1300000 | 4176.0537 | 4040.5967 | 990.3232 | 0.00058583 | 46 | 12.83 | 4.1761 | 4.0406 | 0.99032 | 0.00058583
| 318.15 | 1300000 | 4175.9238 | 4045.4199 | 990.7449 | 0.00059623 | 45 | 12.83 | 4.1759 | 4.0454 | 0.99074 | 0.00059623
| 317.15 | 1300000 | 4175.8159 | 4050.2161 | 991.1599 | 0.00060694 | 44 | 12.83 | 4.1758 | 4.0502 | 0.99116 | 0.00060694
| 316.15 | 1300000 | 4175.73 | 4054.9834 | 991.5677 | 0.00061796 | 43 | 12.83 | 4.1757 | 4.055 | 0.99157 | 0.00061796
| 315.15 | 1300000 | 4175.6665 | 4059.7207 | 991.9684 | 0.00062931 | 42 | 12.83 | 4.1757 | 4.0597 | 0.99197 | 0.00062931
| 314.15 | 1300000 | 4175.6255 | 4064.4268 | 992.3619 | 0.00064101 | 41 | 12.83 | 4.1756 | 4.0644 | 0.99236 | 0.00064101
| 313.15 | 1300000 | 4175.6074 | 4069.0999 | 992.7481 | 0.00065307 | 40 | 12.83 | 4.1756 | 4.0691 | 0.99275 | 0.00065307
| 312.15 | 1300000 | 4175.6123 | 4073.7385 | 993.127 | 0.00066551 | 39 | 12.83 | 4.1756 | 4.0737 | 0.99313 | 0.00066551
| 311.15 | 1300000 | 4175.6411 | 4078.3413 | 993.4982 | 0.00067833 | 38 | 12.83 | 4.1756 | 4.0783 | 0.9935 | 0.00067833
| 310.15 | 1300000 | 4175.6934 | 4082.9065 | 993.8619 | 0.00069156 | 37 | 12.83 | 4.1757 | 4.0829 | 0.99386 | 0.00069156
| 309.15 | 1300000 | 4175.7705 | 4087.4324 | 994.2178 | 0.00070522 | 36 | 12.83 | 4.1758 | 4.0874 | 0.99422 | 0.00070522
| 308.15 | 1300000 | 4175.8726 | 4091.9177 | 994.5659 | 0.00071932 | 35 | 12.83 | 4.1759 | 4.0919 | 0.99457 | 0.00071932
| 307.15 | 1300000 | 4176 | 4096.3608 | 994.9061 | 0.00073389 | 34 | 12.83 | 4.176 | 4.0964 | 0.99491 | 0.00073389
| 306.15 | 1300000 | 4176.1538 | 4100.7598 | 995.2381 | 0.00074894 | 33 | 12.83 | 4.1762 | 4.1008 | 0.99524 | 0.00074894
| 305.15 | 1300000 | 4176.335 | 4105.1128 | 995.562 | 0.0007645 | 32 | 12.83 | 4.1763 | 4.1051 | 0.99556 | 0.0007645
| 304.15 | 1300000 | 4176.5439 | 4109.4189 | 995.8774 | 0.00078059 | 31 | 12.83 | 4.1765 | 4.1094 | 0.99588 | 0.00078059
| 303.15 | 1300000 | 4176.7817 | 4113.6758 | 996.1844 | 0.00079723 | 30 | 12.83 | 4.1768 | 4.1137 | 0.99618 | 0.00079723
| 302.15 | 1300000 | 4177.0493 | 4117.8813 | 996.4828 | 0.00081446 | 29 | 12.83 | 4.177 | 4.1179 | 0.99648 | 0.00081446
| 301.15 | 1300000 | 4177.3486 | 4122.0352 | 996.7724 | 0.0008323 | 28 | 12.83 | 4.1773 | 4.122 | 0.99677 | 0.0008323
| 300.15 | 1300000 | 4177.6802 | 4126.1343 | 997.0531 | 0.00085078 | 27 | 12.83 | 4.1777 | 4.1261 | 0.99705 | 0.00085078
| 299.15 | 1300000 | 4178.0464 | 4130.1777 | 997.3247 | 0.00086994 | 26 | 12.83 | 4.178 | 4.1302 | 0.99732 | 0.00086994
| 298.15 | 1300000 | 4178.4487 | 4134.1631 | 997.5871 | 0.0008898 | 25 | 12.83 | 4.1784 | 4.1342 | 0.99759 | 0.0008898
| 297.15 | 1300000 | 4178.8887 | 4138.0894 | 997.84 | 0.00091041 | 24 | 12.83 | 4.1789 | 4.1381 | 0.99784 | 0.00091041
| 296.15 | 1300000 | 4179.3691 | 4141.9551 | 998.0833 | 0.0009318 | 23 | 12.83 | 4.1794 | 4.142 | 0.99808 | 0.0009318
| 295.15 | 1300000 | 4179.8926 | 4145.7578 | 998.3168 | 0.00095402 | 22 | 12.83 | 4.1799 | 4.1458 | 0.99832 | 0.00095402
| 294.15 | 1300000 | 4180.4609 | 4149.4966 | 998.5404 | 0.0009771 | 21 | 12.83 | 4.1805 | 4.1495 | 0.99854 | 0.0009771
| 293.15 | 1300000 | 4181.0786 | 4153.1694 | 998.7537 | 0.0010011 | 20 | 12.83 | 4.1811 | 4.1532 | 0.99875 | 0.0010011
| 292.15 | 1300000 | 4181.748 | 4156.7754 | 998.9567 | 0.0010261 | 19 | 12.83 | 4.1817 | 4.1568 | 0.99896 | 0.0010261
| 291.15 | 1300000 | 4182.4731 | 4160.3125 | 999.149 | 0.001052 | 18 | 12.83 | 4.1825 | 4.1603 | 0.99915 | 0.001052
| 290.15 | 1300000 | 4183.2593 | 4163.7793 | 999.3304 | 0.0010791 | 17 | 12.83 | 4.1833 | 4.1638 | 0.99933 | 0.0010791
| 289.15 | 1300000 | 4184.1099 | 4167.1753 | 999.5007 | 0.0011073 | 16 | 12.83 | 4.1841 | 4.1672 | 0.9995 | 0.0011073
| 288.15 | 1300000 | 4185.0312 | 4170.499 | 999.6596 | 0.0011367 | 15 | 12.83 | 4.185 | 4.1705 | 0.99966 | 0.0011367
| 287.15 | 1300000 | 4186.0288 | 4173.749 | 999.8069 | 0.0011674 | 14 | 12.83 | 4.186 | 4.1737 | 0.99981 | 0.0011674
| 286.15 | 1300000 | 4187.1094 | 4176.9248 | 999.9422 | 0.0011994 | 13 | 12.83 | 4.1871 | 4.1769 | 0.99994 | 0.0011994
| 285.15 | 1300000 | 4188.2803 | 4180.0254 | 1000.0653 | 0.0012329 | 12 | 12.83 | 4.1883 | 4.18 | 1.0001 | 0.0012329
| 284.15 | 1300000 | 4189.5498 | 4183.0503 | 1000.1758 | 0.0012679 | 11 | 12.83 | 4.1895 | 4.1831 | 1.0002 | 0.0012679
| 283.15 | 1300000 | 4190.9268 | 4185.9985 | 1000.2735 | 0.0013046 | 10 | 12.83 | 4.1909 | 4.186 | 1.0003 | 0.0013046
| 282.15 | 1300000 | 4192.4219 | 4188.8706 | 1000.3579 | 0.0013429 | 9 | 12.83 | 4.1924 | 4.1889 | 1.0004 | 0.0013429
| 281.15 | 1300000 | 4194.0454 | 4191.666 | 1000.4287 | 0.0013832 | 8 | 12.83 | 4.194 | 4.1917 | 1.0004 | 0.0013832
| 280.15 | 1300000 | 4195.8101 | 4194.3848 | 1000.4855 | 0.0014253 | 7 | 12.83 | 4.1958 | 4.1944 | 1.0005 | 0.0014253
| 279.15 | 1300000 | 4197.73 | 4197.0269 | 1000.528 | 0.0014696 | 6 | 12.83 | 4.1977 | 4.197 | 1.0005 | 0.0014696
| 278.15 | 1300000 | 4199.8198 | 4199.5938 | 1000.5555 | 0.0015161 | 5 | 12.83 | 4.1998 | 4.1996 | 1.0006 | 0.0015161
| 277.15 | 1300000 | 4202.0967 | 4202.0859 | 1000.5677 | 0.0015651 | 4 | 12.83 | 4.2021 | 4.2021 | 1.0006 | 0.0015651
| 276.15 | 1300000 | 4204.5796 | 4204.5044 | 1000.5641 | 0.0016166 | 3 | 12.83 | 4.2046 | 4.2045 | 1.0006 | 0.0016166
| 275.15 | 1300000 | 4207.2881 | 4206.8501 | 1000.5443 | 0.0016709 | 2 | 12.83 | 4.2073 | 4.2069 | 1.0005 | 0.0016709
| 274.15 | 1300000 | 4210.2461 | 4209.1255 | 1000.5075 | 0.0017281 | 0.99999 | 12.83 | 4.2102 | 4.2091 | 1.0005 | 0.0017281
| 273.15 | 1300000 | 4213.478 | 4211.332 | 1000.4532 | 0.0017885 | -6.1035e-06 | 12.83 | 4.2135 | 4.2113 | 1.0005 | 0.0017885
| 473.15 | 1200000 | 2581.4197 | 1836.3824 | 5.9059 | 1.583e-05 | 200 | 11.843 | 2.5814 | 1.8364 | 0.0059059 | 1.583e-05
| 472.15 | 1200000 | 2594.7178 | 1844.2867 | 5.9231 | 1.5786e-05 | 199 | 11.843 | 2.5947 | 1.8443 | 0.0059231 | 1.5786e-05
| 471.15 | 1200000 | 2608.7903 | 1852.7109 | 5.9405 | 1.5742e-05 | 198 | 11.843 | 2.6088 | 1.8527 | 0.0059405 | 1.5742e-05
| 470.15 | 1200000 | 2623.7224 | 1861.7139 | 5.9581 | 1.5698e-05 | 197 | 11.843 | 2.6237 | 1.8617 | 0.0059581 | 1.5698e-05
| 469.15 | 1200000 | 2639.6096 | 1871.3622 | 5.9758 | 1.5654e-05 | 196 | 11.843 | 2.6396 | 1.8714 | 0.0059758 | 1.5654e-05
| 468.15 | 1200000 | 2656.5605 | 1881.7316 | 5.9937 | 1.561e-05 | 195 | 11.843 | 2.6566 | 1.8817 | 0.0059937 | 1.561e-05
| 467.15 | 1200000 | 2674.6987 | 1892.9073 | 6.0118 | 1.5566e-05 | 194 | 11.843 | 2.6747 | 1.8929 | 0.0060118 | 1.5566e-05
| 466.15 | 1200000 | 2694.1638 | 1904.9865 | 6.0301 | 1.5522e-05 | 193 | 11.843 | 2.6942 | 1.905 | 0.0060301 | 1.5522e-05
| 465.15 | 1200000 | 2715.1152 | 1918.0786 | 6.0486 | 1.5478e-05 | 192 | 11.843 | 2.7151 | 1.9181 | 0.0060486 | 1.5478e-05
| 464.15 | 1200000 | 2737.7334 | 1932.3081 | 6.0673 | 1.5434e-05 | 191 | 11.843 | 2.7377 | 1.9323 | 0.0060673 | 1.5434e-05
| 463.15 | 1200000 | 2762.2234 | 1947.8157 | 6.0863 | 1.539e-05 | 190 | 11.843 | 2.7622 | 1.9478 | 0.0060863 | 1.539e-05
| 462.15 | 1200000 | 2788.8193 | 1964.761 | 6.1055 | 1.5345e-05 | 189 | 11.843 | 2.7888 | 1.9648 | 0.0061055 | 1.5345e-05
| 461.15 | 1200000 | 2817.7869 | 1983.3247 | 6.1249 | 1.5301e-05 | 188 | 11.843 | 2.8178 | 1.9833 | 0.0061249 | 1.5301e-05
| 460.15 | 1200000 | 4433.6973 | 3367.7725 | 879.4291 | 0.0001442 | 187 | 11.843 | 4.4337 | 3.3678 | 0.87943 | 0.0001442
| 459.15 | 1200000 | 4429.3691 | 3371.7742 | 880.5463 | 0.00014502 | 186 | 11.843 | 4.4294 | 3.3718 | 0.88055 | 0.00014502
| 458.15 | 1200000 | 4425.103 | 3375.792 | 881.6581 | 0.00014586 | 185 | 11.843 | 4.4251 | 3.3758 | 0.88166 | 0.00014586
| 457.15 | 1200000 | 4420.8975 | 3379.8257 | 882.7645 | 0.00014671 | 184 | 11.843 | 4.4209 | 3.3798 | 0.88276 | 0.00014671
| 456.15 | 1200000 | 4416.7515 | 3383.8757 | 883.8657 | 0.00014756 | 183 | 11.843 | 4.4168 | 3.3839 | 0.88387 | 0.00014756
| 455.15 | 1200000 | 4412.6646 | 3387.9414 | 884.9615 | 0.00014843 | 182 | 11.843 | 4.4127 | 3.3879 | 0.88496 | 0.00014843
| 454.15 | 1200000 | 4408.6353 | 3392.0227 | 886.0521 | 0.0001493 | 181 | 11.843 | 4.4086 | 3.392 | 0.88605 | 0.0001493
| 453.15 | 1200000 | 4404.6631 | 3396.1196 | 887.1375 | 0.00015019 | 180 | 11.843 | 4.4047 | 3.3961 | 0.88714 | 0.00015019
| 452.15 | 1200000 | 4400.7461 | 3400.2322 | 888.2177 | 0.00015108 | 179 | 11.843 | 4.4007 | 3.4002 | 0.88822 | 0.00015108
| 451.15 | 1200000 | 4396.8848 | 3404.3601 | 889.2928 | 0.00015199 | 178 | 11.843 | 4.3969 | 3.4044 | 0.88929 | 0.00015199
| 450.15 | 1200000 | 4393.0771 | 3408.5034 | 890.3628 | 0.00015291 | 177 | 11.843 | 4.3931 | 3.4085 | 0.89036 | 0.00015291
| 449.15 | 1200000 | 4389.3228 | 3412.6616 | 891.4277 | 0.00015384 | 176 | 11.843 | 4.3893 | 3.4127 | 0.89143 | 0.00015384
| 448.15 | 1200000 | 4385.6206 | 3416.8352 | 892.4875 | 0.00015478 | 175 | 11.843 | 4.3856 | 3.4168 | 0.89249 | 0.00015478
| 447.15 | 1200000 | 4381.9702 | 3421.0237 | 893.5424 | 0.00015573 | 174 | 11.843 | 4.382 | 3.421 | 0.89354 | 0.00015573
| 446.15 | 1200000 | 4378.3706 | 3425.2268 | 894.5922 | 0.00015669 | 173 | 11.843 | 4.3784 | 3.4252 | 0.89459 | 0.00015669
| 445.15 | 1200000 | 4374.8203 | 3429.4451 | 895.6371 | 0.00015767 | 172 | 11.843 | 4.3748 | 3.4294 | 0.89564 | 0.00015767
| 444.15 | 1200000 | 4371.3198 | 3433.6777 | 896.6771 | 0.00015865 | 171 | 11.843 | 4.3713 | 3.4337 | 0.89668 | 0.00015865
| 443.15 | 1200000 | 4367.8672 | 3437.9248 | 897.7122 | 0.00015965 | 170 | 11.843 | 4.3679 | 3.4379 | 0.89771 | 0.00015965
| 442.15 | 1200000 | 4364.4624 | 3442.1865 | 898.7423 | 0.00016067 | 169 | 11.843 | 4.3645 | 3.4422 | 0.89874 | 0.00016067
| 441.15 | 1200000 | 4361.1045 | 3446.4626 | 899.7676 | 0.00016169 | 168 | 11.843 | 4.3611 | 3.4465 | 0.89977 | 0.00016169
| 440.15 | 1200000 | 4357.793 | 3450.7529 | 900.7881 | 0.00016273 | 167 | 11.843 | 4.3578 | 3.4508 | 0.90079 | 0.00016273
| 439.15 | 1200000 | 4354.5264 | 3455.0574 | 901.8038 | 0.00016378 | 166 | 11.843 | 4.3545 | 3.4551 | 0.9018 | 0.00016378
| 438.15 | 1200000 | 4351.3047 | 3459.3757 | 902.8146 | 0.00016485 | 165 | 11.843 | 4.3513 | 3.4594 | 0.90281 | 0.00016485
| 437.15 | 1200000 | 4348.1274 | 3463.7083 | 903.8208 | 0.00016593 | 164 | 11.843 | 4.3481 | 3.4637 | 0.90382 | 0.00016593
| 436.15 | 1200000 | 4344.9932 | 3468.0544 | 904.8222 | 0.00016702 | 163 | 11.843 | 4.345 | 3.4681 | 0.90482 | 0.00016702
| 435.15 | 1200000 | 4341.9019 | 3472.4146 | 905.8188 | 0.00016813 | 162 | 11.843 | 4.3419 | 3.4724 | 0.90582 | 0.00016813
| 434.15 | 1200000 | 4338.853 | 3476.7883 | 906.8109 | 0.00016925 | 161 | 11.843 | 4.3389 | 3.4768 | 0.90681 | 0.00016925
| 433.15 | 1200000 | 4335.8452 | 3481.1755 | 907.7982 | 0.00017039 | 160 | 11.843 | 4.3358 | 3.4812 | 0.9078 | 0.00017039
| 432.15 | 1200000 | 4332.8784 | 3485.5764 | 908.7808 | 0.00017154 | 159 | 11.843 | 4.3329 | 3.4856 | 0.90878 | 0.00017154
| 431.15 | 1200000 | 4329.9521 | 3489.9905 | 909.7588 | 0.00017271 | 158 | 11.843 | 4.33 | 3.49 | 0.90976 | 0.00017271
| 430.15 | 1200000 | 4327.0654 | 3494.418 | 910.7321 | 0.00017389 | 157 | 11.843 | 4.3271 | 3.4944 | 0.91073 | 0.00017389
| 429.15 | 1200000 | 4324.2178 | 3498.8586 | 911.7009 | 0.00017509 | 156 | 11.843 | 4.3242 | 3.4989 | 0.9117 | 0.00017509
| 428.15 | 1200000 | 4321.4087 | 3503.3123 | 912.6651 | 0.00017631 | 155 | 11.843 | 4.3214 | 3.5033 | 0.91267 | 0.00017631
| 427.15 | 1200000 | 4318.6382 | 3507.7793 | 913.6247 | 0.00017754 | 154 | 11.843 | 4.3186 | 3.5078 | 0.91362 | 0.00017754
| 426.15 | 1200000 | 4315.9048 | 3512.259 | 914.5797 | 0.00017879 | 153 | 11.843 | 4.3159 | 3.5123 | 0.91458 | 0.00017879
| 425.15 | 1200000 | 4313.208 | 3516.7517 | 915.5302 | 0.00018006 | 152 | 11.843 | 4.3132 | 3.5168 | 0.91553 | 0.00018006
| 424.15 | 1200000 | 4310.5483 | 3521.2571 | 916.4762 | 0.00018134 | 151 | 11.843 | 4.3105 | 3.5213 | 0.91648 | 0.00018134
| 423.15 | 1200000 | 4307.9243 | 3525.7751 | 917.4177 | 0.00018264 | 150 | 11.843 | 4.3079 | 3.5258 | 0.91742 | 0.00018264
| 422.15 | 1200000 | 4305.3354 | 3530.3059 | 918.3546 | 0.00018397 | 149 | 11.843 | 4.3053 | 3.5303 | 0.91835 | 0.00018397
| 421.15 | 1200000 | 4302.7822 | 3534.8491 | 919.2871 | 0.00018531 | 148 | 11.843 | 4.3028 | 3.5348 | 0.91929 | 0.00018531
| 420.15 | 1200000 | 4300.2632 | 3539.4048 | 920.2151 | 0.00018667 | 147 | 11.843 | 4.3003 | 3.5394 | 0.92022 | 0.00018667
| 419.15 | 1200000 | 4297.7778 | 3543.9729 | 921.1386 | 0.00018804 | 146 | 11.843 | 4.2978 | 3.544 | 0.92114 | 0.00018804
| 418.15 | 1200000 | 4295.3267 | 3548.5532 | 922.0577 | 0.00018944 | 145 | 11.843 | 4.2953 | 3.5486 | 0.92206 | 0.00018944
| 417.15 | 1200000 | 4292.9082 | 3553.146 | 922.9723 | 0.00019086 | 144 | 11.843 | 4.2929 | 3.5531 | 0.92297 | 0.00019086
| 416.15 | 1200000 | 4290.5229 | 3557.7507 | 923.8825 | 0.0001923 | 143 | 11.843 | 4.2905 | 3.5578 | 0.92388 | 0.0001923
| 415.15 | 1200000 | 4288.1694 | 3562.3674 | 924.7882 | 0.00019377 | 142 | 11.843 | 4.2882 | 3.5624 | 0.92479 | 0.00019377
| 414.15 | 1200000 | 4285.8481 | 3566.9963 | 925.6896 | 0.00019525 | 141 | 11.843 | 4.2858 | 3.567 | 0.92569 | 0.00019525
| 413.15 | 1200000 | 4283.5581 | 3571.637 | 926.5865 | 0.00019676 | 140 | 11.843 | 4.2836 | 3.5716 | 0.92659 | 0.00019676
| 412.15 | 1200000 | 4281.2993 | 3576.2896 | 927.479 | 0.00019828 | 139 | 11.843 | 4.2813 | 3.5763 | 0.92748 | 0.00019828
| 411.15 | 1200000 | 4279.0713 | 3580.9539 | 928.3671 | 0.00019983 | 138 | 11.843 | 4.2791 | 3.581 | 0.92837 | 0.00019983
| 410.15 | 1200000 | 4276.873 | 3585.6296 | 929.2509 | 0.00020141 | 137 | 11.843 | 4.2769 | 3.5856 | 0.92925 | 0.00020141
| 409.15 | 1200000 | 4274.7051 | 3590.3171 | 930.1302 | 0.00020301 | 136 | 11.843 | 4.2747 | 3.5903 | 0.93013 | 0.00020301
| 408.15 | 1200000 | 4272.5669 | 3595.0164 | 931.0052 | 0.00020463 | 135 | 11.843 | 4.2726 | 3.595 | 0.93101 | 0.00020463
| 407.15 | 1200000 | 4270.4575 | 3599.7268 | 931.8758 | 0.00020628 | 134 | 11.843 | 4.2705 | 3.5997 | 0.93188 | 0.00020628
| 406.15 | 1200000 | 4268.3774 | 3604.4487 | 932.742 | 0.00020795 | 133 | 11.843 | 4.2684 | 3.6044 | 0.93274 | 0.00020795
| 405.15 | 1200000 | 4266.3257 | 3609.1819 | 933.6039 | 0.00020965 | 132 | 11.843 | 4.2663 | 3.6092 | 0.9336 | 0.00020965
| 404.15 | 1200000 | 4264.3018 | 3613.9263 | 934.4614 | 0.00021138 | 131 | 11.843 | 4.2643 | 3.6139 | 0.93446 | 0.00021138
| 403.15 | 1200000 | 4262.3062 | 3618.6819 | 935.3145 | 0.00021314 | 130 | 11.843 | 4.2623 | 3.6187 | 0.93531 | 0.00021314
| 402.15 | 1200000 | 4260.3379 | 3623.4485 | 936.1633 | 0.00021492 | 129 | 11.843 | 4.2603 | 3.6234 | 0.93616 | 0.00021492
| 401.15 | 1200000 | 4258.397 | 3628.2261 | 937.0077 | 0.00021673 | 128 | 11.843 | 4.2584 | 3.6282 | 0.93701 | 0.00021673
| 400.15 | 1200000 | 4256.4834 | 3633.0146 | 937.8477 | 0.00021857 | 127 | 11.843 | 4.2565 | 3.633 | 0.93785 | 0.00021857
| 399.15 | 1200000 | 4254.5957 | 3637.814 | 938.6834 | 0.00022044 | 126 | 11.843 | 4.2546 | 3.6378 | 0.93868 | 0.00022044
| 398.15 | 1200000 | 4252.7349 | 3642.6243 | 939.5147 | 0.00022234 | 125 | 11.843 | 4.2527 | 3.6426 | 0.93951 | 0.00022234
| 397.15 | 1200000 | 4250.9004 | 3647.4448 | 940.3417 | 0.00022427 | 124 | 11.843 | 4.2509 | 3.6474 | 0.94034 | 0.00022427
| 396.15 | 1200000 | 4249.0913 | 3652.2764 | 941.1643 | 0.00022623 | 123 | 11.843 | 4.2491 | 3.6523 | 0.94116 | 0.00022623
| 395.15 | 1200000 | 4247.3081 | 3657.1182 | 941.9825 | 0.00022822 | 122 | 11.843 | 4.2473 | 3.6571 | 0.94198 | 0.00022822
| 394.15 | 1200000 | 4245.5503 | 3661.9705 | 942.7964 | 0.00023025 | 121 | 11.843 | 4.2456 | 3.662 | 0.9428 | 0.00023025
| 393.15 | 1200000 | 4243.8174 | 3666.833 | 943.606 | 0.00023231 | 120 | 11.843 | 4.2438 | 3.6668 | 0.94361 | 0.00023231
| 392.15 | 1200000 | 4242.1094 | 3671.7058 | 944.4111 | 0.00023441 | 119 | 11.843 | 4.2421 | 3.6717 | 0.94441 | 0.00023441
| 391.15 | 1200000 | 4240.4263 | 3676.5886 | 945.2119 | 0.00023654 | 118 | 11.843 | 4.2404 | 3.6766 | 0.94521 | 0.00023654
| 390.15 | 1200000 | 4238.7671 | 3681.4817 | 946.0082 | 0.00023871 | 117 | 11.843 | 4.2388 | 3.6815 | 0.94601 | 0.00023871
| 389.15 | 1200000 | 4237.1323 | 3686.3848 | 946.8002 | 0.00024092 | 116 | 11.843 | 4.2371 | 3.6864 | 0.9468 | 0.00024092
| 388.15 | 1200000 | 4235.522 | 3691.2974 | 947.5878 | 0.00024316 | 115 | 11.843 | 4.2355 | 3.6913 | 0.94759 | 0.00024316
| 387.15 | 1200000 | 4233.9351 | 3696.22 | 948.371 | 0.00024544 | 114 | 11.843 | 4.2339 | 3.6962 | 0.94837 | 0.00024544
| 386.15 | 1200000 | 4232.3716 | 3701.1521 | 949.1498 | 0.00024777 | 113 | 11.843 | 4.2324 | 3.7012 | 0.94915 | 0.00024777
| 385.15 | 1200000 | 4230.8315 | 3706.0938 | 949.9241 | 0.00025013 | 112 | 11.843 | 4.2308 | 3.7061 | 0.94992 | 0.00025013
| 384.15 | 1200000 | 4229.3149 | 3711.0449 | 950.6941 | 0.00025253 | 111 | 11.843 | 4.2293 | 3.711 | 0.95069 | 0.00025253
| 383.15 | 1200000 | 4227.8213 | 3716.0054 | 951.4596 | 0.00025498 | 110 | 11.843 | 4.2278 | 3.716 | 0.95146 | 0.00025498
| 382.15 | 1200000 | 4226.3506 | 3720.9749 | 952.2206 | 0.00025747 | 109 | 11.843 | 4.2264 | 3.721 | 0.95222 | 0.00025747
| 381.15 | 1200000 | 4224.9023 | 3725.9534 | 952.9772 | 0.00026001 | 108 | 11.843 | 4.2249 | 3.726 | 0.95298 | 0.00026001
| 380.15 | 1200000 | 4223.4771 | 3730.9409 | 953.7294 | 0.00026259 | 107 | 11.843 | 4.2235 | 3.7309 | 0.95373 | 0.00026259
| 379.15 | 1200000 | 4222.0737 | 3735.9373 | 954.4771 | 0.00026522 | 106 | 11.843 | 4.2221 | 3.7359 | 0.95448 | 0.00026522
| 378.15 | 1200000 | 4220.6929 | 3740.9424 | 955.2203 | 0.00026789 | 105 | 11.843 | 4.2207 | 3.7409 | 0.95522 | 0.00026789
| 377.15 | 1200000 | 4219.3345 | 3745.9558 | 955.959 | 0.00027062 | 104 | 11.843 | 4.2193 | 3.746 | 0.95596 | 0.00027062
| 376.15 | 1200000 | 4217.9976 | 3750.9775 | 956.6932 | 0.00027339 | 103 | 11.843 | 4.218 | 3.751 | 0.95669 | 0.00027339
| 375.15 | 1200000 | 4216.6831 | 3756.0076 | 957.4228 | 0.00027622 | 102 | 11.843 | 4.2167 | 3.756 | 0.95742 | 0.00027622
| 374.15 | 1200000 | 4215.3901 | 3761.0454 | 958.1479 | 0.0002791 | 101 | 11.843 | 4.2154 | 3.761 | 0.95815 | 0.0002791
| 373.15 | 1200000 | 4214.1187 | 3766.0913 | 958.8685 | 0.00028204 | 100 | 11.843 | 4.2141 | 3.7661 | 0.95887 | 0.00028204
| 372.15 | 1200000 | 4212.8687 | 3771.1448 | 959.5845 | 0.00028503 | 99 | 11.843 | 4.2129 | 3.7711 | 0.95958 | 0.00028503
| 371.15 | 1200000 | 4211.6401 | 3776.2058 | 960.2959 | 0.00028808 | 98 | 11.843 | 4.2116 | 3.7762 | 0.9603 | 0.00028808
| 370.15 | 1200000 | 4210.4331 | 3781.2742 | 961.0027 | 0.00029118 | 97 | 11.843 | 4.2104 | 3.7813 | 0.961 | 0.00029118
| 369.15 | 1200000 | 4209.2476 | 3786.3496 | 961.7048 | 0.00029435 | 96 | 11.843 | 4.2092 | 3.7863 | 0.9617 | 0.00029435
| 368.15 | 1200000 | 4208.083 | 3791.4319 | 962.4024 | 0.00029758 | 95 | 11.843 | 4.2081 | 3.7914 | 0.9624 | 0.00029758
| 367.15 | 1200000 | 4206.9395 | 3796.521 | 963.0953 | 0.00030087 | 94 | 11.843 | 4.2069 | 3.7965 | 0.9631 | 0.00030087
| 366.15 | 1200000 | 4205.8169 | 3801.6165 | 963.7834 | 0.00030423 | 93 | 11.843 | 4.2058 | 3.8016 | 0.96378 | 0.00030423
| 365.15 | 1200000 | 4204.7153 | 3806.718 | 964.4669 | 0.00030765 | 92 | 11.843 | 4.2047 | 3.8067 | 0.96447 | 0.00030765
| 364.15 | 1200000 | 4203.6348 | 3811.8254 | 965.1457 | 0.00031114 | 91 | 11.843 | 4.2036 | 3.8118 | 0.96515 | 0.00031114
| 363.15 | 1200000 | 4202.5747 | 3816.9387 | 965.8197 | 0.00031471 | 90 | 11.843 | 4.2026 | 3.8169 | 0.96582 | 0.00031471
| 362.15 | 1200000 | 4201.5356 | 3822.0576 | 966.489 | 0.00031834 | 89 | 11.843 | 4.2015 | 3.8221 | 0.96649 | 0.00031834
| 361.15 | 1200000 | 4200.5171 | 3827.1814 | 967.1534 | 0.00032205 | 88 | 11.843 | 4.2005 | 3.8272 | 0.96715 | 0.00032205
| 360.15 | 1200000 | 4199.5195 | 3832.3101 | 967.813 | 0.00032583 | 87 | 11.843 | 4.1995 | 3.8323 | 0.96781 | 0.00032583
| 359.15 | 1200000 | 4198.5425 | 3837.4434 | 968.4678 | 0.0003297 | 86 | 11.843 | 4.1985 | 3.8374 | 0.96847 | 0.0003297
| 358.15 | 1200000 | 4197.5859 | 3842.5808 | 969.1178 | 0.00033364 | 85 | 11.843 | 4.1976 | 3.8426 | 0.96912 | 0.00033364
| 357.15 | 1200000 | 4196.6499 | 3847.7224 | 969.7628 | 0.00033766 | 84 | 11.843 | 4.1966 | 3.8477 | 0.96976 | 0.00033766
| 356.15 | 1200000 | 4195.7349 | 3852.8672 | 970.403 | 0.00034178 | 83 | 11.843 | 4.1957 | 3.8529 | 0.9704 | 0.00034178
| 355.15 | 1200000 | 4194.8398 | 3858.0154 | 971.0381 | 0.00034597 | 82 | 11.843 | 4.1948 | 3.858 | 0.97104 | 0.00034597
| 354.15 | 1200000 | 4193.9653 | 3863.1665 | 971.6683 | 0.00035026 | 81 | 11.843 | 4.194 | 3.8632 | 0.97167 | 0.00035026
| 353.15 | 1200000 | 4193.1113 | 3868.3198 | 972.2935 | 0.00035464 | 80 | 11.843 | 4.1931 | 3.8683 | 0.97229 | 0.00035464
| 352.15 | 1200000 | 4192.2778 | 3873.4753 | 972.9136 | 0.00035912 | 79 | 11.843 | 4.1923 | 3.8735 | 0.97291 | 0.00035912
| 351.15 | 1200000 | 4191.4644 | 3878.6326 | 973.5287 | 0.00036369 | 78 | 11.843 | 4.1915 | 3.8786 | 0.97353 | 0.00036369
| 350.15 | 1200000 | 4190.6719 | 3883.7908 | 974.1386 | 0.00036837 | 77 | 11.843 | 4.1907 | 3.8838 | 0.97414 | 0.00036837
| 349.15 | 1200000 | 4189.8994 | 3888.9497 | 974.7434 | 0.00037314 | 76 | 11.843 | 4.1899 | 3.8889 | 0.97474 | 0.00037314
| 348.15 | 1200000 | 4189.1475 | 3894.1089 | 975.3431 | 0.00037803 | 75 | 11.843 | 4.1891 | 3.8941 | 0.97534 | 0.00037803
| 347.15 | 1200000 | 4188.416 | 3899.2678 | 975.9375 | 0.00038302 | 74 | 11.843 | 4.1884 | 3.8993 | 0.97594 | 0.00038302
| 346.15 | 1200000 | 4187.7051 | 3904.4258 | 976.5267 | 0.00038813 | 73 | 11.843 | 4.1877 | 3.9044 | 0.97653 | 0.00038813
| 345.15 | 1200000 | 4187.0142 | 3909.5828 | 977.1105 | 0.00039336 | 72 | 11.843 | 4.187 | 3.9096 | 0.97711 | 0.00039336
| 344.15 | 1200000 | 4186.3438 | 3914.7375 | 977.6891 | 0.0003987 | 71 | 11.843 | 4.1863 | 3.9147 | 0.97769 | 0.0003987
| 343.15 | 1200000 | 4185.6938 | 3919.8901 | 978.2623 | 0.00040417 | 70 | 11.843 | 4.1857 | 3.9199 | 0.97826 | 0.00040417
| 342.15 | 1200000 | 4185.0645 | 3925.0396 | 978.83 | 0.00040977 | 69 | 11.843 | 4.1851 | 3.925 | 0.97883 | 0.00040977
| 341.15 | 1200000 | 4184.4556 | 3930.1853 | 979.3923 | 0.0004155 | 68 | 11.843 | 4.1845 | 3.9302 | 0.97939 | 0.0004155
| 340.15 | 1200000 | 4183.8672 | 3935.3267 | 979.9492 | 0.00042137 | 67 | 11.843 | 4.1839 | 3.9353 | 0.97995 | 0.00042137
| 339.15 | 1200000 | 4183.2988 | 3940.4631 | 980.5004 | 0.00042738 | 66 | 11.843 | 4.1833 | 3.9405 | 0.9805 | 0.00042738
| 338.15 | 1200000 | 4182.7515 | 3945.5938 | 981.0461 | 0.00043353 | 65 | 11.843 | 4.1828 | 3.9456 | 0.98105 | 0.00043353
| 337.15 | 1200000 | 4182.2246 | 3950.718 | 981.5862 | 0.00043983 | 64 | 11.843 | 4.1822 | 3.9507 | 0.98159 | 0.00043983
| 336.15 | 1200000 | 4181.7178 | 3955.8352 | 982.1205 | 0.00044629 | 63 | 11.843 | 4.1817 | 3.9558 | 0.98212 | 0.00044629
| 335.15 | 1200000 | 4181.2319 | 3960.9443 | 982.6492 | 0.00045291 | 62 | 11.843 | 4.1812 | 3.9609 | 0.98265 | 0.00045291
| 334.15 | 1200000 | 4180.7666 | 3966.0447 | 983.172 | 0.00045969 | 61 | 11.843 | 4.1808 | 3.966 | 0.98317 | 0.00045969
| 333.15 | 1200000 | 4180.3218 | 3971.1355 | 983.689 | 0.00046665 | 60 | 11.843 | 4.1803 | 3.9711 | 0.98369 | 0.00046665
| 332.15 | 1200000 | 4179.8979 | 3976.2161 | 984.2001 | 0.00047378 | 59 | 11.843 | 4.1799 | 3.9762 | 0.9842 | 0.00047378
| 331.15 | 1200000 | 4179.4946 | 3981.2849 | 984.7053 | 0.00048109 | 58 | 11.843 | 4.1795 | 3.9813 | 0.98471 | 0.00048109
| 330.15 | 1200000 | 4179.1118 | 3986.3418 | 985.2044 | 0.0004886 | 57 | 11.843 | 4.1791 | 3.9863 | 0.9852 | 0.0004886
| 329.15 | 1200000 | 4178.75 | 3991.3853 | 985.6974 | 0.0004963 | 56 | 11.843 | 4.1787 | 3.9914 | 0.9857 | 0.0004963
| 328.15 | 1200000 | 4178.4092 | 3996.4146 | 986.1844 | 0.0005042 | 55 | 11.843 | 4.1784 | 3.9964 | 0.98618 | 0.0005042
| 327.15 | 1200000 | 4178.0889 | 4001.4287 | 986.6652 | 0.00051232 | 54 | 11.843 | 4.1781 | 4.0014 | 0.98667 | 0.00051232
| 326.15 | 1200000 | 4177.7896 | 4006.4268 | 987.1396 | 0.00052065 | 53 | 11.843 | 4.1778 | 4.0064 | 0.98714 | 0.00052065
| 325.15 | 1200000 | 4177.5112 | 4011.4072 | 987.6078 | 0.00052921 | 52 | 11.843 | 4.1775 | 4.0114 | 0.98761 | 0.00052921
| 324.15 | 1200000 | 4177.2544 | 4016.3694 | 988.0695 | 0.00053801 | 51 | 11.843 | 4.1773 | 4.0164 | 0.98807 | 0.00053801
| 323.15 | 1200000 | 4177.0186 | 4021.3118 | 988.5248 | 0.00054704 | 50 | 11.843 | 4.177 | 4.0213 | 0.98852 | 0.00054704
| 322.15 | 1200000 | 4176.8037 | 4026.2334 | 988.9735 | 0.00055633 | 49 | 11.843 | 4.1768 | 4.0262 | 0.98897 | 0.00055633
| 321.15 | 1200000 | 4176.6104 | 4031.1333 | 989.4156 | 0.00056588 | 48 | 11.843 | 4.1766 | 4.0311 | 0.98942 | 0.00056588
| 320.15 | 1200000 | 4176.4385 | 4036.0098 | 989.8511 | 0.00057571 | 47 | 11.843 | 4.1764 | 4.036 | 0.98985 | 0.00057571
| 319.15 | 1200000 | 4176.2886 | 4040.8616 | 990.2797 | 0.00058581 | 46 | 11.843 | 4.1763 | 4.0409 | 0.99028 | 0.00058581
| 318.15 | 1200000 | 4176.1602 | 4045.6877 | 990.7015 | 0.00059622 | 45 | 11.843 | 4.1762 | 4.0457 | 0.9907 | 0.00059622
| 317.15 | 1200000 | 4176.0537 | 4050.4868 | 991.1163 | 0.00060692 | 44 | 11.843 | 4.1761 | 4.0505 | 0.99112 | 0.00060692
| 316.15 | 1200000 | 4175.9692 | 4055.2573 | 991.5242 | 0.00061795 | 43 | 11.843 | 4.176 | 4.0553 | 0.99152 | 0.00061795
| 315.15 | 1200000 | 4175.9077 | 4059.9978 | 991.9249 | 0.0006293 | 42 | 11.843 | 4.1759 | 4.06 | 0.99192 | 0.0006293
| 314.15 | 1200000 | 4175.8682 | 4064.7068 | 992.3183 | 0.00064101 | 41 | 11.843 | 4.1759 | 4.0647 | 0.99232 | 0.00064101
| 313.15 | 1200000 | 4175.8521 | 4069.3831 | 992.7045 | 0.00065307 | 40 | 11.843 | 4.1759 | 4.0694 | 0.9927 | 0.00065307
| 312.15 | 1200000 | 4175.8589 | 4074.0247 | 993.0832 | 0.0006655 | 39 | 11.843 | 4.1759 | 4.074 | 0.99308 | 0.0006655
| 311.15 | 1200000 | 4175.8896 | 4078.6306 | 993.4545 | 0.00067833 | 38 | 11.843 | 4.1759 | 4.0786 | 0.99345 | 0.00067833
| 310.15 | 1200000 | 4175.9443 | 4083.199 | 993.8181 | 0.00069156 | 37 | 11.843 | 4.1759 | 4.0832 | 0.99382 | 0.00069156
| 309.15 | 1200000 | 4176.0239 | 4087.7283 | 994.174 | 0.00070522 | 36 | 11.843 | 4.176 | 4.0877 | 0.99417 | 0.00070522
| 308.15 | 1200000 | 4176.1279 | 4092.2168 | 994.522 | 0.00071932 | 35 | 11.843 | 4.1761 | 4.0922 | 0.99452 | 0.00071932
| 307.15 | 1200000 | 4176.2583 | 4096.6631 | 994.862 | 0.00073389 | 34 | 11.843 | 4.1763 | 4.0967 | 0.99486 | 0.00073389
| 306.15 | 1200000 | 4176.4146 | 4101.0654 | 995.194 | 0.00074894 | 33 | 11.843 | 4.1764 | 4.1011 | 0.99519 | 0.00074894
| 305.15 | 1200000 | 4176.5981 | 4105.4224 | 995.5178 | 0.0007645 | 32 | 11.843 | 4.1766 | 4.1054 | 0.99552 | 0.0007645
| 304.15 | 1200000 | 4176.8101 | 4109.7314 | 995.8331 | 0.00078059 | 31 | 11.843 | 4.1768 | 4.1097 | 0.99583 | 0.00078059
| 303.15 | 1200000 | 4177.0508 | 4113.9917 | 996.1401 | 0.00079724 | 30 | 11.843 | 4.1771 | 4.114 | 0.99614 | 0.00079724
| 302.15 | 1200000 | 4177.3218 | 4118.2012 | 996.4384 | 0.00081447 | 29 | 11.843 | 4.1773 | 4.1182 | 0.99644 | 0.00081447
| 301.15 | 1200000 | 4177.624 | 4122.3584 | 996.7278 | 0.00083232 | 28 | 11.843 | 4.1776 | 4.1224 | 0.99673 | 0.00083232
| 300.15 | 1200000 | 4177.9595 | 4126.4614 | 997.0084 | 0.0008508 | 27 | 11.843 | 4.178 | 4.1265 | 0.99701 | 0.0008508
| 299.15 | 1200000 | 4178.3291 | 4130.5083 | 997.2799 | 0.00086996 | 26 | 11.843 | 4.1783 | 4.1305 | 0.99728 | 0.00086996
| 298.15 | 1200000 | 4178.7349 | 4134.498 | 997.5422 | 0.00088983 | 25 | 11.843 | 4.1787 | 4.1345 | 0.99754 | 0.00088983
| 297.15 | 1200000 | 4179.1792 | 4138.4282 | 997.795 | 0.00091044 | 24 | 11.843 | 4.1792 | 4.1384 | 0.99779 | 0.00091044
| 296.15 | 1200000 | 4179.6641 | 4142.2974 | 998.0381 | 0.00093183 | 23 | 11.843 | 4.1797 | 4.1423 | 0.99804 | 0.00093183
| 295.15 | 1200000 | 4180.1914 | 4146.1045 | 998.2715 | 0.00095405 | 22 | 11.843 | 4.1802 | 4.1461 | 0.99827 | 0.00095405
| 294.15 | 1200000 | 4180.7651 | 4149.8472 | 998.4949 | 0.00097714 | 21 | 11.843 | 4.1808 | 4.1498 | 0.99849 | 0.00097714
| 293.15 | 1200000 | 4181.3872 | 4153.5244 | 998.7081 | 0.0010011 | 20 | 11.843 | 4.1814 | 4.1535 | 0.99871 | 0.0010011
| 292.15 | 1200000 | 4182.0615 | 4157.1343 | 998.9109 | 0.0010261 | 19 | 11.843 | 4.1821 | 4.1571 | 0.99891 | 0.0010261
| 291.15 | 1200000 | 4182.7925 | 4160.6758 | 999.103 | 0.0010521 | 18 | 11.843 | 4.1828 | 4.1607 | 0.9991 | 0.0010521
| 290.15 | 1200000 | 4183.584 | 4164.1475 | 999.2842 | 0.0010792 | 17 | 11.843 | 4.1836 | 4.1641 | 0.99928 | 0.0010792
| 289.15 | 1200000 | 4184.4409 | 4167.5479 | 999.4543 | 0.0011074 | 16 | 11.843 | 4.1844 | 4.1675 | 0.99945 | 0.0011074
| 288.15 | 1200000 | 4185.3687 | 4170.876 | 999.613 | 0.0011368 | 15 | 11.843 | 4.1854 | 4.1709 | 0.99961 | 0.0011368
| 287.15 | 1200000 | 4186.373 | 4174.1313 | 999.7601 | 0.0011675 | 14 | 11.843 | 4.1864 | 4.1741 | 0.99976 | 0.0011675
| 286.15 | 1200000 | 4187.4604 | 4177.312 | 999.8953 | 0.0011995 | 13 | 11.843 | 4.1875 | 4.1773 | 0.9999 | 0.0011995
| 285.15 | 1200000 | 4188.6392 | 4180.4175 | 1000.0181 | 0.001233 | 12 | 11.843 | 4.1886 | 4.1804 | 1 | 0.001233
| 284.15 | 1200000 | 4189.9165 | 4183.4473 | 1000.1284 | 0.001268 | 11 | 11.843 | 4.1899 | 4.1834 | 1.0001 | 0.001268
| 283.15 | 1200000 | 4191.3022 | 4186.4014 | 1000.2258 | 0.0013047 | 10 | 11.843 | 4.1913 | 4.1864 | 1.0002 | 0.0013047
| 282.15 | 1200000 | 4192.8057 | 4189.2788 | 1000.31 | 0.0013431 | 9 | 11.843 | 4.1928 | 4.1893 | 1.0003 | 0.0013431
| 281.15 | 1200000 | 4194.439 | 4192.0801 | 1000.3806 | 0.0013833 | 8 | 11.843 | 4.1944 | 4.1921 | 1.0004 | 0.0013833
| 280.15 | 1200000 | 4196.2139 | 4194.8047 | 1000.4371 | 0.0014255 | 7 | 11.843 | 4.1962 | 4.1948 | 1.0004 | 0.0014255
| 279.15 | 1200000 | 4198.144 | 4197.4531 | 1000.4792 | 0.0014698 | 6 | 11.843 | 4.1981 | 4.1975 | 1.0005 | 0.0014698
| 278.15 | 1200000 | 4200.2456 | 4200.0264 | 1000.5064 | 0.0015163 | 5 | 11.843 | 4.2002 | 4.2 | 1.0005 | 0.0015163
| 277.15 | 1200000 | 4202.5347 | 4202.5249 | 1000.5184 | 0.0015653 | 4 | 11.843 | 4.2025 | 4.2025 | 1.0005 | 0.0015653
| 276.15 | 1200000 | 4205.0298 | 4204.9502 | 1000.5145 | 0.0016168 | 3 | 11.843 | 4.205 | 4.205 | 1.0005 | 0.0016168
| 275.15 | 1200000 | 4207.752 | 4207.3032 | 1000.4943 | 0.0016711 | 2 | 11.843 | 4.2078 | 4.2073 | 1.0005 | 0.0016711
| 274.15 | 1200000 | 4210.7246 | 4209.5864 | 1000.4572 | 0.0017283 | 0.99999 | 11.843 | 4.2107 | 4.2096 | 1.0005 | 0.0017283
| 273.15 | 1200000 | 4213.9722 | 4211.8008 | 1000.4025 | 0.0017888 | -6.1035e-06 | 11.843 | 4.214 | 4.2118 | 1.0004 | 0.0017888
| 473.15 | 1100000 | 2500.8567 | 1792.0363 | 5.376 | 1.5862e-05 | 200 | 10.8561 | 2.5009 | 1.792 | 0.005376 | 1.5862e-05
| 472.15 | 1100000 | 2511.1479 | 1798.0508 | 5.3912 | 1.5818e-05 | 199 | 10.8561 | 2.5111 | 1.7981 | 0.0053912 | 1.5818e-05
| 471.15 | 1100000 | 2521.9375 | 1804.3969 | 5.4065 | 1.5775e-05 | 198 | 10.8561 | 2.5219 | 1.8044 | 0.0054065 | 1.5775e-05
| 470.15 | 1100000 | 2533.2747 | 1811.1091 | 5.4219 | 1.5731e-05 | 197 | 10.8561 | 2.5333 | 1.8111 | 0.0054219 | 1.5731e-05
| 469.15 | 1100000 | 2545.2153 | 1818.2267 | 5.4375 | 1.5687e-05 | 196 | 10.8561 | 2.5452 | 1.8182 | 0.0054375 | 1.5687e-05
| 468.15 | 1100000 | 2557.8225 | 1825.7939 | 5.4532 | 1.5644e-05 | 195 | 10.8561 | 2.5578 | 1.8258 | 0.0054532 | 1.5644e-05
| 467.15 | 1100000 | 2571.1677 | 1833.861 | 5.469 | 1.56e-05 | 194 | 10.8561 | 2.5712 | 1.8339 | 0.005469 | 1.56e-05
| 466.15 | 1100000 | 2585.3313 | 1842.4846 | 5.4851 | 1.5556e-05 | 193 | 10.8561 | 2.5853 | 1.8425 | 0.0054851 | 1.5556e-05
| 465.15 | 1100000 | 2600.4053 | 1851.7291 | 5.5012 | 1.5513e-05 | 192 | 10.8561 | 2.6004 | 1.8517 | 0.0055012 | 1.5513e-05
| 464.15 | 1100000 | 2616.4934 | 1861.6674 | 5.5176 | 1.5469e-05 | 191 | 10.8561 | 2.6165 | 1.8617 | 0.0055176 | 1.5469e-05
| 463.15 | 1100000 | 2633.7139 | 1872.3818 | 5.5341 | 1.5425e-05 | 190 | 10.8561 | 2.6337 | 1.8724 | 0.0055341 | 1.5425e-05
| 462.15 | 1100000 | 2652.2007 | 1883.9662 | 5.5508 | 1.5382e-05 | 189 | 10.8561 | 2.6522 | 1.884 | 0.0055508 | 1.5382e-05
| 461.15 | 1100000 | 2672.1062 | 1896.5264 | 5.5676 | 1.5338e-05 | 188 | 10.8561 | 2.6721 | 1.8965 | 0.0055676 | 1.5338e-05
| 460.15 | 1100000 | 2693.6033 | 1910.1827 | 5.5847 | 1.5294e-05 | 187 | 10.8561 | 2.6936 | 1.9102 | 0.0055847 | 1.5294e-05
| 459.15 | 1100000 | 2716.8892 | 1925.0714 | 5.6019 | 1.525e-05 | 186 | 10.8561 | 2.7169 | 1.9251 | 0.0056019 | 1.525e-05
| 458.15 | 1100000 | 2742.1875 | 1941.347 | 5.6194 | 1.5206e-05 | 185 | 10.8561 | 2.7422 | 1.9413 | 0.0056194 | 1.5206e-05
| 457.15 | 1100000 | 4421.3716 | 3379.9043 | 882.6959 | 0.00014668 | 184 | 10.8561 | 4.4214 | 3.3799 | 0.8827 | 0.00014668
| 456.15 | 1100000 | 4417.2197 | 3383.9543 | 883.7974 | 0.00014754 | 183 | 10.8561 | 4.4172 | 3.384 | 0.8838 | 0.00014754
| 455.15 | 1100000 | 4413.1265 | 3388.0203 | 884.8937 | 0.0001484 | 182 | 10.8561 | 4.4131 | 3.388 | 0.88489 | 0.0001484
| 454.15 | 1100000 | 4409.0913 | 3392.1018 | 885.9847 | 0.00014928 | 181 | 10.8561 | 4.4091 | 3.3921 | 0.88598 | 0.00014928
| 453.15 | 1100000 | 4405.1133 | 3396.199 | 887.0706 | 0.00015016 | 180 | 10.8561 | 4.4051 | 3.3962 | 0.88707 | 0.00015016
| 452.15 | 1100000 | 4401.1909 | 3400.3118 | 888.1512 | 0.00015106 | 179 | 10.8561 | 4.4012 | 3.4003 | 0.88815 | 0.00015106
| 451.15 | 1100000 | 4397.3237 | 3404.4399 | 889.2267 | 0.00015197 | 178 | 10.8561 | 4.3973 | 3.4044 | 0.88923 | 0.00015197
| 450.15 | 1100000 | 4393.5107 | 3408.5835 | 890.2971 | 0.00015288 | 177 | 10.8561 | 4.3935 | 3.4086 | 0.8903 | 0.00015288
| 449.15 | 1100000 | 4389.7515 | 3412.7419 | 891.3624 | 0.00015381 | 176 | 10.8561 | 4.3898 | 3.4127 | 0.89136 | 0.00015381
| 448.15 | 1100000 | 4386.0439 | 3416.9158 | 892.4226 | 0.00015475 | 175 | 10.8561 | 4.386 | 3.4169 | 0.89242 | 0.00015475
| 447.15 | 1100000 | 4382.3887 | 3421.1045 | 893.4778 | 0.0001557 | 174 | 10.8561 | 4.3824 | 3.4211 | 0.89348 | 0.0001557
| 446.15 | 1100000 | 4378.7837 | 3425.3081 | 894.5281 | 0.00015667 | 173 | 10.8561 | 4.3788 | 3.4253 | 0.89453 | 0.00015667
| 445.15 | 1100000 | 4375.229 | 3429.5264 | 895.5733 | 0.00015764 | 172 | 10.8561 | 4.3752 | 3.4295 | 0.89557 | 0.00015764
| 444.15 | 1100000 | 4371.7236 | 3433.7595 | 896.6136 | 0.00015863 | 171 | 10.8561 | 4.3717 | 3.4338 | 0.89661 | 0.00015863
| 443.15 | 1100000 | 4368.2666 | 3438.0071 | 897.649 | 0.00015963 | 170 | 10.8561 | 4.3683 | 3.438 | 0.89765 | 0.00015963
| 442.15 | 1100000 | 4364.8569 | 3442.269 | 898.6796 | 0.00016064 | 169 | 10.8561 | 4.3649 | 3.4423 | 0.89868 | 0.00016064
| 441.15 | 1100000 | 4361.4946 | 3446.5457 | 899.7053 | 0.00016167 | 168 | 10.8561 | 4.3615 | 3.4465 | 0.89971 | 0.00016167
| 440.15 | 1100000 | 4358.1787 | 3450.8362 | 900.7261 | 0.00016271 | 167 | 10.8561 | 4.3582 | 3.4508 | 0.90073 | 0.00016271
| 439.15 | 1100000 | 4354.9082 | 3455.1411 | 901.7421 | 0.00016376 | 166 | 10.8561 | 4.3549 | 3.4551 | 0.90174 | 0.00016376
| 438.15 | 1100000 | 4351.6821 | 3459.46 | 902.7534 | 0.00016482 | 165 | 10.8561 | 4.3517 | 3.4595 | 0.90275 | 0.00016482
| 437.15 | 1100000 | 4348.5005 | 3463.7927 | 903.7598 | 0.0001659 | 164 | 10.8561 | 4.3485 | 3.4638 | 0.90376 | 0.0001659
| 436.15 | 1100000 | 4345.3623 | 3468.1396 | 904.7615 | 0.00016699 | 163 | 10.8561 | 4.3454 | 3.4681 | 0.90476 | 0.00016699
| 435.15 | 1100000 | 4342.2671 | 3472.5 | 905.7585 | 0.0001681 | 162 | 10.8561 | 4.3423 | 3.4725 | 0.90576 | 0.0001681
| 434.15 | 1100000 | 4339.2144 | 3476.8743 | 906.7509 | 0.00016922 | 161 | 10.8561 | 4.3392 | 3.4769 | 0.90675 | 0.00016922
| 433.15 | 1100000 | 4336.2026 | 3481.262 | 907.7385 | 0.00017036 | 160 | 10.8561 | 4.3362 | 3.4813 | 0.90774 | 0.00017036
| 432.15 | 1100000 | 4333.2324 | 3485.6633 | 908.7214 | 0.00017151 | 159 | 10.8561 | 4.3332 | 3.4857 | 0.90872 | 0.00017151
| 431.15 | 1100000 | 4330.3022 | 3490.0779 | 909.6997 | 0.00017268 | 158 | 10.8561 | 4.3303 | 3.4901 | 0.9097 | 0.00017268
| 430.15 | 1100000 | 4327.4116 | 3494.5059 | 910.6734 | 0.00017386 | 157 | 10.8561 | 4.3274 | 3.4945 | 0.91067 | 0.00017386
| 429.15 | 1100000 | 4324.5605 | 3498.947 | 911.6425 | 0.00017506 | 156 | 10.8561 | 4.3246 | 3.4989 | 0.91164 | 0.00017506
| 428.15 | 1100000 | 4321.7485 | 3503.4016 | 912.6069 | 0.00017628 | 155 | 10.8561 | 4.3217 | 3.5034 | 0.91261 | 0.00017628
| 427.15 | 1100000 | 4318.9741 | 3507.8689 | 913.5668 | 0.00017751 | 154 | 10.8561 | 4.319 | 3.5079 | 0.91357 | 0.00017751
| 426.15 | 1100000 | 4316.2373 | 3512.3494 | 914.5222 | 0.00017876 | 153 | 10.8561 | 4.3162 | 3.5123 | 0.91452 | 0.00017876
| 425.15 | 1100000 | 4313.5376 | 3516.8425 | 915.473 | 0.00018003 | 152 | 10.8561 | 4.3135 | 3.5168 | 0.91547 | 0.00018003
| 424.15 | 1100000 | 4310.8745 | 3521.3486 | 916.4192 | 0.00018132 | 151 | 10.8561 | 4.3109 | 3.5213 | 0.91642 | 0.00018132
| 423.15 | 1100000 | 4308.2476 | 3525.8674 | 917.361 | 0.00018262 | 150 | 10.8561 | 4.3082 | 3.5259 | 0.91736 | 0.00018262
| 422.15 | 1100000 | 4305.6558 | 3530.3987 | 918.2982 | 0.00018394 | 149 | 10.8561 | 4.3057 | 3.5304 | 0.9183 | 0.00018394
| 421.15 | 1100000 | 4303.0991 | 3534.9426 | 919.2309 | 0.00018528 | 148 | 10.8561 | 4.3031 | 3.5349 | 0.91923 | 0.00018528
| 420.15 | 1100000 | 4300.5771 | 3539.499 | 920.1592 | 0.00018664 | 147 | 10.8561 | 4.3006 | 3.5395 | 0.92016 | 0.00018664
| 419.15 | 1100000 | 4298.0894 | 3544.0679 | 921.0829 | 0.00018802 | 146 | 10.8561 | 4.2981 | 3.5441 | 0.92108 | 0.00018802
| 418.15 | 1100000 | 4295.6353 | 3548.6489 | 922.0023 | 0.00018942 | 145 | 10.8561 | 4.2956 | 3.5486 | 0.922 | 0.00018942
| 417.15 | 1100000 | 4293.2139 | 3553.2424 | 922.9172 | 0.00019084 | 144 | 10.8561 | 4.2932 | 3.5532 | 0.92292 | 0.00019084
| 416.15 | 1100000 | 4290.8257 | 3557.8479 | 923.8276 | 0.00019228 | 143 | 10.8561 | 4.2908 | 3.5578 | 0.92383 | 0.00019228
| 415.15 | 1100000 | 4288.4697 | 3562.4653 | 924.7336 | 0.00019374 | 142 | 10.8561 | 4.2885 | 3.5625 | 0.92473 | 0.00019374
| 414.15 | 1100000 | 4286.146 | 3567.095 | 925.6352 | 0.00019522 | 141 | 10.8561 | 4.2861 | 3.5671 | 0.92564 | 0.00019522
| 413.15 | 1100000 | 4283.8535 | 3571.7366 | 926.5323 | 0.00019673 | 140 | 10.8561 | 4.2839 | 3.5717 | 0.92653 | 0.00019673
| 412.15 | 1100000 | 4281.5918 | 3576.3899 | 927.4252 | 0.00019826 | 139 | 10.8561 | 4.2816 | 3.5764 | 0.92743 | 0.00019826
| 411.15 | 1100000 | 4279.3613 | 3581.0549 | 928.3135 | 0.00019981 | 138 | 10.8561 | 4.2794 | 3.5811 | 0.92831 | 0.00019981
| 410.15 | 1100000 | 4277.1611 | 3585.7317 | 929.1974 | 0.00020138 | 137 | 10.8561 | 4.2772 | 3.5857 | 0.9292 | 0.00020138
| 409.15 | 1100000 | 4274.9907 | 3590.4202 | 930.0771 | 0.00020298 | 136 | 10.8561 | 4.275 | 3.5904 | 0.93008 | 0.00020298
| 408.15 | 1100000 | 4272.8501 | 3595.1201 | 930.9523 | 0.00020461 | 135 | 10.8561 | 4.2729 | 3.5951 | 0.93095 | 0.00020461
| 407.15 | 1100000 | 4270.7388 | 3599.8315 | 931.8231 | 0.00020625 | 134 | 10.8561 | 4.2707 | 3.5998 | 0.93182 | 0.00020625
| 406.15 | 1100000 | 4268.6562 | 3604.5544 | 932.6895 | 0.00020793 | 133 | 10.8561 | 4.2687 | 3.6046 | 0.93269 | 0.00020793
| 405.15 | 1100000 | 4266.6021 | 3609.2886 | 933.5516 | 0.00020963 | 132 | 10.8561 | 4.2666 | 3.6093 | 0.93355 | 0.00020963
| 404.15 | 1100000 | 4264.5762 | 3614.0339 | 934.4093 | 0.00021136 | 131 | 10.8561 | 4.2646 | 3.614 | 0.93441 | 0.00021136
| 403.15 | 1100000 | 4262.5786 | 3618.7905 | 935.2626 | 0.00021311 | 130 | 10.8561 | 4.2626 | 3.6188 | 0.93526 | 0.00021311
| 402.15 | 1100000 | 4260.6084 | 3623.5581 | 936.1116 | 0.00021489 | 129 | 10.8561 | 4.2606 | 3.6236 | 0.93611 | 0.00021489
| 401.15 | 1100000 | 4258.6655 | 3628.3367 | 936.9562 | 0.0002167 | 128 | 10.8561 | 4.2587 | 3.6283 | 0.93696 | 0.0002167
| 400.15 | 1100000 | 4256.7495 | 3633.1262 | 937.7965 | 0.00021854 | 127 | 10.8561 | 4.2567 | 3.6331 | 0.9378 | 0.00021854
| 399.15 | 1100000 | 4254.8604 | 3637.9265 | 938.6324 | 0.00022041 | 126 | 10.8561 | 4.2549 | 3.6379 | 0.93863 | 0.00022041
| 398.15 | 1100000 | 4252.998 | 3642.7378 | 939.4639 | 0.00022231 | 125 | 10.8561 | 4.253 | 3.6427 | 0.93946 | 0.00022231
| 397.15 | 1100000 | 4251.1611 | 3647.5596 | 940.2911 | 0.00022424 | 124 | 10.8561 | 4.2512 | 3.6476 | 0.94029 | 0.00022424
| 396.15 | 1100000 | 4249.3506 | 3652.3921 | 941.1138 | 0.0002262 | 123 | 10.8561 | 4.2494 | 3.6524 | 0.94111 | 0.0002262
| 395.15 | 1100000 | 4247.5659 | 3657.2351 | 941.9323 | 0.0002282 | 122 | 10.8561 | 4.2476 | 3.6572 | 0.94193 | 0.0002282
| 394.15 | 1100000 | 4245.8062 | 3662.0884 | 942.7463 | 0.00023023 | 121 | 10.8561 | 4.2458 | 3.6621 | 0.94275 | 0.00023023
| 393.15 | 1100000 | 4244.0718 | 3666.9521 | 943.556 | 0.00023229 | 120 | 10.8561 | 4.2441 | 3.667 | 0.94356 | 0.00023229
| 392.15 | 1100000 | 4242.3618 | 3671.8262 | 944.3614 | 0.00023438 | 119 | 10.8561 | 4.2424 | 3.6718 | 0.94436 | 0.00023438
| 391.15 | 1100000 | 4240.6772 | 3676.7102 | 945.1623 | 0.00023652 | 118 | 10.8561 | 4.2407 | 3.6767 | 0.94516 | 0.00023652
| 390.15 | 1100000 | 4239.0166 | 3681.6045 | 945.9589 | 0.00023869 | 117 | 10.8561 | 4.239 | 3.6816 | 0.94596 | 0.00023869
| 389.15 | 1100000 | 4237.3804 | 3686.5085 | 946.751 | 0.00024089 | 116 | 10.8561 | 4.2374 | 3.6865 | 0.94675 | 0.00024089
| 388.15 | 1100000 | 4235.7686 | 3691.4226 | 947.5388 | 0.00024313 | 115 | 10.8561 | 4.2358 | 3.6914 | 0.94754 | 0.00024313
| 387.15 | 1100000 | 4234.1802 | 3696.3464 | 948.3221 | 0.00024542 | 114 | 10.8561 | 4.2342 | 3.6963 | 0.94832 | 0.00024542
| 386.15 | 1100000 | 4232.6152 | 3701.28 | 949.1011 | 0.00024774 | 113 | 10.8561 | 4.2326 | 3.7013 | 0.9491 | 0.00024774
| 385.15 | 1100000 | 4231.0742 | 3706.2229 | 949.8756 | 0.0002501 | 112 | 10.8561 | 4.2311 | 3.7062 | 0.94988 | 0.0002501
| 384.15 | 1100000 | 4229.5562 | 3711.1753 | 950.6457 | 0.00025251 | 111 | 10.8561 | 4.2296 | 3.7112 | 0.95065 | 0.00025251
| 383.15 | 1100000 | 4228.061 | 3716.137 | 951.4114 | 0.00025495 | 110 | 10.8561 | 4.2281 | 3.7161 | 0.95141 | 0.00025495
| 382.15 | 1100000 | 4226.5894 | 3721.1079 | 952.1726 | 0.00025744 | 109 | 10.8561 | 4.2266 | 3.7211 | 0.95217 | 0.00025744
| 381.15 | 1100000 | 4225.1401 | 3726.0879 | 952.9294 | 0.00025998 | 108 | 10.8561 | 4.2251 | 3.7261 | 0.95293 | 0.00025998
| 380.15 | 1100000 | 4223.7134 | 3731.0769 | 953.6817 | 0.00026256 | 107 | 10.8561 | 4.2237 | 3.7311 | 0.95368 | 0.00026256
| 379.15 | 1100000 | 4222.3091 | 3736.0747 | 954.4295 | 0.00026519 | 106 | 10.8561 | 4.2223 | 3.7361 | 0.95443 | 0.00026519
| 378.15 | 1100000 | 4220.9272 | 3741.0811 | 955.1729 | 0.00026787 | 105 | 10.8561 | 4.2209 | 3.7411 | 0.95517 | 0.00026787
| 377.15 | 1100000 | 4219.5674 | 3746.0959 | 955.9117 | 0.00027059 | 104 | 10.8561 | 4.2196 | 3.7461 | 0.95591 | 0.00027059
| 376.15 | 1100000 | 4218.23 | 3751.1191 | 956.646 | 0.00027337 | 103 | 10.8561 | 4.2182 | 3.7511 | 0.95665 | 0.00027337
| 375.15 | 1100000 | 4216.9141 | 3756.1506 | 957.3758 | 0.0002762 | 102 | 10.8561 | 4.2169 | 3.7562 | 0.95738 | 0.0002762
| 374.15 | 1100000 | 4215.6201 | 3761.1902 | 958.1011 | 0.00027908 | 101 | 10.8561 | 4.2156 | 3.7612 | 0.9581 | 0.00027908
| 373.15 | 1100000 | 4214.3477 | 3766.2375 | 958.8218 | 0.00028201 | 100 | 10.8561 | 4.2143 | 3.7662 | 0.95882 | 0.00028201
| 372.15 | 1100000 | 4213.0972 | 3771.2927 | 959.5378 | 0.000285 | 99 | 10.8561 | 4.2131 | 3.7713 | 0.95954 | 0.000285
| 371.15 | 1100000 | 4211.8682 | 3776.3555 | 960.2494 | 0.00028805 | 98 | 10.8561 | 4.2119 | 3.7764 | 0.96025 | 0.00028805
| 370.15 | 1100000 | 4210.6602 | 3781.4253 | 960.9563 | 0.00029116 | 97 | 10.8561 | 4.2107 | 3.7814 | 0.96096 | 0.00029116
| 369.15 | 1100000 | 4209.4736 | 3786.5024 | 961.6586 | 0.00029432 | 96 | 10.8561 | 4.2095 | 3.7865 | 0.96166 | 0.00029432
| 368.15 | 1100000 | 4208.3081 | 3791.5862 | 962.3563 | 0.00029755 | 95 | 10.8561 | 4.2083 | 3.7916 | 0.96236 | 0.00029755
| 367.15 | 1100000 | 4207.1641 | 3796.677 | 963.0493 | 0.00030085 | 94 | 10.8561 | 4.2072 | 3.7967 | 0.96305 | 0.00030085
| 366.15 | 1100000 | 4206.041 | 3801.7742 | 963.7375 | 0.0003042 | 93 | 10.8561 | 4.206 | 3.8018 | 0.96374 | 0.0003042
| 365.15 | 1100000 | 4204.9385 | 3806.8774 | 964.4211 | 0.00030763 | 92 | 10.8561 | 4.2049 | 3.8069 | 0.96442 | 0.00030763
| 364.15 | 1100000 | 4203.8574 | 3811.9868 | 965.1 | 0.00031112 | 91 | 10.8561 | 4.2039 | 3.812 | 0.9651 | 0.00031112
| 363.15 | 1100000 | 4202.7969 | 3817.1018 | 965.7742 | 0.00031468 | 90 | 10.8561 | 4.2028 | 3.8171 | 0.96577 | 0.00031468
| 362.15 | 1100000 | 4201.7573 | 3822.2222 | 966.4435 | 0.00031831 | 89 | 10.8561 | 4.2018 | 3.8222 | 0.96644 | 0.00031831
| 361.15 | 1100000 | 4200.7383 | 3827.3479 | 967.1081 | 0.00032202 | 88 | 10.8561 | 4.2007 | 3.8273 | 0.96711 | 0.00032202
| 360.15 | 1100000 | 4199.7402 | 3832.4785 | 967.7678 | 0.00032581 | 87 | 10.8561 | 4.1997 | 3.8325 | 0.96777 | 0.00032581
| 359.15 | 1100000 | 4198.7627 | 3837.6135 | 968.4227 | 0.00032967 | 86 | 10.8561 | 4.1988 | 3.8376 | 0.96842 | 0.00032967
| 358.15 | 1100000 | 4197.8057 | 3842.7529 | 969.0728 | 0.00033361 | 85 | 10.8561 | 4.1978 | 3.8428 | 0.96907 | 0.00033361
| 357.15 | 1100000 | 4196.8696 | 3847.8962 | 969.7179 | 0.00033764 | 84 | 10.8561 | 4.1969 | 3.8479 | 0.96972 | 0.00033764
| 356.15 | 1100000 | 4195.9536 | 3853.0432 | 970.3581 | 0.00034175 | 83 | 10.8561 | 4.196 | 3.853 | 0.97036 | 0.00034175
| 355.15 | 1100000 | 4195.0586 | 3858.1934 | 970.9933 | 0.00034595 | 82 | 10.8561 | 4.1951 | 3.8582 | 0.97099 | 0.00034595
| 354.15 | 1100000 | 4194.1836 | 3863.3464 | 971.6236 | 0.00035024 | 81 | 10.8561 | 4.1942 | 3.8633 | 0.97162 | 0.00035024
| 353.15 | 1100000 | 4193.3296 | 3868.5017 | 972.2489 | 0.00035462 | 80 | 10.8561 | 4.1933 | 3.8685 | 0.97225 | 0.00035462
| 352.15 | 1100000 | 4192.4956 | 3873.6592 | 972.8691 | 0.00035909 | 79 | 10.8561 | 4.1925 | 3.8737 | 0.97287 | 0.00035909
| 351.15 | 1100000 | 4191.6821 | 3878.8184 | 973.4843 | 0.00036367 | 78 | 10.8561 | 4.1917 | 3.8788 | 0.97348 | 0.00036367
| 350.15 | 1100000 | 4190.8896 | 3883.9788 | 974.0942 | 0.00036834 | 77 | 10.8561 | 4.1909 | 3.884 | 0.97409 | 0.00036834
| 349.15 | 1100000 | 4190.1172 | 3889.1396 | 974.6992 | 0.00037312 | 76 | 10.8561 | 4.1901 | 3.8891 | 0.9747 | 0.00037312
| 348.15 | 1100000 | 4189.3652 | 3894.301 | 975.2988 | 0.000378 | 75 | 10.8561 | 4.1894 | 3.8943 | 0.9753 | 0.000378
| 347.15 | 1100000 | 4188.6338 | 3899.4622 | 975.8933 | 0.000383 | 74 | 10.8561 | 4.1886 | 3.8995 | 0.97589 | 0.000383
| 346.15 | 1100000 | 4187.9224 | 3904.6223 | 976.4825 | 0.00038811 | 73 | 10.8561 | 4.1879 | 3.9046 | 0.97648 | 0.00038811
| 345.15 | 1100000 | 4187.2319 | 3909.7815 | 977.0665 | 0.00039333 | 72 | 10.8561 | 4.1872 | 3.9098 | 0.97707 | 0.00039333
| 344.15 | 1100000 | 4186.5615 | 3914.9385 | 977.6451 | 0.00039868 | 71 | 10.8561 | 4.1866 | 3.9149 | 0.97765 | 0.00039868
| 343.15 | 1100000 | 4185.9121 | 3920.0933 | 978.2183 | 0.00040415 | 70 | 10.8561 | 4.1859 | 3.9201 | 0.97822 | 0.00040415
| 342.15 | 1100000 | 4185.2827 | 3925.2449 | 978.7862 | 0.00040975 | 69 | 10.8561 | 4.1853 | 3.9252 | 0.97879 | 0.00040975
| 341.15 | 1100000 | 4184.6738 | 3930.3931 | 979.3486 | 0.00041548 | 68 | 10.8561 | 4.1847 | 3.9304 | 0.97935 | 0.00041548
| 340.15 | 1100000 | 4184.0854 | 3935.5369 | 979.9054 | 0.00042135 | 67 | 10.8561 | 4.1841 | 3.9355 | 0.97991 | 0.00042135
| 339.15 | 1100000 | 4183.5181 | 3940.6755 | 980.4567 | 0.00042735 | 66 | 10.8561 | 4.1835 | 3.9407 | 0.98046 | 0.00042735
| 338.15 | 1100000 | 4182.9707 | 3945.8086 | 981.0024 | 0.00043351 | 65 | 10.8561 | 4.183 | 3.9458 | 0.981 | 0.00043351
| 337.15 | 1100000 | 4182.4438 | 3950.9353 | 981.5425 | 0.00043981 | 64 | 10.8561 | 4.1824 | 3.9509 | 0.98154 | 0.00043981
| 336.15 | 1100000 | 4181.938 | 3956.0549 | 982.077 | 0.00044627 | 63 | 10.8561 | 4.1819 | 3.9561 | 0.98208 | 0.00044627
| 335.15 | 1100000 | 4181.4526 | 3961.1665 | 982.6057 | 0.00045289 | 62 | 10.8561 | 4.1815 | 3.9612 | 0.98261 | 0.00045289
| 334.15 | 1100000 | 4180.9878 | 3966.2693 | 983.1285 | 0.00045967 | 61 | 10.8561 | 4.181 | 3.9663 | 0.98313 | 0.00045967
| 333.15 | 1100000 | 4180.5435 | 3971.3625 | 983.6455 | 0.00046663 | 60 | 10.8561 | 4.1805 | 3.9714 | 0.98365 | 0.00046663
| 332.15 | 1100000 | 4180.1201 | 3976.4456 | 984.1567 | 0.00047376 | 59 | 10.8561 | 4.1801 | 3.9764 | 0.98416 | 0.00047376
| 331.15 | 1100000 | 4179.7173 | 3981.5171 | 984.6618 | 0.00048107 | 58 | 10.8561 | 4.1797 | 3.9815 | 0.98466 | 0.00048107
| 330.15 | 1100000 | 4179.3354 | 3986.5764 | 985.1609 | 0.00048858 | 57 | 10.8561 | 4.1793 | 3.9866 | 0.98516 | 0.00048858
| 329.15 | 1100000 | 4178.9741 | 3991.6226 | 985.6541 | 0.00049628 | 56 | 10.8561 | 4.179 | 3.9916 | 0.98565 | 0.00049628
| 328.15 | 1100000 | 4178.6343 | 3996.6545 | 986.141 | 0.00050418 | 55 | 10.8561 | 4.1786 | 3.9967 | 0.98614 | 0.00050418
| 327.15 | 1100000 | 4178.3149 | 4001.6714 | 986.6218 | 0.0005123 | 54 | 10.8561 | 4.1783 | 4.0017 | 0.98662 | 0.0005123
| 326.15 | 1100000 | 4178.0166 | 4006.6721 | 987.0963 | 0.00052063 | 53 | 10.8561 | 4.178 | 4.0067 | 0.9871 | 0.00052063
| 325.15 | 1100000 | 4177.7393 | 4011.6553 | 987.5644 | 0.00052919 | 52 | 10.8561 | 4.1777 | 4.0117 | 0.98756 | 0.00052919
| 324.15 | 1100000 | 4177.4834 | 4016.6201 | 988.0261 | 0.00053799 | 51 | 10.8561 | 4.1775 | 4.0166 | 0.98803 | 0.00053799
| 323.15 | 1100000 | 4177.2485 | 4021.5654 | 988.4814 | 0.00054703 | 50 | 10.8561 | 4.1772 | 4.0216 | 0.98848 | 0.00054703
| 322.15 | 1100000 | 4177.0352 | 4026.49 | 988.9301 | 0.00055632 | 49 | 10.8561 | 4.177 | 4.0265 | 0.98893 | 0.00055632
| 321.15 | 1100000 | 4176.8428 | 4031.3926 | 989.3722 | 0.00056587 | 48 | 10.8561 | 4.1768 | 4.0314 | 0.98937 | 0.00056587
| 320.15 | 1100000 | 4176.6724 | 4036.272 | 989.8076 | 0.00057569 | 47 | 10.8561 | 4.1767 | 4.0363 | 0.98981 | 0.00057569
| 319.15 | 1100000 | 4176.5234 | 4041.1267 | 990.2363 | 0.0005858 | 46 | 10.8561 | 4.1765 | 4.0411 | 0.99024 | 0.0005858
| 318.15 | 1100000 | 4176.3965 | 4045.9558 | 990.658 | 0.0005962 | 45 | 10.8561 | 4.1764 | 4.046 | 0.99066 | 0.0005962
| 317.15 | 1100000 | 4176.292 | 4050.7578 | 991.0728 | 0.00060691 | 44 | 10.8561 | 4.1763 | 4.0508 | 0.99107 | 0.00060691
| 316.15 | 1100000 | 4176.209 | 4055.5312 | 991.4806 | 0.00061794 | 43 | 10.8561 | 4.1762 | 4.0555 | 0.99148 | 0.00061794
| 315.15 | 1100000 | 4176.1489 | 4060.2747 | 991.8813 | 0.00062929 | 42 | 10.8561 | 4.1761 | 4.0603 | 0.99188 | 0.00062929
| 314.15 | 1100000 | 4176.1113 | 4064.9868 | 992.2747 | 0.000641 | 41 | 10.8561 | 4.1761 | 4.065 | 0.99227 | 0.000641
| 313.15 | 1100000 | 4176.0972 | 4069.6663 | 992.6608 | 0.00065306 | 40 | 10.8561 | 4.1761 | 4.0697 | 0.99266 | 0.00065306
| 312.15 | 1100000 | 4176.106 | 4074.311 | 993.0395 | 0.00066549 | 39 | 10.8561 | 4.1761 | 4.0743 | 0.99304 | 0.00066549
| 311.15 | 1100000 | 4176.1387 | 4078.9202 | 993.4107 | 0.00067832 | 38 | 10.8561 | 4.1761 | 4.0789 | 0.99341 | 0.00067832
| 310.15 | 1100000 | 4176.1958 | 4083.4917 | 993.7742 | 0.00069156 | 37 | 10.8561 | 4.1762 | 4.0835 | 0.99377 | 0.00069156
| 309.15 | 1100000 | 4176.2769 | 4088.0244 | 994.1301 | 0.00070522 | 36 | 10.8561 | 4.1763 | 4.088 | 0.99413 | 0.00070522
| 308.15 | 1100000 | 4176.3838 | 4092.5161 | 994.478 | 0.00071932 | 35 | 10.8561 | 4.1764 | 4.0925 | 0.99448 | 0.00071932
| 307.15 | 1100000 | 4176.5161 | 4096.9658 | 994.818 | 0.00073389 | 34 | 10.8561 | 4.1765 | 4.097 | 0.99482 | 0.00073389
| 306.15 | 1100000 | 4176.6753 | 4101.3716 | 995.1499 | 0.00074894 | 33 | 10.8561 | 4.1767 | 4.1014 | 0.99515 | 0.00074894
| 305.15 | 1100000 | 4176.8618 | 4105.7314 | 995.4736 | 0.00076451 | 32 | 10.8561 | 4.1769 | 4.1057 | 0.99547 | 0.00076451
| 304.15 | 1100000 | 4177.0762 | 4110.0444 | 995.7889 | 0.0007806 | 31 | 10.8561 | 4.1771 | 4.11 | 0.99579 | 0.0007806
| 303.15 | 1100000 | 4177.3198 | 4114.3081 | 996.0957 | 0.00079725 | 30 | 10.8561 | 4.1773 | 4.1143 | 0.9961 | 0.00079725
| 302.15 | 1100000 | 4177.5942 | 4118.5215 | 996.3939 | 0.00081448 | 29 | 10.8561 | 4.1776 | 4.1185 | 0.99639 | 0.00081448
| 301.15 | 1100000 | 4177.8999 | 4122.6821 | 996.6833 | 0.00083233 | 28 | 10.8561 | 4.1779 | 4.1227 | 0.99668 | 0.00083233
| 300.15 | 1100000 | 4178.2388 | 4126.7886 | 996.9637 | 0.00085082 | 27 | 10.8561 | 4.1782 | 4.1268 | 0.99696 | 0.00085082
| 299.15 | 1100000 | 4178.6118 | 4130.8394 | 997.2351 | 0.00086998 | 26 | 10.8561 | 4.1786 | 4.1308 | 0.99724 | 0.00086998
| 298.15 | 1100000 | 4179.022 | 4134.833 | 997.4973 | 0.00088985 | 25 | 10.8561 | 4.179 | 4.1348 | 0.9975 | 0.00088985
| 297.15 | 1100000 | 4179.4697 | 4138.7671 | 997.7499 | 0.00091046 | 24 | 10.8561 | 4.1795 | 4.1388 | 0.99775 | 0.00091046
| 296.15 | 1100000 | 4179.959 | 4142.6401 | 997.9929 | 0.00093186 | 23 | 10.8561 | 4.18 | 4.1426 | 0.99799 | 0.00093186
| 295.15 | 1100000 | 4180.4907 | 4146.4512 | 998.2262 | 0.00095408 | 22 | 10.8561 | 4.1805 | 4.1465 | 0.99823 | 0.00095408
| 294.15 | 1100000 | 4181.0688 | 4150.1982 | 998.4494 | 0.00097717 | 21 | 10.8561 | 4.1811 | 4.1502 | 0.99845 | 0.00097717
| 293.15 | 1100000 | 4181.6958 | 4153.8794 | 998.6625 | 0.0010012 | 20 | 10.8561 | 4.1817 | 4.1539 | 0.99866 | 0.0010012
| 292.15 | 1100000 | 4182.376 | 4157.4937 | 998.8651 | 0.0010262 | 19 | 10.8561 | 4.1824 | 4.1575 | 0.99887 | 0.0010262
| 291.15 | 1100000 | 4183.1123 | 4161.0396 | 999.057 | 0.0010521 | 18 | 10.8561 | 4.1831 | 4.161 | 0.99906 | 0.0010521
| 290.15 | 1100000 | 4183.9092 | 4164.5156 | 999.238 | 0.0010792 | 17 | 10.8561 | 4.1839 | 4.1645 | 0.99924 | 0.0010792
| 289.15 | 1100000 | 4184.772 | 4167.9209 | 999.408 | 0.0011074 | 16 | 10.8561 | 4.1848 | 4.1679 | 0.99941 | 0.0011074
| 288.15 | 1100000 | 4185.7061 | 4171.2534 | 999.5665 | 0.0011369 | 15 | 10.8561 | 4.1857 | 4.1713 | 0.99957 | 0.0011369
| 287.15 | 1100000 | 4186.7173 | 4174.5132 | 999.7134 | 0.0011676 | 14 | 10.8561 | 4.1867 | 4.1745 | 0.99971 | 0.0011676
| 286.15 | 1100000 | 4187.812 | 4177.6992 | 999.8483 | 0.0011996 | 13 | 10.8561 | 4.1878 | 4.1777 | 0.99985 | 0.0011996
| 285.15 | 1100000 | 4188.998 | 4180.8096 | 999.9709 | 0.0012331 | 12 | 10.8561 | 4.189 | 4.1808 | 0.99997 | 0.0012331
| 284.15 | 1100000 | 4190.2837 | 4183.8452 | 1000.081 | 0.0012681 | 11 | 10.8561 | 4.1903 | 4.1838 | 1.0001 | 0.0012681
| 283.15 | 1100000 | 4191.6777 | 4186.8042 | 1000.1782 | 0.0013048 | 10 | 10.8561 | 4.1917 | 4.1868 | 1.0002 | 0.0013048
| 282.15 | 1100000 | 4193.1904 | 4189.6875 | 1000.2621 | 0.0013432 | 9 | 10.8561 | 4.1932 | 4.1897 | 1.0003 | 0.0013432
| 281.15 | 1100000 | 4194.833 | 4192.4941 | 1000.3323 | 0.0013834 | 8 | 10.8561 | 4.1948 | 4.1925 | 1.0003 | 0.0013834
| 280.15 | 1100000 | 4196.6177 | 4195.2246 | 1000.3886 | 0.0014256 | 7 | 10.8561 | 4.1966 | 4.1952 | 1.0004 | 0.0014256
| 279.15 | 1100000 | 4198.5591 | 4197.8794 | 1000.4304 | 0.0014699 | 6 | 10.8561 | 4.1986 | 4.1979 | 1.0004 | 0.0014699
| 278.15 | 1100000 | 4200.6714 | 4200.459 | 1000.4574 | 0.0015165 | 5 | 10.8561 | 4.2007 | 4.2005 | 1.0005 | 0.0015165
| 277.15 | 1100000 | 4202.9727 | 4202.9644 | 1000.469 | 0.0015654 | 4 | 10.8561 | 4.203 | 4.203 | 1.0005 | 0.0015654
| 276.15 | 1100000 | 4205.4805 | 4205.3965 | 1000.4648 | 0.001617 | 3 | 10.8561 | 4.2055 | 4.2054 | 1.0005 | 0.001617
| 275.15 | 1100000 | 4208.2168 | 4207.7568 | 1000.4442 | 0.0016713 | 2 | 10.8561 | 4.2082 | 4.2078 | 1.0004 | 0.0016713
| 274.15 | 1100000 | 4211.2036 | 4210.0474 | 1000.4067 | 0.0017286 | 0.99999 | 10.8561 | 4.2112 | 4.21 | 1.0004 | 0.0017286
| 273.15 | 1100000 | 4214.4663 | 4212.2695 | 1000.3518 | 0.001789 | -6.1035e-06 | 10.8561 | 4.2145 | 4.2123 | 1.0004 | 0.001789
| 473.15 | 1000000 | 2428.8462 | 1752.6189 | 4.8543 | 1.5894e-05 | 200 | 9.8692 | 2.4288 | 1.7526 | 0.0048543 | 1.5894e-05
| 472.15 | 1000000 | 2436.9348 | 1757.2754 | 4.8675 | 1.585e-05 | 199 | 9.8692 | 2.4369 | 1.7573 | 0.0048675 | 1.585e-05
| 471.15 | 1000000 | 2445.3477 | 1762.1443 | 4.8809 | 1.5807e-05 | 198 | 9.8692 | 2.4453 | 1.7621 | 0.0048809 | 1.5807e-05
| 470.15 | 1000000 | 2454.1121 | 1767.2451 | 4.8944 | 1.5764e-05 | 197 | 9.8692 | 2.4541 | 1.7672 | 0.0048944 | 1.5764e-05
| 469.15 | 1000000 | 2463.2595 | 1772.6001 | 4.908 | 1.5721e-05 | 196 | 9.8692 | 2.4633 | 1.7726 | 0.004908 | 1.5721e-05
| 468.15 | 1000000 | 2472.8254 | 1778.2343 | 4.9217 | 1.5677e-05 | 195 | 9.8692 | 2.4728 | 1.7782 | 0.0049217 | 1.5677e-05
| 467.15 | 1000000 | 2482.8496 | 1784.1758 | 4.9355 | 1.5634e-05 | 194 | 9.8692 | 2.4828 | 1.7842 | 0.0049355 | 1.5634e-05
| 466.15 | 1000000 | 2493.3772 | 1790.4565 | 4.9495 | 1.5591e-05 | 193 | 9.8692 | 2.4934 | 1.7905 | 0.0049495 | 1.5591e-05
| 465.15 | 1000000 | 2504.459 | 1797.1125 | 4.9635 | 1.5547e-05 | 192 | 9.8692 | 2.5045 | 1.7971 | 0.0049635 | 1.5547e-05
| 464.15 | 1000000 | 2516.1526 | 1804.1848 | 4.9777 | 1.5504e-05 | 191 | 9.8692 | 2.5162 | 1.8042 | 0.0049777 | 1.5504e-05
| 463.15 | 1000000 | 2528.5232 | 1811.7194 | 4.992 | 1.5461e-05 | 190 | 9.8692 | 2.5285 | 1.8117 | 0.004992 | 1.5461e-05
| 462.15 | 1000000 | 2541.645 | 1819.7686 | 5.0065 | 1.5417e-05 | 189 | 9.8692 | 2.5416 | 1.8198 | 0.0050065 | 1.5417e-05
| 461.15 | 1000000 | 2555.6013 | 1828.3918 | 5.0211 | 1.5374e-05 | 188 | 9.8692 | 2.5556 | 1.8284 | 0.0050211 | 1.5374e-05
| 460.15 | 1000000 | 2570.4875 | 1837.6564 | 5.0359 | 1.5331e-05 | 187 | 9.8692 | 2.5705 | 1.8377 | 0.0050359 | 1.5331e-05
| 459.15 | 1000000 | 2586.4116 | 1847.6384 | 5.0508 | 1.5287e-05 | 186 | 9.8692 | 2.5864 | 1.8476 | 0.0050508 | 1.5287e-05
| 458.15 | 1000000 | 2603.4961 | 1858.4243 | 5.0658 | 1.5244e-05 | 185 | 9.8692 | 2.6035 | 1.8584 | 0.0050658 | 1.5244e-05
| 457.15 | 1000000 | 2621.8806 | 1870.1122 | 5.081 | 1.52e-05 | 184 | 9.8692 | 2.6219 | 1.8701 | 0.005081 | 1.52e-05
| 456.15 | 1000000 | 2641.7236 | 1882.8132 | 5.0964 | 1.5157e-05 | 183 | 9.8692 | 2.6417 | 1.8828 | 0.0050964 | 1.5157e-05
| 455.15 | 1000000 | 2663.2056 | 1896.6534 | 5.1119 | 1.5114e-05 | 182 | 9.8692 | 2.6632 | 1.8967 | 0.0051119 | 1.5114e-05
| 454.15 | 1000000 | 2686.5315 | 1911.7761 | 5.1276 | 1.507e-05 | 181 | 9.8692 | 2.6865 | 1.9118 | 0.0051276 | 1.507e-05
| 453.15 | 1000000 | 2711.9353 | 1928.3433 | 5.1436 | 1.5027e-05 | 180 | 9.8692 | 2.7119 | 1.9283 | 0.0051436 | 1.5027e-05
| 452.15 | 1000000 | 4401.6362 | 3400.3914 | 888.0846 | 0.00015103 | 179 | 9.8692 | 4.4016 | 3.4004 | 0.88808 | 0.00015103
| 451.15 | 1000000 | 4397.7637 | 3404.5198 | 889.1605 | 0.00015194 | 178 | 9.8692 | 4.3978 | 3.4045 | 0.88916 | 0.00015194
| 450.15 | 1000000 | 4393.9453 | 3408.6636 | 890.2313 | 0.00015286 | 177 | 9.8692 | 4.3939 | 3.4087 | 0.89023 | 0.00015286
| 449.15 | 1000000 | 4390.1807 | 3412.8225 | 891.297 | 0.00015379 | 176 | 9.8692 | 4.3902 | 3.4128 | 0.8913 | 0.00015379
| 448.15 | 1000000 | 4386.4683 | 3416.9963 | 892.3576 | 0.00015473 | 175 | 9.8692 | 4.3865 | 3.417 | 0.89236 | 0.00015473
| 447.15 | 1000000 | 4382.8076 | 3421.1855 | 893.4132 | 0.00015568 | 174 | 9.8692 | 4.3828 | 3.4212 | 0.89341 | 0.00015568
| 446.15 | 1000000 | 4379.1978 | 3425.3894 | 894.4639 | 0.00015664 | 173 | 9.8692 | 4.3792 | 3.4254 | 0.89446 | 0.00015664
| 445.15 | 1000000 | 4375.6382 | 3429.6079 | 895.5095 | 0.00015762 | 172 | 9.8692 | 4.3756 | 3.4296 | 0.89551 | 0.00015762
| 444.15 | 1000000 | 4372.1279 | 3433.8413 | 896.5502 | 0.0001586 | 171 | 9.8692 | 4.3721 | 3.4338 | 0.89655 | 0.0001586
| 443.15 | 1000000 | 4368.666 | 3438.0894 | 897.5859 | 0.0001596 | 170 | 9.8692 | 4.3687 | 3.4381 | 0.89759 | 0.0001596
| 442.15 | 1000000 | 4365.2524 | 3442.3518 | 898.6169 | 0.00016062 | 169 | 9.8692 | 4.3653 | 3.4424 | 0.89862 | 0.00016062
| 441.15 | 1000000 | 4361.8853 | 3446.6284 | 899.6429 | 0.00016164 | 168 | 9.8692 | 4.3619 | 3.4466 | 0.89964 | 0.00016164
| 440.15 | 1000000 | 4358.5649 | 3450.9197 | 900.6641 | 0.00016268 | 167 | 9.8692 | 4.3586 | 3.4509 | 0.90066 | 0.00016268
| 439.15 | 1000000 | 4355.29 | 3455.2249 | 901.6804 | 0.00016373 | 166 | 9.8692 | 4.3553 | 3.4552 | 0.90168 | 0.00016373
| 438.15 | 1000000 | 4352.0601 | 3459.5442 | 902.692 | 0.0001648 | 165 | 9.8692 | 4.3521 | 3.4595 | 0.90269 | 0.0001648
| 437.15 | 1000000 | 4348.874 | 3463.8774 | 903.6988 | 0.00016588 | 164 | 9.8692 | 4.3489 | 3.4639 | 0.9037 | 0.00016588
| 436.15 | 1000000 | 4345.7319 | 3468.2246 | 904.7009 | 0.00016697 | 163 | 9.8692 | 4.3457 | 3.4682 | 0.9047 | 0.00016697
| 435.15 | 1000000 | 4342.6328 | 3472.5854 | 905.6982 | 0.00016808 | 162 | 9.8692 | 4.3426 | 3.4726 | 0.9057 | 0.00016808
| 434.15 | 1000000 | 4339.5757 | 3476.9602 | 906.6908 | 0.0001692 | 161 | 9.8692 | 4.3396 | 3.477 | 0.90669 | 0.0001692
| 433.15 | 1000000 | 4336.5605 | 3481.3484 | 907.6788 | 0.00017034 | 160 | 9.8692 | 4.3366 | 3.4813 | 0.90768 | 0.00017034
| 432.15 | 1000000 | 4333.5864 | 3485.7502 | 908.662 | 0.00017149 | 159 | 9.8692 | 4.3336 | 3.4858 | 0.90866 | 0.00017149
| 431.15 | 1000000 | 4330.6523 | 3490.1655 | 909.6406 | 0.00017266 | 158 | 9.8692 | 4.3307 | 3.4902 | 0.90964 | 0.00017266
| 430.15 | 1000000 | 4327.7588 | 3494.594 | 910.6146 | 0.00017384 | 157 | 9.8692 | 4.3278 | 3.4946 | 0.91061 | 0.00017384
| 429.15 | 1000000 | 4324.9038 | 3499.0356 | 911.584 | 0.00017504 | 156 | 9.8692 | 4.3249 | 3.499 | 0.91158 | 0.00017504
| 428.15 | 1000000 | 4322.0879 | 3503.4907 | 912.5488 | 0.00017625 | 155 | 9.8692 | 4.3221 | 3.5035 | 0.91255 | 0.00017625
| 427.15 | 1000000 | 4319.3105 | 3507.9587 | 913.509 | 0.00017749 | 154 | 9.8692 | 4.3193 | 3.508 | 0.91351 | 0.00017749
| 426.15 | 1000000 | 4316.5703 | 3512.4397 | 914.4646 | 0.00017874 | 153 | 9.8692 | 4.3166 | 3.5124 | 0.91446 | 0.00017874
| 425.15 | 1000000 | 4313.8677 | 3516.9336 | 915.4156 | 0.00018 | 152 | 9.8692 | 4.3139 | 3.5169 | 0.91542 | 0.00018
| 424.15 | 1000000 | 4311.2012 | 3521.4402 | 916.3622 | 0.00018129 | 151 | 9.8692 | 4.3112 | 3.5214 | 0.91636 | 0.00018129
| 423.15 | 1000000 | 4308.5708 | 3525.9595 | 917.3042 | 0.00018259 | 150 | 9.8692 | 4.3086 | 3.526 | 0.9173 | 0.00018259
| 422.15 | 1000000 | 4305.9761 | 3530.4917 | 918.2417 | 0.00018391 | 149 | 9.8692 | 4.306 | 3.5305 | 0.91824 | 0.00018391
| 421.15 | 1000000 | 4303.4165 | 3535.0361 | 919.1747 | 0.00018525 | 148 | 9.8692 | 4.3034 | 3.535 | 0.91917 | 0.00018525
| 420.15 | 1000000 | 4300.8916 | 3539.5933 | 920.1033 | 0.00018661 | 147 | 9.8692 | 4.3009 | 3.5396 | 0.9201 | 0.00018661
| 419.15 | 1000000 | 4298.4009 | 3544.1628 | 921.0273 | 0.00018799 | 146 | 9.8692 | 4.2984 | 3.5442 | 0.92103 | 0.00018799
| 418.15 | 1000000 | 4295.9438 | 3548.7446 | 921.9469 | 0.00018939 | 145 | 9.8692 | 4.2959 | 3.5487 | 0.92195 | 0.00018939
| 417.15 | 1000000 | 4293.52 | 3553.3389 | 922.8621 | 0.00019081 | 144 | 9.8692 | 4.2935 | 3.5533 | 0.92286 | 0.00019081
| 416.15 | 1000000 | 4291.1289 | 3557.9451 | 923.7727 | 0.00019225 | 143 | 9.8692 | 4.2911 | 3.5579 | 0.92377 | 0.00019225
| 415.15 | 1000000 | 4288.7705 | 3562.5635 | 924.679 | 0.00019372 | 142 | 9.8692 | 4.2888 | 3.5626 | 0.92468 | 0.00019372
| 414.15 | 1000000 | 4286.4438 | 3567.1938 | 925.5808 | 0.0001952 | 141 | 9.8692 | 4.2864 | 3.5672 | 0.92558 | 0.0001952
| 413.15 | 1000000 | 4284.1489 | 3571.8359 | 926.4782 | 0.0001967 | 140 | 9.8692 | 4.2841 | 3.5718 | 0.92648 | 0.0001967
| 412.15 | 1000000 | 4281.8848 | 3576.4902 | 927.3712 | 0.00019823 | 139 | 9.8692 | 4.2819 | 3.5765 | 0.92737 | 0.00019823
| 411.15 | 1000000 | 4279.6519 | 3581.1562 | 928.2598 | 0.00019978 | 138 | 9.8692 | 4.2797 | 3.5812 | 0.92826 | 0.00019978
| 410.15 | 1000000 | 4277.4492 | 3585.8337 | 929.144 | 0.00020136 | 137 | 9.8692 | 4.2774 | 3.5858 | 0.92914 | 0.00020136
| 409.15 | 1000000 | 4275.2764 | 3590.5232 | 930.0239 | 0.00020296 | 136 | 9.8692 | 4.2753 | 3.5905 | 0.93002 | 0.00020296
| 408.15 | 1000000 | 4273.1333 | 3595.2239 | 930.8993 | 0.00020458 | 135 | 9.8692 | 4.2731 | 3.5952 | 0.9309 | 0.00020458
| 407.15 | 1000000 | 4271.0195 | 3599.9363 | 931.7703 | 0.00020623 | 134 | 9.8692 | 4.271 | 3.5999 | 0.93177 | 0.00020623
| 406.15 | 1000000 | 4268.9351 | 3604.6599 | 932.637 | 0.0002079 | 133 | 9.8692 | 4.2689 | 3.6047 | 0.93264 | 0.0002079
| 405.15 | 1000000 | 4266.8789 | 3609.395 | 933.4993 | 0.0002096 | 132 | 9.8692 | 4.2669 | 3.6094 | 0.9335 | 0.0002096
| 404.15 | 1000000 | 4264.8511 | 3614.1414 | 934.3572 | 0.00021133 | 131 | 9.8692 | 4.2649 | 3.6141 | 0.93436 | 0.00021133
| 403.15 | 1000000 | 4262.8511 | 3618.8989 | 935.2108 | 0.00021308 | 130 | 9.8692 | 4.2629 | 3.6189 | 0.93521 | 0.00021308
| 402.15 | 1000000 | 4260.8789 | 3623.6675 | 936.0599 | 0.00021487 | 129 | 9.8692 | 4.2609 | 3.6237 | 0.93606 | 0.00021487
| 401.15 | 1000000 | 4258.9341 | 3628.4473 | 936.9048 | 0.00021668 | 128 | 9.8692 | 4.2589 | 3.6284 | 0.9369 | 0.00021668
| 400.15 | 1000000 | 4257.0166 | 3633.2378 | 937.7452 | 0.00021852 | 127 | 9.8692 | 4.257 | 3.6332 | 0.93775 | 0.00021852
| 399.15 | 1000000 | 4255.1255 | 3638.0393 | 938.5813 | 0.00022038 | 126 | 9.8692 | 4.2551 | 3.638 | 0.93858 | 0.00022038
| 398.15 | 1000000 | 4253.2607 | 3642.8513 | 939.413 | 0.00022228 | 125 | 9.8692 | 4.2533 | 3.6429 | 0.93941 | 0.00022228
| 397.15 | 1000000 | 4251.4224 | 3647.6743 | 940.2404 | 0.00022421 | 124 | 9.8692 | 4.2514 | 3.6477 | 0.94024 | 0.00022421
| 396.15 | 1000000 | 4249.6099 | 3652.5078 | 941.0634 | 0.00022618 | 123 | 9.8692 | 4.2496 | 3.6525 | 0.94106 | 0.00022618
| 395.15 | 1000000 | 4247.8232 | 3657.3521 | 941.882 | 0.00022817 | 122 | 9.8692 | 4.2478 | 3.6574 | 0.94188 | 0.00022817
| 394.15 | 1000000 | 4246.062 | 3662.2065 | 942.6963 | 0.0002302 | 121 | 9.8692 | 4.2461 | 3.6622 | 0.9427 | 0.0002302
| 393.15 | 1000000 | 4244.3262 | 3667.0713 | 943.5062 | 0.00023226 | 120 | 9.8692 | 4.2443 | 3.6671 | 0.94351 | 0.00023226
| 392.15 | 1000000 | 4242.6147 | 3671.9465 | 944.3116 | 0.00023436 | 119 | 9.8692 | 4.2426 | 3.6719 | 0.94431 | 0.00023436
| 391.15 | 1000000 | 4240.9282 | 3676.8318 | 945.1127 | 0.00023649 | 118 | 9.8692 | 4.2409 | 3.6768 | 0.94511 | 0.00023649
| 390.15 | 1000000 | 4239.2666 | 3681.7273 | 945.9095 | 0.00023866 | 117 | 9.8692 | 4.2393 | 3.6817 | 0.94591 | 0.00023866
| 389.15 | 1000000 | 4237.6289 | 3686.6326 | 946.7018 | 0.00024086 | 116 | 9.8692 | 4.2376 | 3.6866 | 0.9467 | 0.00024086
| 388.15 | 1000000 | 4236.0151 | 3691.5479 | 947.4897 | 0.00024311 | 115 | 9.8692 | 4.236 | 3.6915 | 0.94749 | 0.00024311
| 387.15 | 1000000 | 4234.4253 | 3696.4729 | 948.2733 | 0.00024539 | 114 | 9.8692 | 4.2344 | 3.6965 | 0.94827 | 0.00024539
| 386.15 | 1000000 | 4232.8594 | 3701.4077 | 949.0524 | 0.00024771 | 113 | 9.8692 | 4.2329 | 3.7014 | 0.94905 | 0.00024771
| 385.15 | 1000000 | 4231.3169 | 3706.3521 | 949.8271 | 0.00025008 | 112 | 9.8692 | 4.2313 | 3.7064 | 0.94983 | 0.00025008
| 384.15 | 1000000 | 4229.7974 | 3711.3057 | 950.5974 | 0.00025248 | 111 | 9.8692 | 4.2298 | 3.7113 | 0.9506 | 0.00025248
| 383.15 | 1000000 | 4228.3013 | 3716.2688 | 951.3632 | 0.00025493 | 110 | 9.8692 | 4.2283 | 3.7163 | 0.95136 | 0.00025493
| 382.15 | 1000000 | 4226.8281 | 3721.2412 | 952.1246 | 0.00025742 | 109 | 9.8692 | 4.2268 | 3.7212 | 0.95212 | 0.00025742
| 381.15 | 1000000 | 4225.3774 | 3726.2224 | 952.8815 | 0.00025995 | 108 | 9.8692 | 4.2254 | 3.7262 | 0.95288 | 0.00025995
| 380.15 | 1000000 | 4223.9497 | 3731.2129 | 953.634 | 0.00026253 | 107 | 9.8692 | 4.2239 | 3.7312 | 0.95363 | 0.00026253
| 379.15 | 1000000 | 4222.5444 | 3736.2119 | 954.3819 | 0.00026516 | 106 | 9.8692 | 4.2225 | 3.7362 | 0.95438 | 0.00026516
| 378.15 | 1000000 | 4221.1616 | 3741.2197 | 955.1254 | 0.00026784 | 105 | 9.8692 | 4.2212 | 3.7412 | 0.95513 | 0.00026784
| 377.15 | 1000000 | 4219.8008 | 3746.2363 | 955.8644 | 0.00027057 | 104 | 9.8692 | 4.2198 | 3.7462 | 0.95586 | 0.00027057
| 376.15 | 1000000 | 4218.4619 | 3751.261 | 956.5989 | 0.00027334 | 103 | 9.8692 | 4.2185 | 3.7513 | 0.9566 | 0.00027334
| 375.15 | 1000000 | 4217.1455 | 3756.2939 | 957.3288 | 0.00027617 | 102 | 9.8692 | 4.2171 | 3.7563 | 0.95733 | 0.00027617
| 374.15 | 1000000 | 4215.8506 | 3761.335 | 958.0542 | 0.00027905 | 101 | 9.8692 | 4.2159 | 3.7613 | 0.95805 | 0.00027905
| 373.15 | 1000000 | 4214.5771 | 3766.384 | 958.775 | 0.00028199 | 100 | 9.8692 | 4.2146 | 3.7664 | 0.95878 | 0.00028199
| 372.15 | 1000000 | 4213.3257 | 3771.4407 | 959.4913 | 0.00028498 | 99 | 9.8692 | 4.2133 | 3.7714 | 0.95949 | 0.00028498
| 371.15 | 1000000 | 4212.0957 | 3776.5049 | 960.2029 | 0.00028802 | 98 | 9.8692 | 4.2121 | 3.7765 | 0.9602 | 0.00028802
| 370.15 | 1000000 | 4210.8872 | 3781.5764 | 960.91 | 0.00029113 | 97 | 9.8692 | 4.2109 | 3.7816 | 0.96091 | 0.00029113
| 369.15 | 1000000 | 4209.6997 | 3786.655 | 961.6124 | 0.0002943 | 96 | 9.8692 | 4.2097 | 3.7867 | 0.96161 | 0.0002943
| 368.15 | 1000000 | 4208.5337 | 3791.7407 | 962.3101 | 0.00029753 | 95 | 9.8692 | 4.2085 | 3.7917 | 0.96231 | 0.00029753
| 367.15 | 1000000 | 4207.3887 | 3796.833 | 963.0032 | 0.00030082 | 94 | 9.8692 | 4.2074 | 3.7968 | 0.963 | 0.00030082
| 366.15 | 1000000 | 4206.2646 | 3801.9319 | 963.6917 | 0.00030418 | 93 | 9.8692 | 4.2063 | 3.8019 | 0.96369 | 0.00030418
| 365.15 | 1000000 | 4205.1621 | 3807.0369 | 964.3754 | 0.0003076 | 92 | 9.8692 | 4.2052 | 3.807 | 0.96438 | 0.0003076
| 364.15 | 1000000 | 4204.0801 | 3812.1479 | 965.0544 | 0.00031109 | 91 | 9.8692 | 4.2041 | 3.8121 | 0.96505 | 0.00031109
| 363.15 | 1000000 | 4203.019 | 3817.2646 | 965.7286 | 0.00031465 | 90 | 9.8692 | 4.203 | 3.8173 | 0.96573 | 0.00031465
| 362.15 | 1000000 | 4201.979 | 3822.387 | 966.3981 | 0.00031829 | 89 | 9.8692 | 4.202 | 3.8224 | 0.9664 | 0.00031829
| 361.15 | 1000000 | 4200.9595 | 3827.5146 | 967.0627 | 0.000322 | 88 | 9.8692 | 4.201 | 3.8275 | 0.96706 | 0.000322
| 360.15 | 1000000 | 4199.9609 | 3832.647 | 967.7226 | 0.00032578 | 87 | 9.8692 | 4.2 | 3.8326 | 0.96772 | 0.00032578
| 359.15 | 1000000 | 4198.9829 | 3837.7839 | 968.3776 | 0.00032964 | 86 | 9.8692 | 4.199 | 3.8378 | 0.96838 | 0.00032964
| 358.15 | 1000000 | 4198.0254 | 3842.9253 | 969.0277 | 0.00033359 | 85 | 9.8692 | 4.198 | 3.8429 | 0.96903 | 0.00033359
| 357.15 | 1000000 | 4197.0889 | 3848.0703 | 969.6729 | 0.00033761 | 84 | 9.8692 | 4.1971 | 3.8481 | 0.96967 | 0.00033761
| 356.15 | 1000000 | 4196.1729 | 3853.2192 | 970.3132 | 0.00034172 | 83 | 9.8692 | 4.1962 | 3.8532 | 0.97031 | 0.00034172
| 355.15 | 1000000 | 4195.2773 | 3858.3713 | 970.9485 | 0.00034592 | 82 | 9.8692 | 4.1953 | 3.8584 | 0.97095 | 0.00034592
| 354.15 | 1000000 | 4194.4023 | 3863.5264 | 971.5789 | 0.00035021 | 81 | 9.8692 | 4.1944 | 3.8635 | 0.97158 | 0.00035021
| 353.15 | 1000000 | 4193.5479 | 3868.6836 | 972.2043 | 0.00035459 | 80 | 9.8692 | 4.1935 | 3.8687 | 0.9722 | 0.00035459
| 352.15 | 1000000 | 4192.7139 | 3873.8433 | 972.8246 | 0.00035907 | 79 | 9.8692 | 4.1927 | 3.8738 | 0.97282 | 0.00035907
| 351.15 | 1000000 | 4191.9004 | 3879.0044 | 973.4398 | 0.00036364 | 78 | 9.8692 | 4.1919 | 3.879 | 0.97344 | 0.00036364
| 350.15 | 1000000 | 4191.1074 | 3884.1667 | 974.0499 | 0.00036831 | 77 | 9.8692 | 4.1911 | 3.8842 | 0.97405 | 0.00036831
| 349.15 | 1000000 | 4190.335 | 3889.3298 | 974.6548 | 0.00037309 | 76 | 9.8692 | 4.1903 | 3.8893 | 0.97465 | 0.00037309
| 348.15 | 1000000 | 4189.583 | 3894.4934 | 975.2546 | 0.00037798 | 75 | 9.8692 | 4.1896 | 3.8945 | 0.97525 | 0.00037798
| 347.15 | 1000000 | 4188.8511 | 3899.6565 | 975.8492 | 0.00038297 | 74 | 9.8692 | 4.1889 | 3.8997 | 0.97585 | 0.00038297
| 346.15 | 1000000 | 4188.1401 | 3904.8191 | 976.4385 | 0.00038808 | 73 | 9.8692 | 4.1881 | 3.9048 | 0.97644 | 0.00038808
| 345.15 | 1000000 | 4187.4497 | 3909.9802 | 977.0225 | 0.00039331 | 72 | 9.8692 | 4.1874 | 3.91 | 0.97702 | 0.00039331
| 344.15 | 1000000 | 4186.7798 | 3915.1396 | 977.6011 | 0.00039865 | 71 | 9.8692 | 4.1868 | 3.9151 | 0.9776 | 0.00039865
| 343.15 | 1000000 | 4186.1299 | 3920.2966 | 978.1744 | 0.00040412 | 70 | 9.8692 | 4.1861 | 3.9203 | 0.97817 | 0.00040412
| 342.15 | 1000000 | 4185.501 | 3925.4504 | 978.7423 | 0.00040972 | 69 | 9.8692 | 4.1855 | 3.9255 | 0.97874 | 0.00040972
| 341.15 | 1000000 | 4184.8921 | 3930.6008 | 979.3047 | 0.00041545 | 68 | 9.8692 | 4.1849 | 3.9306 | 0.9793 | 0.00041545
| 340.15 | 1000000 | 4184.3042 | 3935.7468 | 979.8616 | 0.00042132 | 67 | 9.8692 | 4.1843 | 3.9357 | 0.97986 | 0.00042132
| 339.15 | 1000000 | 4183.7368 | 3940.8879 | 980.413 | 0.00042733 | 66 | 9.8692 | 4.1837 | 3.9409 | 0.98041 | 0.00042733
| 338.15 | 1000000 | 4183.1899 | 3946.0234 | 980.9588 | 0.00043348 | 65 | 9.8692 | 4.1832 | 3.946 | 0.98096 | 0.00043348
| 337.15 | 1000000 | 4182.6636 | 3951.1526 | 981.4989 | 0.00043979 | 64 | 9.8692 | 4.1827 | 3.9512 | 0.9815 | 0.00043979
| 336.15 | 1000000 | 4182.1582 | 3956.2747 | 982.0334 | 0.00044624 | 63 | 9.8692 | 4.1822 | 3.9563 | 0.98203 | 0.00044624
| 335.15 | 1000000 | 4181.6729 | 3961.3887 | 982.5621 | 0.00045286 | 62 | 9.8692 | 4.1817 | 3.9614 | 0.98256 | 0.00045286
| 334.15 | 1000000 | 4181.209 | 3966.4939 | 983.085 | 0.00045965 | 61 | 9.8692 | 4.1812 | 3.9665 | 0.98308 | 0.00045965
| 333.15 | 1000000 | 4180.7651 | 3971.5898 | 983.602 | 0.0004666 | 60 | 9.8692 | 4.1808 | 3.9716 | 0.9836 | 0.0004666
| 332.15 | 1000000 | 4180.3423 | 3976.6753 | 984.1132 | 0.00047374 | 59 | 9.8692 | 4.1803 | 3.9767 | 0.98411 | 0.00047374
| 331.15 | 1000000 | 4179.9404 | 3981.7495 | 984.6183 | 0.00048105 | 58 | 9.8692 | 4.1799 | 3.9817 | 0.98462 | 0.00048105
| 330.15 | 1000000 | 4179.5591 | 3986.8113 | 985.1176 | 0.00048856 | 57 | 9.8692 | 4.1796 | 3.9868 | 0.98512 | 0.00048856
| 329.15 | 1000000 | 4179.1987 | 3991.8601 | 985.6107 | 0.00049626 | 56 | 9.8692 | 4.1792 | 3.9919 | 0.98561 | 0.00049626
| 328.15 | 1000000 | 4178.8594 | 3996.8948 | 986.0976 | 0.00050416 | 55 | 9.8692 | 4.1789 | 3.9969 | 0.9861 | 0.00050416
| 327.15 | 1000000 | 4178.541 | 4001.9143 | 986.5783 | 0.00051228 | 54 | 9.8692 | 4.1785 | 4.0019 | 0.98658 | 0.00051228
| 326.15 | 1000000 | 4178.2437 | 4006.9175 | 987.0528 | 0.00052061 | 53 | 9.8692 | 4.1782 | 4.0069 | 0.98705 | 0.00052061
| 325.15 | 1000000 | 4177.9673 | 4011.9036 | 987.521 | 0.00052917 | 52 | 9.8692 | 4.178 | 4.0119 | 0.98752 | 0.00052917
| 324.15 | 1000000 | 4177.7124 | 4016.8711 | 987.9827 | 0.00053797 | 51 | 9.8692 | 4.1777 | 4.0169 | 0.98798 | 0.00053797
| 323.15 | 1000000 | 4177.4785 | 4021.8191 | 988.438 | 0.00054701 | 50 | 9.8692 | 4.1775 | 4.0218 | 0.98844 | 0.00054701
| 322.15 | 1000000 | 4177.2666 | 4026.7466 | 988.8867 | 0.0005563 | 49 | 9.8692 | 4.1773 | 4.0267 | 0.98889 | 0.0005563
| 321.15 | 1000000 | 4177.0757 | 4031.6519 | 989.3288 | 0.00056585 | 48 | 9.8692 | 4.1771 | 4.0317 | 0.98933 | 0.00056585
| 320.15 | 1000000 | 4176.9062 | 4036.5342 | 989.7642 | 0.00057568 | 47 | 9.8692 | 4.1769 | 4.0365 | 0.98976 | 0.00057568
| 319.15 | 1000000 | 4176.7588 | 4041.3921 | 990.1927 | 0.00058579 | 46 | 9.8692 | 4.1768 | 4.0414 | 0.99019 | 0.00058579
| 318.15 | 1000000 | 4176.6333 | 4046.2241 | 990.6145 | 0.00059619 | 45 | 9.8692 | 4.1766 | 4.0462 | 0.99061 | 0.00059619
| 317.15 | 1000000 | 4176.5303 | 4051.0291 | 991.0293 | 0.0006069 | 44 | 9.8692 | 4.1765 | 4.051 | 0.99103 | 0.0006069
| 316.15 | 1000000 | 4176.4492 | 4055.8054 | 991.4371 | 0.00061792 | 43 | 9.8692 | 4.1764 | 4.0558 | 0.99144 | 0.00061792
| 315.15 | 1000000 | 4176.3906 | 4060.552 | 991.8376 | 0.00062928 | 42 | 9.8692 | 4.1764 | 4.0606 | 0.99184 | 0.00062928
| 314.15 | 1000000 | 4176.355 | 4065.2671 | 992.2311 | 0.00064099 | 41 | 9.8692 | 4.1764 | 4.0653 | 0.99223 | 0.00064099
| 313.15 | 1000000 | 4176.3423 | 4069.9495 | 992.6171 | 0.00065305 | 40 | 9.8692 | 4.1763 | 4.0699 | 0.99262 | 0.00065305
| 312.15 | 1000000 | 4176.353 | 4074.5977 | 992.9958 | 0.00066549 | 39 | 9.8692 | 4.1764 | 4.0746 | 0.993 | 0.00066549
| 311.15 | 1000000 | 4176.3877 | 4079.2097 | 993.3669 | 0.00067832 | 38 | 9.8692 | 4.1764 | 4.0792 | 0.99337 | 0.00067832
| 310.15 | 1000000 | 4176.4468 | 4083.7847 | 993.7304 | 0.00069155 | 37 | 9.8692 | 4.1764 | 4.0838 | 0.99373 | 0.00069155
| 309.15 | 1000000 | 4176.5308 | 4088.3206 | 994.0861 | 0.00070521 | 36 | 9.8692 | 4.1765 | 4.0883 | 0.99409 | 0.00070521
| 308.15 | 1000000 | 4176.6396 | 4092.8157 | 994.434 | 0.00071932 | 35 | 9.8692 | 4.1766 | 4.0928 | 0.99443 | 0.00071932
| 307.15 | 1000000 | 4176.7744 | 4097.2686 | 994.7739 | 0.00073389 | 34 | 9.8692 | 4.1768 | 4.0973 | 0.99477 | 0.00073389
| 306.15 | 1000000 | 4176.9365 | 4101.6777 | 995.1058 | 0.00074895 | 33 | 9.8692 | 4.1769 | 4.1017 | 0.99511 | 0.00074895
| 305.15 | 1000000 | 4177.1255 | 4106.0415 | 995.4293 | 0.00076451 | 32 | 9.8692 | 4.1771 | 4.106 | 0.99543 | 0.00076451
| 304.15 | 1000000 | 4177.3428 | 4110.3574 | 995.7446 | 0.00078061 | 31 | 9.8692 | 4.1773 | 4.1104 | 0.99574 | 0.00078061
| 303.15 | 1000000 | 4177.5894 | 4114.625 | 996.0513 | 0.00079726 | 30 | 9.8692 | 4.1776 | 4.1146 | 0.99605 | 0.00079726
| 302.15 | 1000000 | 4177.8667 | 4118.8418 | 996.3494 | 0.0008145 | 29 | 9.8692 | 4.1779 | 4.1188 | 0.99635 | 0.0008145
| 301.15 | 1000000 | 4178.1758 | 4123.0059 | 996.6387 | 0.00083234 | 28 | 9.8692 | 4.1782 | 4.123 | 0.99664 | 0.00083234
| 300.15 | 1000000 | 4178.5181 | 4127.1162 | 996.9191 | 0.00085084 | 27 | 9.8692 | 4.1785 | 4.1271 | 0.99692 | 0.00085084
| 299.15 | 1000000 | 4178.895 | 4131.1709 | 997.1903 | 0.00087 | 26 | 9.8692 | 4.1789 | 4.1312 | 0.99719 | 0.00087
| 298.15 | 1000000 | 4179.3086 | 4135.168 | 997.4523 | 0.00088987 | 25 | 9.8692 | 4.1793 | 4.1352 | 0.99745 | 0.00088987
| 297.15 | 1000000 | 4179.7607 | 4139.106 | 997.7048 | 0.00091049 | 24 | 9.8692 | 4.1798 | 4.1391 | 0.9977 | 0.00091049
| 296.15 | 1000000 | 4180.2539 | 4142.9834 | 997.9478 | 0.00093189 | 23 | 9.8692 | 4.1803 | 4.143 | 0.99795 | 0.00093189
| 295.15 | 1000000 | 4180.7905 | 4146.7983 | 998.1808 | 0.00095412 | 22 | 9.8692 | 4.1808 | 4.1468 | 0.99818 | 0.00095412
| 294.15 | 1000000 | 4181.373 | 4150.5493 | 998.4039 | 0.00097721 | 21 | 9.8692 | 4.1814 | 4.1505 | 0.9984 | 0.00097721
| 293.15 | 1000000 | 4182.0054 | 4154.2344 | 998.6168 | 0.0010012 | 20 | 9.8692 | 4.182 | 4.1542 | 0.99862 | 0.0010012
| 292.15 | 1000000 | 4182.6899 | 4157.853 | 998.8192 | 0.0010262 | 19 | 9.8692 | 4.1827 | 4.1579 | 0.99882 | 0.0010262
| 291.15 | 1000000 | 4183.4316 | 4161.4033 | 999.011 | 0.0010522 | 18 | 9.8692 | 4.1834 | 4.1614 | 0.99901 | 0.0010522
| 290.15 | 1000000 | 4184.2349 | 4164.8838 | 999.1919 | 0.0010793 | 17 | 9.8692 | 4.1842 | 4.1649 | 0.99919 | 0.0010793
| 289.15 | 1000000 | 4185.1035 | 4168.2935 | 999.3616 | 0.0011075 | 16 | 9.8692 | 4.1851 | 4.1683 | 0.99936 | 0.0011075
| 288.15 | 1000000 | 4186.0439 | 4171.6313 | 999.52 | 0.0011369 | 15 | 9.8692 | 4.186 | 4.1716 | 0.99952 | 0.0011369
| 287.15 | 1000000 | 4187.062 | 4174.896 | 999.6666 | 0.0011676 | 14 | 9.8692 | 4.1871 | 4.1749 | 0.99967 | 0.0011676
| 286.15 | 1000000 | 4188.1641 | 4178.0864 | 999.8013 | 0.0011997 | 13 | 9.8692 | 4.1882 | 4.1781 | 0.9998 | 0.0011997
| 285.15 | 1000000 | 4189.3574 | 4181.2021 | 999.9237 | 0.0012332 | 12 | 9.8692 | 4.1894 | 4.1812 | 0.99992 | 0.0012332
| 284.15 | 1000000 | 4190.6509 | 4184.2427 | 1000.0336 | 0.0012682 | 11 | 9.8692 | 4.1907 | 4.1842 | 1 | 0.0012682
| 283.15 | 1000000 | 4192.0537 | 4187.2075 | 1000.1305 | 0.0013049 | 10 | 9.8692 | 4.1921 | 4.1872 | 1.0001 | 0.0013049
| 282.15 | 1000000 | 4193.5752 | 4190.0962 | 1000.2141 | 0.0013433 | 9 | 9.8692 | 4.1936 | 4.1901 | 1.0002 | 0.0013433
| 281.15 | 1000000 | 4195.2271 | 4192.9087 | 1000.2842 | 0.0013835 | 8 | 9.8692 | 4.1952 | 4.1929 | 1.0003 | 0.0013835
| 280.15 | 1000000 | 4197.022 | 4195.645 | 1000.3401 | 0.0014258 | 7 | 9.8692 | 4.197 | 4.1956 | 1.0003 | 0.0014258
| 279.15 | 1000000 | 4198.9741 | 4198.3062 | 1000.3817 | 0.0014701 | 6 | 9.8692 | 4.199 | 4.1983 | 1.0004 | 0.0014701
| 278.15 | 1000000 | 4201.0977 | 4200.8921 | 1000.4083 | 0.0015166 | 5 | 9.8692 | 4.2011 | 4.2009 | 1.0004 | 0.0015166
| 277.15 | 1000000 | 4203.4111 | 4203.4043 | 1000.4196 | 0.0015656 | 4 | 9.8692 | 4.2034 | 4.2034 | 1.0004 | 0.0015656
| 276.15 | 1000000 | 4205.9316 | 4205.8433 | 1000.4151 | 0.0016172 | 3 | 9.8692 | 4.2059 | 4.2058 | 1.0004 | 0.0016172
| 275.15 | 1000000 | 4208.6816 | 4208.2109 | 1000.3942 | 0.0016715 | 2 | 9.8692 | 4.2087 | 4.2082 | 1.0004 | 0.0016715
| 274.15 | 1000000 | 4211.6831 | 4210.5088 | 1000.3563 | 0.0017288 | 0.99999 | 9.8692 | 4.2117 | 4.2105 | 1.0004 | 0.0017288
| 273.15 | 1000000 | 4214.9614 | 4212.7388 | 1000.301 | 0.0017893 | -6.1035e-06 | 9.8692 | 4.215 | 4.2127 | 1.0003 | 0.0017893
| 473.15 | 900000 | 2363.3638 | 1716.8186 | 4.3402 | 1.5925e-05 | 200 | 8.8823 | 2.3634 | 1.7168 | 0.0043402 | 1.5925e-05
| 472.15 | 900000 | 2369.7898 | 1720.4716 | 4.3517 | 1.5883e-05 | 199 | 8.8823 | 2.3698 | 1.7205 | 0.0043517 | 1.5883e-05
| 471.15 | 900000 | 2376.4309 | 1724.2631 | 4.3633 | 1.584e-05 | 198 | 8.8823 | 2.3764 | 1.7243 | 0.0043633 | 1.584e-05
| 470.15 | 900000 | 2383.3025 | 1728.2041 | 4.375 | 1.5797e-05 | 197 | 8.8823 | 2.3833 | 1.7282 | 0.004375 | 1.5797e-05
| 469.15 | 900000 | 2390.4216 | 1732.3065 | 4.3867 | 1.5754e-05 | 196 | 8.8823 | 2.3904 | 1.7323 | 0.0043867 | 1.5754e-05
| 468.15 | 900000 | 2397.8074 | 1736.5839 | 4.3986 | 1.5711e-05 | 195 | 8.8823 | 2.3978 | 1.7366 | 0.0043986 | 1.5711e-05
| 467.15 | 900000 | 2405.4814 | 1741.0515 | 4.4106 | 1.5668e-05 | 194 | 8.8823 | 2.4055 | 1.7411 | 0.0044106 | 1.5668e-05
| 466.15 | 900000 | 2413.4678 | 1745.7264 | 4.4226 | 1.5625e-05 | 193 | 8.8823 | 2.4135 | 1.7457 | 0.0044226 | 1.5625e-05
| 465.15 | 900000 | 2421.7939 | 1750.6281 | 4.4348 | 1.5582e-05 | 192 | 8.8823 | 2.4218 | 1.7506 | 0.0044348 | 1.5582e-05
| 464.15 | 900000 | 2430.4902 | 1755.7782 | 4.447 | 1.5539e-05 | 191 | 8.8823 | 2.4305 | 1.7558 | 0.004447 | 1.5539e-05
| 463.15 | 900000 | 2439.5916 | 1761.2015 | 4.4594 | 1.5496e-05 | 190 | 8.8823 | 2.4396 | 1.7612 | 0.0044594 | 1.5496e-05
| 462.15 | 900000 | 2449.1365 | 1766.9259 | 4.4718 | 1.5453e-05 | 189 | 8.8823 | 2.4491 | 1.7669 | 0.0044718 | 1.5453e-05
| 461.15 | 900000 | 2459.1697 | 1772.9828 | 4.4844 | 1.541e-05 | 188 | 8.8823 | 2.4592 | 1.773 | 0.0044844 | 1.541e-05
| 460.15 | 900000 | 2469.7405 | 1779.4077 | 4.4971 | 1.5367e-05 | 187 | 8.8823 | 2.4697 | 1.7794 | 0.0044971 | 1.5367e-05
| 459.15 | 900000 | 2480.9058 | 1786.2412 | 4.5099 | 1.5324e-05 | 186 | 8.8823 | 2.4809 | 1.7862 | 0.0045099 | 1.5324e-05
| 458.15 | 900000 | 2492.7295 | 1793.5291 | 4.5228 | 1.5281e-05 | 185 | 8.8823 | 2.4927 | 1.7935 | 0.0045228 | 1.5281e-05
| 457.15 | 900000 | 2505.2842 | 1801.3229 | 4.5358 | 1.5238e-05 | 184 | 8.8823 | 2.5053 | 1.8013 | 0.0045358 | 1.5238e-05
| 456.15 | 900000 | 2518.6523 | 1809.6816 | 4.5489 | 1.5195e-05 | 183 | 8.8823 | 2.5187 | 1.8097 | 0.0045489 | 1.5195e-05
| 455.15 | 900000 | 2532.9272 | 1818.6719 | 4.5622 | 1.5152e-05 | 182 | 8.8823 | 2.5329 | 1.8187 | 0.0045622 | 1.5152e-05
| 454.15 | 900000 | 2548.2156 | 1828.3693 | 4.5756 | 1.5109e-05 | 181 | 8.8823 | 2.5482 | 1.8284 | 0.0045756 | 1.5109e-05
| 453.15 | 900000 | 2564.6377 | 1838.8595 | 4.5891 | 1.5066e-05 | 180 | 8.8823 | 2.5646 | 1.8389 | 0.0045891 | 1.5066e-05
| 452.15 | 900000 | 2582.3313 | 1850.2401 | 4.6028 | 1.5023e-05 | 179 | 8.8823 | 2.5823 | 1.8502 | 0.0046028 | 1.5023e-05
| 451.15 | 900000 | 2601.4524 | 1862.6215 | 4.6166 | 1.498e-05 | 178 | 8.8823 | 2.6015 | 1.8626 | 0.0046166 | 1.498e-05
| 450.15 | 900000 | 2622.1794 | 1876.1293 | 4.6306 | 1.4937e-05 | 177 | 8.8823 | 2.6222 | 1.8761 | 0.0046306 | 1.4937e-05
| 449.15 | 900000 | 2644.7148 | 1890.9056 | 4.6447 | 1.4893e-05 | 176 | 8.8823 | 2.6447 | 1.8909 | 0.0046447 | 1.4893e-05
| 448.15 | 900000 | 4386.8926 | 3417.0771 | 892.2926 | 0.0001547 | 175 | 8.8823 | 4.3869 | 3.4171 | 0.89229 | 0.0001547
| 447.15 | 900000 | 4383.2271 | 3421.2664 | 893.3486 | 0.00015565 | 174 | 8.8823 | 4.3832 | 3.4213 | 0.89335 | 0.00015565
| 446.15 | 900000 | 4379.6123 | 3425.4707 | 894.3996 | 0.00015662 | 173 | 8.8823 | 4.3796 | 3.4255 | 0.8944 | 0.00015662
| 445.15 | 900000 | 4376.0479 | 3429.6897 | 895.4456 | 0.00015759 | 172 | 8.8823 | 4.376 | 3.4297 | 0.89545 | 0.00015759
| 444.15 | 900000 | 4372.5327 | 3433.9233 | 896.4867 | 0.00015858 | 171 | 8.8823 | 4.3725 | 3.4339 | 0.89649 | 0.00015858
| 443.15 | 900000 | 4369.0664 | 3438.1716 | 897.5228 | 0.00015958 | 170 | 8.8823 | 4.3691 | 3.4382 | 0.89752 | 0.00015958
| 442.15 | 900000 | 4365.6479 | 3442.4343 | 898.5541 | 0.00016059 | 169 | 8.8823 | 4.3656 | 3.4424 | 0.89855 | 0.00016059
| 441.15 | 900000 | 4362.2764 | 3446.7114 | 899.5804 | 0.00016162 | 168 | 8.8823 | 4.3623 | 3.4467 | 0.89958 | 0.00016162
| 440.15 | 900000 | 4358.9512 | 3451.0029 | 900.602 | 0.00016266 | 167 | 8.8823 | 4.359 | 3.451 | 0.9006 | 0.00016266
| 439.15 | 900000 | 4355.6724 | 3455.3086 | 901.6187 | 0.00016371 | 166 | 8.8823 | 4.3557 | 3.4553 | 0.90162 | 0.00016371
| 438.15 | 900000 | 4352.438 | 3459.6284 | 902.6306 | 0.00016477 | 165 | 8.8823 | 4.3524 | 3.4596 | 0.90263 | 0.00016477
| 437.15 | 900000 | 4349.248 | 3463.9622 | 903.6378 | 0.00016585 | 164 | 8.8823 | 4.3492 | 3.464 | 0.90364 | 0.00016585
| 436.15 | 900000 | 4346.1016 | 3468.3098 | 904.6401 | 0.00016694 | 163 | 8.8823 | 4.3461 | 3.4683 | 0.90464 | 0.00016694
| 435.15 | 900000 | 4342.9985 | 3472.6711 | 905.6378 | 0.00016805 | 162 | 8.8823 | 4.343 | 3.4727 | 0.90564 | 0.00016805
| 434.15 | 900000 | 4339.9375 | 3477.0461 | 906.6307 | 0.00016917 | 161 | 8.8823 | 4.3399 | 3.477 | 0.90663 | 0.00016917
| 433.15 | 900000 | 4336.9185 | 3481.4351 | 907.619 | 0.00017031 | 160 | 8.8823 | 4.3369 | 3.4814 | 0.90762 | 0.00017031
| 432.15 | 900000 | 4333.9404 | 3485.8374 | 908.6026 | 0.00017146 | 159 | 8.8823 | 4.3339 | 3.4858 | 0.9086 | 0.00017146
| 431.15 | 900000 | 4331.0029 | 3490.2529 | 909.5815 | 0.00017263 | 158 | 8.8823 | 4.331 | 3.4903 | 0.90958 | 0.00017263
| 430.15 | 900000 | 4328.1055 | 3494.6821 | 910.5558 | 0.00017381 | 157 | 8.8823 | 4.3281 | 3.4947 | 0.91056 | 0.00017381
| 429.15 | 900000 | 4325.2476 | 3499.1243 | 911.5255 | 0.00017501 | 156 | 8.8823 | 4.3252 | 3.4991 | 0.91153 | 0.00017501
| 428.15 | 900000 | 4322.4282 | 3503.5798 | 912.4905 | 0.00017623 | 155 | 8.8823 | 4.3224 | 3.5036 | 0.91249 | 0.00017623
| 427.15 | 900000 | 4319.647 | 3508.0483 | 913.451 | 0.00017746 | 154 | 8.8823 | 4.3196 | 3.508 | 0.91345 | 0.00017746
| 426.15 | 900000 | 4316.9038 | 3512.53 | 914.407 | 0.00017871 | 153 | 8.8823 | 4.3169 | 3.5125 | 0.91441 | 0.00017871
| 425.15 | 900000 | 4314.1978 | 3517.0244 | 915.3583 | 0.00017998 | 152 | 8.8823 | 4.3142 | 3.517 | 0.91536 | 0.00017998
| 424.15 | 900000 | 4311.5278 | 3521.5317 | 916.3052 | 0.00018126 | 151 | 8.8823 | 4.3115 | 3.5215 | 0.91631 | 0.00018126
| 423.15 | 900000 | 4308.8945 | 3526.0518 | 917.2474 | 0.00018257 | 150 | 8.8823 | 4.3089 | 3.5261 | 0.91725 | 0.00018257
| 422.15 | 900000 | 4306.2969 | 3530.5845 | 918.1852 | 0.00018389 | 149 | 8.8823 | 4.3063 | 3.5306 | 0.91819 | 0.00018389
| 421.15 | 900000 | 4303.7344 | 3535.1299 | 919.1185 | 0.00018523 | 148 | 8.8823 | 4.3037 | 3.5351 | 0.91912 | 0.00018523
| 420.15 | 900000 | 4301.2065 | 3539.6877 | 920.0473 | 0.00018659 | 147 | 8.8823 | 4.3012 | 3.5397 | 0.92005 | 0.00018659
| 419.15 | 900000 | 4298.7129 | 3544.2578 | 920.9716 | 0.00018797 | 146 | 8.8823 | 4.2987 | 3.5443 | 0.92097 | 0.00018797
| 418.15 | 900000 | 4296.2529 | 3548.8403 | 921.8915 | 0.00018937 | 145 | 8.8823 | 4.2963 | 3.5488 | 0.92189 | 0.00018937
| 417.15 | 900000 | 4293.8262 | 3553.4353 | 922.8069 | 0.00019079 | 144 | 8.8823 | 4.2938 | 3.5534 | 0.92281 | 0.00019079
| 416.15 | 900000 | 4291.4326 | 3558.0422 | 923.7178 | 0.00019223 | 143 | 8.8823 | 4.2914 | 3.558 | 0.92372 | 0.00019223
| 415.15 | 900000 | 4289.0713 | 3562.6614 | 924.6243 | 0.00019369 | 142 | 8.8823 | 4.2891 | 3.5627 | 0.92462 | 0.00019369
| 414.15 | 900000 | 4286.7422 | 3567.2925 | 925.5264 | 0.00019517 | 141 | 8.8823 | 4.2867 | 3.5673 | 0.92553 | 0.00019517
| 413.15 | 900000 | 4284.4443 | 3571.9355 | 926.4241 | 0.00019668 | 140 | 8.8823 | 4.2844 | 3.5719 | 0.92642 | 0.00019668
| 412.15 | 900000 | 4282.1782 | 3576.5906 | 927.3173 | 0.00019821 | 139 | 8.8823 | 4.2822 | 3.5766 | 0.92732 | 0.00019821
| 411.15 | 900000 | 4279.9424 | 3581.2573 | 928.2062 | 0.00019976 | 138 | 8.8823 | 4.2799 | 3.5813 | 0.92821 | 0.00019976
| 410.15 | 900000 | 4277.7373 | 3585.9358 | 929.0906 | 0.00020133 | 137 | 8.8823 | 4.2777 | 3.5859 | 0.92909 | 0.00020133
| 409.15 | 900000 | 4275.5625 | 3590.626 | 929.9706 | 0.00020293 | 136 | 8.8823 | 4.2756 | 3.5906 | 0.92997 | 0.00020293
| 408.15 | 900000 | 4273.417 | 3595.3279 | 930.8463 | 0.00020455 | 135 | 8.8823 | 4.2734 | 3.5953 | 0.93085 | 0.00020455
| 407.15 | 900000 | 4271.3013 | 3600.041 | 931.7176 | 0.0002062 | 134 | 8.8823 | 4.2713 | 3.6 | 0.93172 | 0.0002062
| 406.15 | 900000 | 4269.2144 | 3604.7656 | 932.5845 | 0.00020788 | 133 | 8.8823 | 4.2692 | 3.6048 | 0.93258 | 0.00020788
| 405.15 | 900000 | 4267.1558 | 3609.5017 | 933.447 | 0.00020958 | 132 | 8.8823 | 4.2672 | 3.6095 | 0.93345 | 0.00020958
| 404.15 | 900000 | 4265.126 | 3614.249 | 934.3051 | 0.0002113 | 131 | 8.8823 | 4.2651 | 3.6142 | 0.93431 | 0.0002113
| 403.15 | 900000 | 4263.124 | 3619.0076 | 935.1589 | 0.00021306 | 130 | 8.8823 | 4.2631 | 3.619 | 0.93516 | 0.00021306
| 402.15 | 900000 | 4261.1499 | 3623.7771 | 936.0082 | 0.00021484 | 129 | 8.8823 | 4.2611 | 3.6238 | 0.93601 | 0.00021484
| 401.15 | 900000 | 4259.2031 | 3628.5576 | 936.8533 | 0.00021665 | 128 | 8.8823 | 4.2592 | 3.6286 | 0.93685 | 0.00021665
| 400.15 | 900000 | 4257.2832 | 3633.3494 | 937.694 | 0.00021849 | 127 | 8.8823 | 4.2573 | 3.6333 | 0.93769 | 0.00021849
| 399.15 | 900000 | 4255.3901 | 3638.1519 | 938.5303 | 0.00022036 | 126 | 8.8823 | 4.2554 | 3.6382 | 0.93853 | 0.00022036
| 398.15 | 900000 | 4253.5239 | 3642.9651 | 939.3622 | 0.00022226 | 125 | 8.8823 | 4.2535 | 3.643 | 0.93936 | 0.00022226
| 397.15 | 900000 | 4251.6836 | 3647.7891 | 940.1898 | 0.00022419 | 124 | 8.8823 | 4.2517 | 3.6478 | 0.94019 | 0.00022419
| 396.15 | 900000 | 4249.8696 | 3652.6238 | 941.0129 | 0.00022615 | 123 | 8.8823 | 4.2499 | 3.6526 | 0.94101 | 0.00022615
| 395.15 | 900000 | 4248.0811 | 3657.469 | 941.8317 | 0.00022815 | 122 | 8.8823 | 4.2481 | 3.6575 | 0.94183 | 0.00022815
| 394.15 | 900000 | 4246.3184 | 3662.3247 | 942.6462 | 0.00023017 | 121 | 8.8823 | 4.2463 | 3.6623 | 0.94265 | 0.00023017
| 393.15 | 900000 | 4244.5806 | 3667.1907 | 943.4562 | 0.00023224 | 120 | 8.8823 | 4.2446 | 3.6672 | 0.94346 | 0.00023224
| 392.15 | 900000 | 4242.8677 | 3672.0669 | 944.2619 | 0.00023433 | 119 | 8.8823 | 4.2429 | 3.6721 | 0.94426 | 0.00023433
| 391.15 | 900000 | 4241.1797 | 3676.9534 | 945.0632 | 0.00023646 | 118 | 8.8823 | 4.2412 | 3.677 | 0.94506 | 0.00023646
| 390.15 | 900000 | 4239.5161 | 3681.8501 | 945.8601 | 0.00023863 | 117 | 8.8823 | 4.2395 | 3.6819 | 0.94586 | 0.00023863
| 389.15 | 900000 | 4237.877 | 3686.7566 | 946.6526 | 0.00024084 | 116 | 8.8823 | 4.2379 | 3.6868 | 0.94665 | 0.00024084
| 388.15 | 900000 | 4236.2622 | 3691.6733 | 947.4407 | 0.00024308 | 115 | 8.8823 | 4.2363 | 3.6917 | 0.94744 | 0.00024308
| 387.15 | 900000 | 4234.6709 | 3696.5996 | 948.2244 | 0.00024536 | 114 | 8.8823 | 4.2347 | 3.6966 | 0.94822 | 0.00024536
| 386.15 | 900000 | 4233.1035 | 3701.5356 | 949.0037 | 0.00024769 | 113 | 8.8823 | 4.2331 | 3.7015 | 0.949 | 0.00024769
| 385.15 | 900000 | 4231.5596 | 3706.4812 | 949.7786 | 0.00025005 | 112 | 8.8823 | 4.2316 | 3.7065 | 0.94978 | 0.00025005
| 384.15 | 900000 | 4230.0391 | 3711.4363 | 950.549 | 0.00025245 | 111 | 8.8823 | 4.23 | 3.7114 | 0.95055 | 0.00025245
| 383.15 | 900000 | 4228.5415 | 3716.4006 | 951.3149 | 0.0002549 | 110 | 8.8823 | 4.2285 | 3.7164 | 0.95131 | 0.0002549
| 382.15 | 900000 | 4227.0669 | 3721.3743 | 952.0765 | 0.00025739 | 109 | 8.8823 | 4.2271 | 3.7214 | 0.95208 | 0.00025739
| 381.15 | 900000 | 4225.6152 | 3726.3569 | 952.8336 | 0.00025993 | 108 | 8.8823 | 4.2256 | 3.7264 | 0.95283 | 0.00025993
| 380.15 | 900000 | 4224.1865 | 3731.3489 | 953.5862 | 0.00026251 | 107 | 8.8823 | 4.2242 | 3.7313 | 0.95359 | 0.00026251
| 379.15 | 900000 | 4222.7798 | 3736.3494 | 954.3343 | 0.00026514 | 106 | 8.8823 | 4.2228 | 3.7363 | 0.95433 | 0.00026514
| 378.15 | 900000 | 4221.396 | 3741.3586 | 955.0779 | 0.00026781 | 105 | 8.8823 | 4.2214 | 3.7414 | 0.95508 | 0.00026781
| 377.15 | 900000 | 4220.0342 | 3746.3765 | 955.8171 | 0.00027054 | 104 | 8.8823 | 4.22 | 3.7464 | 0.95582 | 0.00027054
| 376.15 | 900000 | 4218.6943 | 3751.4028 | 956.5517 | 0.00027331 | 103 | 8.8823 | 4.2187 | 3.7514 | 0.95655 | 0.00027331
| 375.15 | 900000 | 4217.377 | 3756.4373 | 957.2817 | 0.00027614 | 102 | 8.8823 | 4.2174 | 3.7564 | 0.95728 | 0.00027614
| 374.15 | 900000 | 4216.0811 | 3761.4797 | 958.0073 | 0.00027902 | 101 | 8.8823 | 4.2161 | 3.7615 | 0.95801 | 0.00027902
| 373.15 | 900000 | 4214.8066 | 3766.5303 | 958.7282 | 0.00028196 | 100 | 8.8823 | 4.2148 | 3.7665 | 0.95873 | 0.00028196
| 372.15 | 900000 | 4213.5542 | 3771.5886 | 959.4446 | 0.00028495 | 99 | 8.8823 | 4.2136 | 3.7716 | 0.95944 | 0.00028495
| 371.15 | 900000 | 4212.3232 | 3776.6543 | 960.1564 | 0.000288 | 98 | 8.8823 | 4.2123 | 3.7767 | 0.96016 | 0.000288
| 370.15 | 900000 | 4211.1138 | 3781.7275 | 960.8636 | 0.0002911 | 97 | 8.8823 | 4.2111 | 3.7817 | 0.96086 | 0.0002911
| 369.15 | 900000 | 4209.9258 | 3786.8079 | 961.5661 | 0.00029427 | 96 | 8.8823 | 4.2099 | 3.7868 | 0.96157 | 0.00029427
| 368.15 | 900000 | 4208.7593 | 3791.895 | 962.264 | 0.0002975 | 95 | 8.8823 | 4.2088 | 3.7919 | 0.96226 | 0.0002975
| 367.15 | 900000 | 4207.6133 | 3796.989 | 962.9572 | 0.00030079 | 94 | 8.8823 | 4.2076 | 3.797 | 0.96296 | 0.00030079
| 366.15 | 900000 | 4206.4888 | 3802.0896 | 963.6458 | 0.00030415 | 93 | 8.8823 | 4.2065 | 3.8021 | 0.96365 | 0.00030415
| 365.15 | 900000 | 4205.3853 | 3807.1963 | 964.3296 | 0.00030757 | 92 | 8.8823 | 4.2054 | 3.8072 | 0.96433 | 0.00030757
| 364.15 | 900000 | 4204.3027 | 3812.3093 | 965.0087 | 0.00031106 | 91 | 8.8823 | 4.2043 | 3.8123 | 0.96501 | 0.00031106
| 363.15 | 900000 | 4203.2412 | 3817.4277 | 965.683 | 0.00031463 | 90 | 8.8823 | 4.2032 | 3.8174 | 0.96568 | 0.00031463
| 362.15 | 900000 | 4202.2007 | 3822.5518 | 966.3526 | 0.00031826 | 89 | 8.8823 | 4.2022 | 3.8226 | 0.96635 | 0.00031826
| 361.15 | 900000 | 4201.1807 | 3827.6812 | 967.0174 | 0.00032197 | 88 | 8.8823 | 4.2012 | 3.8277 | 0.96702 | 0.00032197
| 360.15 | 900000 | 4200.1816 | 3832.8154 | 967.6773 | 0.00032575 | 87 | 8.8823 | 4.2002 | 3.8328 | 0.96768 | 0.00032575
| 359.15 | 900000 | 4199.2031 | 3837.9543 | 968.3324 | 0.00032962 | 86 | 8.8823 | 4.1992 | 3.838 | 0.96833 | 0.00032962
| 358.15 | 900000 | 4198.2456 | 3843.0974 | 968.9827 | 0.00033356 | 85 | 8.8823 | 4.1982 | 3.8431 | 0.96898 | 0.00033356
| 357.15 | 900000 | 4197.3086 | 3848.2446 | 969.628 | 0.00033759 | 84 | 8.8823 | 4.1973 | 3.8482 | 0.96963 | 0.00033759
| 356.15 | 900000 | 4196.3921 | 3853.3953 | 970.2684 | 0.0003417 | 83 | 8.8823 | 4.1964 | 3.8534 | 0.97027 | 0.0003417
| 355.15 | 900000 | 4195.4961 | 3858.5493 | 970.9038 | 0.00034589 | 82 | 8.8823 | 4.1955 | 3.8585 | 0.9709 | 0.00034589
| 354.15 | 900000 | 4194.6211 | 3863.7063 | 971.5342 | 0.00035018 | 81 | 8.8823 | 4.1946 | 3.8637 | 0.97153 | 0.00035018
| 353.15 | 900000 | 4193.7661 | 3868.8657 | 972.1597 | 0.00035456 | 80 | 8.8823 | 4.1938 | 3.8689 | 0.97216 | 0.00035456
| 352.15 | 900000 | 4192.9321 | 3874.0273 | 972.78 | 0.00035904 | 79 | 8.8823 | 4.1929 | 3.874 | 0.97278 | 0.00035904
| 351.15 | 900000 | 4192.1187 | 3879.1904 | 973.3953 | 0.00036361 | 78 | 8.8823 | 4.1921 | 3.8792 | 0.9734 | 0.00036361
| 350.15 | 900000 | 4191.3252 | 3884.355 | 974.0055 | 0.00036829 | 77 | 8.8823 | 4.1913 | 3.8844 | 0.97401 | 0.00036829
| 349.15 | 900000 | 4190.5527 | 3889.5203 | 974.6105 | 0.00037307 | 76 | 8.8823 | 4.1906 | 3.8895 | 0.97461 | 0.00037307
| 348.15 | 900000 | 4189.8008 | 3894.6858 | 975.2104 | 0.00037795 | 75 | 8.8823 | 4.1898 | 3.8947 | 0.97521 | 0.00037795
| 347.15 | 900000 | 4189.0693 | 3899.8511 | 975.805 | 0.00038295 | 74 | 8.8823 | 4.1891 | 3.8999 | 0.9758 | 0.00038295
| 346.15 | 900000 | 4188.3579 | 3905.0156 | 976.3943 | 0.00038806 | 73 | 8.8823 | 4.1884 | 3.905 | 0.97639 | 0.00038806
| 345.15 | 900000 | 4187.6675 | 3910.1792 | 976.9784 | 0.00039328 | 72 | 8.8823 | 4.1877 | 3.9102 | 0.97698 | 0.00039328
| 344.15 | 900000 | 4186.9976 | 3915.3406 | 977.5571 | 0.00039863 | 71 | 8.8823 | 4.187 | 3.9153 | 0.97756 | 0.00039863
| 343.15 | 900000 | 4186.3481 | 3920.5 | 978.1305 | 0.0004041 | 70 | 8.8823 | 4.1863 | 3.9205 | 0.97813 | 0.0004041
| 342.15 | 900000 | 4185.7192 | 3925.6562 | 978.6984 | 0.0004097 | 69 | 8.8823 | 4.1857 | 3.9257 | 0.9787 | 0.0004097
| 341.15 | 900000 | 4185.1108 | 3930.8088 | 979.2609 | 0.00041543 | 68 | 8.8823 | 4.1851 | 3.9308 | 0.97926 | 0.00041543
| 340.15 | 900000 | 4184.5229 | 3935.9573 | 979.8179 | 0.0004213 | 67 | 8.8823 | 4.1845 | 3.936 | 0.97982 | 0.0004213
| 339.15 | 900000 | 4183.9561 | 3941.1006 | 980.3693 | 0.0004273 | 66 | 8.8823 | 4.184 | 3.9411 | 0.98037 | 0.0004273
| 338.15 | 900000 | 4183.4097 | 3946.2385 | 980.9151 | 0.00043346 | 65 | 8.8823 | 4.1834 | 3.9462 | 0.98092 | 0.00043346
| 337.15 | 900000 | 4182.8838 | 3951.3699 | 981.4553 | 0.00043976 | 64 | 8.8823 | 4.1829 | 3.9514 | 0.98146 | 0.00043976
| 336.15 | 900000 | 4182.3784 | 3956.4944 | 981.9897 | 0.00044622 | 63 | 8.8823 | 4.1824 | 3.9565 | 0.98199 | 0.00044622
| 335.15 | 900000 | 4181.894 | 3961.6108 | 982.5185 | 0.00045284 | 62 | 8.8823 | 4.1819 | 3.9616 | 0.98252 | 0.00045284
| 334.15 | 900000 | 4181.4302 | 3966.7188 | 983.0414 | 0.00045962 | 61 | 8.8823 | 4.1814 | 3.9667 | 0.98304 | 0.00045962
| 333.15 | 900000 | 4180.9868 | 3971.8171 | 983.5585 | 0.00046658 | 60 | 8.8823 | 4.181 | 3.9718 | 0.98356 | 0.00046658
| 332.15 | 900000 | 4180.5649 | 3976.905 | 984.0697 | 0.00047371 | 59 | 8.8823 | 4.1806 | 3.9769 | 0.98407 | 0.00047371
| 331.15 | 900000 | 4180.1636 | 3981.9817 | 984.5749 | 0.00048103 | 58 | 8.8823 | 4.1802 | 3.982 | 0.98457 | 0.00048103
| 330.15 | 900000 | 4179.7827 | 3987.0464 | 985.0741 | 0.00048854 | 57 | 8.8823 | 4.1798 | 3.987 | 0.98507 | 0.00048854
| 329.15 | 900000 | 4179.4233 | 3992.0977 | 985.5672 | 0.00049624 | 56 | 8.8823 | 4.1794 | 3.9921 | 0.98557 | 0.00049624
| 328.15 | 900000 | 4179.085 | 3997.135 | 986.0541 | 0.00050414 | 55 | 8.8823 | 4.1791 | 3.9971 | 0.98605 | 0.00050414
| 327.15 | 900000 | 4178.7671 | 4002.1572 | 986.5349 | 0.00051226 | 54 | 8.8823 | 4.1788 | 4.0022 | 0.98653 | 0.00051226
| 326.15 | 900000 | 4178.4707 | 4007.1631 | 987.0094 | 0.0005206 | 53 | 8.8823 | 4.1785 | 4.0072 | 0.98701 | 0.0005206
| 325.15 | 900000 | 4178.1958 | 4012.1519 | 987.4775 | 0.00052916 | 52 | 8.8823 | 4.1782 | 4.0122 | 0.98748 | 0.00052916
| 324.15 | 900000 | 4177.9419 | 4017.1221 | 987.9393 | 0.00053795 | 51 | 8.8823 | 4.1779 | 4.0171 | 0.98794 | 0.00053795
| 323.15 | 900000 | 4177.709 | 4022.073 | 988.3945 | 0.00054699 | 50 | 8.8823 | 4.1777 | 4.0221 | 0.98839 | 0.00054699
| 322.15 | 900000 | 4177.498 | 4027.0032 | 988.8433 | 0.00055628 | 49 | 8.8823 | 4.1775 | 4.027 | 0.98884 | 0.00055628
| 321.15 | 900000 | 4177.3081 | 4031.9114 | 989.2853 | 0.00056584 | 48 | 8.8823 | 4.1773 | 4.0319 | 0.98929 | 0.00056584
| 320.15 | 900000 | 4177.1406 | 4036.7966 | 989.7207 | 0.00057566 | 47 | 8.8823 | 4.1771 | 4.0368 | 0.98972 | 0.00057566
| 319.15 | 900000 | 4176.9946 | 4041.6572 | 990.1493 | 0.00058577 | 46 | 8.8823 | 4.177 | 4.0417 | 0.99015 | 0.00058577
| 318.15 | 900000 | 4176.8701 | 4046.4922 | 990.571 | 0.00059618 | 45 | 8.8823 | 4.1769 | 4.0465 | 0.99057 | 0.00059618
| 317.15 | 900000 | 4176.7686 | 4051.3003 | 990.9858 | 0.00060689 | 44 | 8.8823 | 4.1768 | 4.0513 | 0.99099 | 0.00060689
| 316.15 | 900000 | 4176.689 | 4056.0796 | 991.3935 | 0.00061791 | 43 | 8.8823 | 4.1767 | 4.0561 | 0.99139 | 0.00061791
| 315.15 | 900000 | 4176.6323 | 4060.8293 | 991.7941 | 0.00062927 | 42 | 8.8823 | 4.1766 | 4.0608 | 0.99179 | 0.00062927
| 314.15 | 900000 | 4176.5981 | 4065.5476 | 992.1874 | 0.00064098 | 41 | 8.8823 | 4.1766 | 4.0655 | 0.99219 | 0.00064098
| 313.15 | 900000 | 4176.5874 | 4070.2329 | 992.5734 | 0.00065304 | 40 | 8.8823 | 4.1766 | 4.0702 | 0.99257 | 0.00065304
| 312.15 | 900000 | 4176.6006 | 4074.8843 | 992.952 | 0.00066548 | 39 | 8.8823 | 4.1766 | 4.0749 | 0.99295 | 0.00066548
| 311.15 | 900000 | 4176.6372 | 4079.4998 | 993.3231 | 0.00067831 | 38 | 8.8823 | 4.1766 | 4.0795 | 0.99332 | 0.00067831
| 310.15 | 900000 | 4176.6982 | 4084.0776 | 993.6866 | 0.00069155 | 37 | 8.8823 | 4.1767 | 4.0841 | 0.99369 | 0.00069155
| 309.15 | 900000 | 4176.7842 | 4088.6167 | 994.0422 | 0.00070521 | 36 | 8.8823 | 4.1768 | 4.0886 | 0.99404 | 0.00070521
| 308.15 | 900000 | 4176.8955 | 4093.1152 | 994.3901 | 0.00071932 | 35 | 8.8823 | 4.1769 | 4.0931 | 0.99439 | 0.00071932
| 307.15 | 900000 | 4177.0332 | 4097.5718 | 994.7299 | 0.00073389 | 34 | 8.8823 | 4.177 | 4.0976 | 0.99473 | 0.00073389
| 306.15 | 900000 | 4177.1973 | 4101.9839 | 995.0616 | 0.00074895 | 33 | 8.8823 | 4.1772 | 4.102 | 0.99506 | 0.00074895
| 305.15 | 900000 | 4177.3892 | 4106.3511 | 995.3851 | 0.00076452 | 32 | 8.8823 | 4.1774 | 4.1064 | 0.99539 | 0.00076452
| 304.15 | 900000 | 4177.6094 | 4110.6709 | 995.7003 | 0.00078061 | 31 | 8.8823 | 4.1776 | 4.1107 | 0.9957 | 0.00078061
| 303.15 | 900000 | 4177.8594 | 4114.9419 | 996.0069 | 0.00079727 | 30 | 8.8823 | 4.1779 | 4.1149 | 0.99601 | 0.00079727
| 302.15 | 900000 | 4178.1396 | 4119.1621 | 996.3049 | 0.00081451 | 29 | 8.8823 | 4.1781 | 4.1192 | 0.9963 | 0.00081451
| 301.15 | 900000 | 4178.4521 | 4123.3301 | 996.5941 | 0.00083236 | 28 | 8.8823 | 4.1785 | 4.1233 | 0.99659 | 0.00083236
| 300.15 | 900000 | 4178.7979 | 4127.4438 | 996.8743 | 0.00085085 | 27 | 8.8823 | 4.1788 | 4.1274 | 0.99687 | 0.00085085
| 299.15 | 900000 | 4179.1782 | 4131.5024 | 997.1455 | 0.00087002 | 26 | 8.8823 | 4.1792 | 4.1315 | 0.99715 | 0.00087002
| 298.15 | 900000 | 4179.5957 | 4135.5034 | 997.4073 | 0.0008899 | 25 | 8.8823 | 4.1796 | 4.1355 | 0.99741 | 0.0008899
| 297.15 | 900000 | 4180.0518 | 4139.4453 | 997.6597 | 0.00091052 | 24 | 8.8823 | 4.1801 | 4.1394 | 0.99766 | 0.00091052
| 296.15 | 900000 | 4180.5493 | 4143.3262 | 997.9025 | 0.00093192 | 23 | 8.8823 | 4.1805 | 4.1433 | 0.9979 | 0.00093192
| 295.15 | 900000 | 4181.0903 | 4147.1455 | 998.1355 | 0.00095415 | 22 | 8.8823 | 4.1811 | 4.1471 | 0.99814 | 0.00095415
| 294.15 | 900000 | 4181.6777 | 4150.9004 | 998.3584 | 0.00097725 | 21 | 8.8823 | 4.1817 | 4.1509 | 0.99836 | 0.00097725
| 293.15 | 900000 | 4182.3145 | 4154.5898 | 998.5711 | 0.0010013 | 20 | 8.8823 | 4.1823 | 4.1546 | 0.99857 | 0.0010013
| 292.15 | 900000 | 4183.0049 | 4158.2129 | 998.7734 | 0.0010262 | 19 | 8.8823 | 4.183 | 4.1582 | 0.99877 | 0.0010262
| 291.15 | 900000 | 4183.752 | 4161.7676 | 998.965 | 0.0010523 | 18 | 8.8823 | 4.1838 | 4.1618 | 0.99897 | 0.0010523
| 290.15 | 900000 | 4184.5605 | 4165.2524 | 999.1457 | 0.0010793 | 17 | 8.8823 | 4.1846 | 4.1653 | 0.99915 | 0.0010793
| 289.15 | 900000 | 4185.4355 | 4168.667 | 999.3152 | 0.0011076 | 16 | 8.8823 | 4.1854 | 4.1687 | 0.99932 | 0.0011076
| 288.15 | 900000 | 4186.3823 | 4172.0093 | 999.4734 | 0.001137 | 15 | 8.8823 | 4.1864 | 4.172 | 0.99947 | 0.001137
| 287.15 | 900000 | 4187.4072 | 4175.2783 | 999.6198 | 0.0011677 | 14 | 8.8823 | 4.1874 | 4.1753 | 0.99962 | 0.0011677
| 286.15 | 900000 | 4188.5161 | 4178.4741 | 999.7543 | 0.0011998 | 13 | 8.8823 | 4.1885 | 4.1785 | 0.99975 | 0.0011998
| 285.15 | 900000 | 4189.7173 | 4181.5952 | 999.8765 | 0.0012333 | 12 | 8.8823 | 4.1897 | 4.1816 | 0.99988 | 0.0012333
| 284.15 | 900000 | 4191.0186 | 4184.6406 | 999.9861 | 0.0012683 | 11 | 8.8823 | 4.191 | 4.1846 | 0.99999 | 0.0012683
| 283.15 | 900000 | 4192.4297 | 4187.6108 | 1000.0828 | 0.001305 | 10 | 8.8823 | 4.1924 | 4.1876 | 1.0001 | 0.001305
| 282.15 | 900000 | 4193.9604 | 4190.5049 | 1000.1662 | 0.0013434 | 9 | 8.8823 | 4.194 | 4.1905 | 1.0002 | 0.0013434
| 281.15 | 900000 | 4195.6216 | 4193.3232 | 1000.236 | 0.0013837 | 8 | 8.8823 | 4.1956 | 4.1933 | 1.0002 | 0.0013837
| 280.15 | 900000 | 4197.4268 | 4196.0659 | 1000.2916 | 0.0014259 | 7 | 8.8823 | 4.1974 | 4.1961 | 1.0003 | 0.0014259
| 279.15 | 900000 | 4199.3892 | 4198.7329 | 1000.3329 | 0.0014702 | 6 | 8.8823 | 4.1994 | 4.1987 | 1.0003 | 0.0014702
| 278.15 | 900000 | 4201.5244 | 4201.3257 | 1000.3593 | 0.0015168 | 5 | 8.8823 | 4.2015 | 4.2013 | 1.0004 | 0.0015168
| 277.15 | 900000 | 4203.8496 | 4203.8442 | 1000.3702 | 0.0015658 | 4 | 8.8823 | 4.2038 | 4.2038 | 1.0004 | 0.0015658
| 276.15 | 900000 | 4206.3833 | 4206.29 | 1000.3654 | 0.0016174 | 3 | 8.8823 | 4.2064 | 4.2063 | 1.0004 | 0.0016174
| 275.15 | 900000 | 4209.147 | 4208.665 | 1000.3441 | 0.0016717 | 2 | 8.8823 | 4.2091 | 4.2087 | 1.0003 | 0.0016717
| 274.15 | 900000 | 4212.1626 | 4210.9702 | 1000.306 | 0.001729 | 0.99999 | 8.8823 | 4.2122 | 4.211 | 1.0003 | 0.001729
| 273.15 | 900000 | 4215.457 | 4213.2085 | 1000.2502 | 0.0017895 | -6.1035e-06 | 8.8823 | 4.2155 | 4.2132 | 1.0003 | 0.0017895
| 473.15 | 800000 | 2303.0095 | 1683.7325 | 3.8334 | 1.5957e-05 | 200 | 7.8954 | 2.303 | 1.6837 | 0.0038334 | 1.5957e-05
| 472.15 | 800000 | 2308.1306 | 1686.6125 | 3.8432 | 1.5915e-05 | 199 | 7.8954 | 2.3081 | 1.6866 | 0.0038432 | 1.5915e-05
| 471.15 | 800000 | 2313.3992 | 1689.5863 | 3.8532 | 1.5872e-05 | 198 | 7.8954 | 2.3134 | 1.6896 | 0.0038532 | 1.5872e-05
| 470.15 | 800000 | 2318.8235 | 1692.6594 | 3.8632 | 1.5829e-05 | 197 | 7.8954 | 2.3188 | 1.6927 | 0.0038632 | 1.5829e-05
| 469.15 | 800000 | 2324.4128 | 1695.8381 | 3.8733 | 1.5787e-05 | 196 | 7.8954 | 2.3244 | 1.6958 | 0.0038733 | 1.5787e-05
| 468.15 | 800000 | 2330.1772 | 1699.1298 | 3.8834 | 1.5744e-05 | 195 | 7.8954 | 2.3302 | 1.6991 | 0.0038834 | 1.5744e-05
| 467.15 | 800000 | 2336.1282 | 1702.5422 | 3.8937 | 1.5702e-05 | 194 | 7.8954 | 2.3361 | 1.7025 | 0.0038937 | 1.5702e-05
| 466.15 | 800000 | 2342.2778 | 1706.0841 | 3.904 | 1.5659e-05 | 193 | 7.8954 | 2.3423 | 1.7061 | 0.003904 | 1.5659e-05
| 465.15 | 800000 | 2348.6406 | 1709.7655 | 3.9144 | 1.5616e-05 | 192 | 7.8954 | 2.3486 | 1.7098 | 0.0039144 | 1.5616e-05
| 464.15 | 800000 | 2355.2322 | 1713.5975 | 3.9248 | 1.5574e-05 | 191 | 7.8954 | 2.3552 | 1.7136 | 0.0039248 | 1.5574e-05
| 463.15 | 800000 | 2362.0698 | 1717.5928 | 3.9354 | 1.5531e-05 | 190 | 7.8954 | 2.3621 | 1.7176 | 0.0039354 | 1.5531e-05
| 462.15 | 800000 | 2369.1736 | 1721.7651 | 3.946 | 1.5489e-05 | 189 | 7.8954 | 2.3692 | 1.7218 | 0.003946 | 1.5489e-05
| 461.15 | 800000 | 2376.5657 | 1726.1305 | 3.9567 | 1.5446e-05 | 188 | 7.8954 | 2.3766 | 1.7261 | 0.0039567 | 1.5446e-05
| 460.15 | 800000 | 2384.2708 | 1730.7068 | 3.9675 | 1.5403e-05 | 187 | 7.8954 | 2.3843 | 1.7307 | 0.0039675 | 1.5403e-05
| 459.15 | 800000 | 2392.3169 | 1735.5142 | 3.9784 | 1.5361e-05 | 186 | 7.8954 | 2.3923 | 1.7355 | 0.0039784 | 1.5361e-05
| 458.15 | 800000 | 2400.7363 | 1740.5754 | 3.9893 | 1.5318e-05 | 185 | 7.8954 | 2.4007 | 1.7406 | 0.0039893 | 1.5318e-05
| 457.15 | 800000 | 2409.5642 | 1745.9163 | 4.0004 | 1.5275e-05 | 184 | 7.8954 | 2.4096 | 1.7459 | 0.0040004 | 1.5275e-05
| 456.15 | 800000 | 2418.8416 | 1751.5658 | 4.0116 | 1.5233e-05 | 183 | 7.8954 | 2.4188 | 1.7516 | 0.0040116 | 1.5233e-05
| 455.15 | 800000 | 2428.614 | 1757.5571 | 4.0228 | 1.519e-05 | 182 | 7.8954 | 2.4286 | 1.7576 | 0.0040228 | 1.519e-05
| 454.15 | 800000 | 2438.9333 | 1763.9275 | 4.0341 | 1.5148e-05 | 181 | 7.8954 | 2.4389 | 1.7639 | 0.0040341 | 1.5148e-05
| 453.15 | 800000 | 2449.8584 | 1770.7194 | 4.0456 | 1.5105e-05 | 180 | 7.8954 | 2.4499 | 1.7707 | 0.0040456 | 1.5105e-05
| 452.15 | 800000 | 2461.4561 | 1777.9807 | 4.0571 | 1.5062e-05 | 179 | 7.8954 | 2.4615 | 1.778 | 0.0040571 | 1.5062e-05
| 451.15 | 800000 | 2473.802 | 1785.7661 | 4.0688 | 1.502e-05 | 178 | 7.8954 | 2.4738 | 1.7858 | 0.0040688 | 1.502e-05
| 450.15 | 800000 | 2486.9822 | 1794.1372 | 4.0805 | 1.4977e-05 | 177 | 7.8954 | 2.487 | 1.7941 | 0.0040805 | 1.4977e-05
| 449.15 | 800000 | 2501.0947 | 1803.1643 | 4.0924 | 1.4934e-05 | 176 | 7.8954 | 2.5011 | 1.8032 | 0.0040924 | 1.4934e-05
| 448.15 | 800000 | 2516.2505 | 1812.927 | 4.1044 | 1.4891e-05 | 175 | 7.8954 | 2.5163 | 1.8129 | 0.0041044 | 1.4891e-05
| 447.15 | 800000 | 2532.5759 | 1823.516 | 4.1165 | 1.4849e-05 | 174 | 7.8954 | 2.5326 | 1.8235 | 0.0041165 | 1.4849e-05
| 446.15 | 800000 | 2550.2156 | 1835.0339 | 4.1287 | 1.4806e-05 | 173 | 7.8954 | 2.5502 | 1.835 | 0.0041287 | 1.4806e-05
| 445.15 | 800000 | 2569.3333 | 1847.5974 | 4.1411 | 1.4763e-05 | 172 | 7.8954 | 2.5693 | 1.8476 | 0.0041411 | 1.4763e-05
| 444.15 | 800000 | 2590.116 | 1861.3394 | 4.1536 | 1.4721e-05 | 171 | 7.8954 | 2.5901 | 1.8613 | 0.0041536 | 1.4721e-05
| 443.15 | 800000 | 4369.4668 | 3438.2539 | 897.4597 | 0.00015955 | 170 | 7.8954 | 4.3695 | 3.4383 | 0.89746 | 0.00015955
| 442.15 | 800000 | 4366.0435 | 3442.5171 | 898.4913 | 0.00016057 | 169 | 7.8954 | 4.366 | 3.4425 | 0.89849 | 0.00016057
| 441.15 | 800000 | 4362.668 | 3446.7947 | 899.518 | 0.00016159 | 168 | 7.8954 | 4.3627 | 3.4468 | 0.89952 | 0.00016159
| 440.15 | 800000 | 4359.3384 | 3451.0864 | 900.5399 | 0.00016263 | 167 | 7.8954 | 4.3593 | 3.4511 | 0.90054 | 0.00016263
| 439.15 | 800000 | 4356.0547 | 3455.3926 | 901.5569 | 0.00016368 | 166 | 7.8954 | 4.3561 | 3.4554 | 0.90156 | 0.00016368
| 438.15 | 800000 | 4352.8164 | 3459.7126 | 902.5692 | 0.00016475 | 165 | 7.8954 | 4.3528 | 3.4597 | 0.90257 | 0.00016475
| 437.15 | 800000 | 4349.6221 | 3464.0469 | 903.5767 | 0.00016583 | 164 | 7.8954 | 4.3496 | 3.464 | 0.90358 | 0.00016583
| 436.15 | 800000 | 4346.4722 | 3468.3948 | 904.5794 | 0.00016692 | 163 | 7.8954 | 4.3465 | 3.4684 | 0.90458 | 0.00016692
| 435.15 | 800000 | 4343.3647 | 3472.7568 | 905.5774 | 0.00016803 | 162 | 7.8954 | 4.3434 | 3.4728 | 0.90558 | 0.00016803
| 434.15 | 800000 | 4340.2998 | 3477.1323 | 906.5707 | 0.00016915 | 161 | 7.8954 | 4.3403 | 3.4771 | 0.90657 | 0.00016915
| 433.15 | 800000 | 4337.2769 | 3481.5215 | 907.5593 | 0.00017029 | 160 | 7.8954 | 4.3373 | 3.4815 | 0.90756 | 0.00017029
| 432.15 | 800000 | 4334.2954 | 3485.9243 | 908.5432 | 0.00017144 | 159 | 7.8954 | 4.3343 | 3.4859 | 0.90854 | 0.00017144
| 431.15 | 800000 | 4331.354 | 3490.3406 | 909.5224 | 0.00017261 | 158 | 7.8954 | 4.3314 | 3.4903 | 0.90952 | 0.00017261
| 430.15 | 800000 | 4328.4531 | 3494.7703 | 910.497 | 0.00017379 | 157 | 7.8954 | 4.3285 | 3.4948 | 0.9105 | 0.00017379
| 429.15 | 800000 | 4325.5913 | 3499.2131 | 911.467 | 0.00017499 | 156 | 7.8954 | 4.3256 | 3.4992 | 0.91147 | 0.00017499
| 428.15 | 800000 | 4322.7686 | 3503.6692 | 912.4324 | 0.0001762 | 155 | 7.8954 | 4.3228 | 3.5037 | 0.91243 | 0.0001762
| 427.15 | 800000 | 4319.9839 | 3508.1382 | 913.3931 | 0.00017744 | 154 | 7.8954 | 4.32 | 3.5081 | 0.91339 | 0.00017744
| 426.15 | 800000 | 4317.2373 | 3512.6204 | 914.3494 | 0.00017869 | 153 | 7.8954 | 4.3172 | 3.5126 | 0.91435 | 0.00017869
| 425.15 | 800000 | 4314.5278 | 3517.1155 | 915.301 | 0.00017995 | 152 | 7.8954 | 4.3145 | 3.5171 | 0.9153 | 0.00017995
| 424.15 | 800000 | 4311.855 | 3521.6235 | 916.2481 | 0.00018124 | 151 | 7.8954 | 4.3119 | 3.5216 | 0.91625 | 0.00018124
| 423.15 | 800000 | 4309.2188 | 3526.144 | 917.1907 | 0.00018254 | 150 | 7.8954 | 4.3092 | 3.5261 | 0.91719 | 0.00018254
| 422.15 | 800000 | 4306.6177 | 3530.6775 | 918.1287 | 0.00018386 | 149 | 7.8954 | 4.3066 | 3.5307 | 0.91813 | 0.00018386
| 421.15 | 800000 | 4304.0522 | 3535.2234 | 919.0623 | 0.0001852 | 148 | 7.8954 | 4.3041 | 3.5352 | 0.91906 | 0.0001852
| 420.15 | 800000 | 4301.5215 | 3539.782 | 919.9913 | 0.00018656 | 147 | 7.8954 | 4.3015 | 3.5398 | 0.91999 | 0.00018656
| 419.15 | 800000 | 4299.0249 | 3544.3528 | 920.916 | 0.00018794 | 146 | 7.8954 | 4.299 | 3.5444 | 0.92092 | 0.00018794
| 418.15 | 800000 | 4296.562 | 3548.9363 | 921.8361 | 0.00018934 | 145 | 7.8954 | 4.2966 | 3.5489 | 0.92184 | 0.00018934
| 417.15 | 800000 | 4294.1328 | 3553.5317 | 922.7517 | 0.00019076 | 144 | 7.8954 | 4.2941 | 3.5535 | 0.92275 | 0.00019076
| 416.15 | 800000 | 4291.7363 | 3558.1394 | 923.6629 | 0.0001922 | 143 | 7.8954 | 4.2917 | 3.5581 | 0.92366 | 0.0001922
| 415.15 | 800000 | 4289.3726 | 3562.7593 | 924.5696 | 0.00019366 | 142 | 7.8954 | 4.2894 | 3.5628 | 0.92457 | 0.00019366
| 414.15 | 800000 | 4287.0405 | 3567.3914 | 925.472 | 0.00019515 | 141 | 7.8954 | 4.287 | 3.5674 | 0.92547 | 0.00019515
| 413.15 | 800000 | 4284.7402 | 3572.0352 | 926.3699 | 0.00019665 | 140 | 7.8954 | 4.2847 | 3.572 | 0.92637 | 0.00019665
| 412.15 | 800000 | 4282.4717 | 3576.6909 | 927.2634 | 0.00019818 | 139 | 7.8954 | 4.2825 | 3.5767 | 0.92726 | 0.00019818
| 411.15 | 800000 | 4280.2334 | 3581.3586 | 928.1525 | 0.00019973 | 138 | 7.8954 | 4.2802 | 3.5814 | 0.92815 | 0.00019973
| 410.15 | 800000 | 4278.0259 | 3586.0381 | 929.0371 | 0.00020131 | 137 | 7.8954 | 4.278 | 3.586 | 0.92904 | 0.00020131
| 409.15 | 800000 | 4275.8486 | 3590.729 | 929.9174 | 0.00020291 | 136 | 7.8954 | 4.2758 | 3.5907 | 0.92992 | 0.00020291
| 408.15 | 800000 | 4273.7012 | 3595.4316 | 930.7933 | 0.00020453 | 135 | 7.8954 | 4.2737 | 3.5954 | 0.93079 | 0.00020453
| 407.15 | 800000 | 4271.5825 | 3600.1458 | 931.6648 | 0.00020618 | 134 | 7.8954 | 4.2716 | 3.6001 | 0.93166 | 0.00020618
| 406.15 | 800000 | 4269.4937 | 3604.8713 | 932.5319 | 0.00020785 | 133 | 7.8954 | 4.2695 | 3.6049 | 0.93253 | 0.00020785
| 405.15 | 800000 | 4267.4331 | 3609.6084 | 933.3947 | 0.00020955 | 132 | 7.8954 | 4.2674 | 3.6096 | 0.93339 | 0.00020955
| 404.15 | 800000 | 4265.4009 | 3614.3567 | 934.253 | 0.00021128 | 131 | 7.8954 | 4.2654 | 3.6144 | 0.93425 | 0.00021128
| 403.15 | 800000 | 4263.397 | 3619.116 | 935.1069 | 0.00021303 | 130 | 7.8954 | 4.2634 | 3.6191 | 0.93511 | 0.00021303
| 402.15 | 800000 | 4261.4209 | 3623.8867 | 935.9565 | 0.00021481 | 129 | 7.8954 | 4.2614 | 3.6239 | 0.93596 | 0.00021481
| 401.15 | 800000 | 4259.4722 | 3628.6682 | 936.8018 | 0.00021662 | 128 | 7.8954 | 4.2595 | 3.6287 | 0.9368 | 0.00021662
| 400.15 | 800000 | 4257.5503 | 3633.4609 | 937.6426 | 0.00021846 | 127 | 7.8954 | 4.2576 | 3.6335 | 0.93764 | 0.00021846
| 399.15 | 800000 | 4255.6558 | 3638.2644 | 938.4792 | 0.00022033 | 126 | 7.8954 | 4.2557 | 3.6383 | 0.93848 | 0.00022033
| 398.15 | 800000 | 4253.7871 | 3643.0789 | 939.3113 | 0.00022223 | 125 | 7.8954 | 4.2538 | 3.6431 | 0.93931 | 0.00022223
| 397.15 | 800000 | 4251.9453 | 3647.9038 | 940.139 | 0.00022416 | 124 | 7.8954 | 4.2519 | 3.6479 | 0.94014 | 0.00022416
| 396.15 | 800000 | 4250.1294 | 3652.7395 | 940.9624 | 0.00022612 | 123 | 7.8954 | 4.2501 | 3.6527 | 0.94096 | 0.00022612
| 395.15 | 800000 | 4248.3394 | 3657.5859 | 941.7814 | 0.00022812 | 122 | 7.8954 | 4.2483 | 3.6576 | 0.94178 | 0.00022812
| 394.15 | 800000 | 4246.5747 | 3662.4426 | 942.5961 | 0.00023015 | 121 | 7.8954 | 4.2466 | 3.6624 | 0.9426 | 0.00023015
| 393.15 | 800000 | 4244.8354 | 3667.3098 | 943.4063 | 0.00023221 | 120 | 7.8954 | 4.2448 | 3.6673 | 0.94341 | 0.00023221
| 392.15 | 800000 | 4243.1211 | 3672.1875 | 944.2122 | 0.00023431 | 119 | 7.8954 | 4.2431 | 3.6722 | 0.94421 | 0.00023431
| 391.15 | 800000 | 4241.4312 | 3677.0752 | 945.0136 | 0.00023644 | 118 | 7.8954 | 4.2414 | 3.6771 | 0.94501 | 0.00023644
| 390.15 | 800000 | 4239.7661 | 3681.9729 | 945.8107 | 0.00023861 | 117 | 7.8954 | 4.2398 | 3.682 | 0.94581 | 0.00023861
| 389.15 | 800000 | 4238.1255 | 3686.8809 | 946.6034 | 0.00024081 | 116 | 7.8954 | 4.2381 | 3.6869 | 0.9466 | 0.00024081
| 388.15 | 800000 | 4236.5093 | 3691.7986 | 947.3917 | 0.00024306 | 115 | 7.8954 | 4.2365 | 3.6918 | 0.94739 | 0.00024306
| 387.15 | 800000 | 4234.9165 | 3696.7261 | 948.1755 | 0.00024534 | 114 | 7.8954 | 4.2349 | 3.6967 | 0.94818 | 0.00024534
| 386.15 | 800000 | 4233.3477 | 3701.6633 | 948.955 | 0.00024766 | 113 | 7.8954 | 4.2333 | 3.7017 | 0.94895 | 0.00024766
| 385.15 | 800000 | 4231.8022 | 3706.6104 | 949.73 | 0.00025002 | 112 | 7.8954 | 4.2318 | 3.7066 | 0.94973 | 0.00025002
| 384.15 | 800000 | 4230.2808 | 3711.5667 | 950.5006 | 0.00025243 | 111 | 7.8954 | 4.2303 | 3.7116 | 0.9505 | 0.00025243
| 383.15 | 800000 | 4228.7817 | 3716.5325 | 951.2667 | 0.00025487 | 110 | 7.8954 | 4.2288 | 3.7165 | 0.95127 | 0.00025487
| 382.15 | 800000 | 4227.3062 | 3721.5076 | 952.0284 | 0.00025736 | 109 | 7.8954 | 4.2273 | 3.7215 | 0.95203 | 0.00025736
| 381.15 | 800000 | 4225.8535 | 3726.4917 | 952.7856 | 0.0002599 | 108 | 7.8954 | 4.2259 | 3.7265 | 0.95279 | 0.0002599
| 380.15 | 800000 | 4224.4233 | 3731.4849 | 953.5385 | 0.00026248 | 107 | 7.8954 | 4.2244 | 3.7315 | 0.95354 | 0.00026248
| 379.15 | 800000 | 4223.0156 | 3736.4868 | 954.2867 | 0.00026511 | 106 | 7.8954 | 4.223 | 3.7365 | 0.95429 | 0.00026511
| 378.15 | 800000 | 4221.6304 | 3741.4976 | 955.0305 | 0.00026779 | 105 | 7.8954 | 4.2216 | 3.7415 | 0.95503 | 0.00026779
| 377.15 | 800000 | 4220.2676 | 3746.5168 | 955.7697 | 0.00027051 | 104 | 7.8954 | 4.2203 | 3.7465 | 0.95577 | 0.00027051
| 376.15 | 800000 | 4218.9272 | 3751.5444 | 956.5045 | 0.00027329 | 103 | 7.8954 | 4.2189 | 3.7515 | 0.9565 | 0.00027329
| 375.15 | 800000 | 4217.6084 | 3756.5806 | 957.2347 | 0.00027612 | 102 | 7.8954 | 4.2176 | 3.7566 | 0.95723 | 0.00027612
| 374.15 | 800000 | 4216.3115 | 3761.6248 | 957.9603 | 0.000279 | 101 | 7.8954 | 4.2163 | 3.7616 | 0.95796 | 0.000279
| 373.15 | 800000 | 4215.0366 | 3766.6768 | 958.6815 | 0.00028193 | 100 | 7.8954 | 4.215 | 3.7667 | 0.95868 | 0.00028193
| 372.15 | 800000 | 4213.7832 | 3771.7366 | 959.3979 | 0.00028492 | 99 | 7.8954 | 4.2138 | 3.7717 | 0.9594 | 0.00028492
| 371.15 | 800000 | 4212.5513 | 3776.804 | 960.1099 | 0.00028797 | 98 | 7.8954 | 4.2126 | 3.7768 | 0.96011 | 0.00028797
| 370.15 | 800000 | 4211.3413 | 3781.8787 | 960.8172 | 0.00029108 | 97 | 7.8954 | 4.2113 | 3.7819 | 0.96082 | 0.00029108
| 369.15 | 800000 | 4210.1523 | 3786.9607 | 961.5198 | 0.00029424 | 96 | 7.8954 | 4.2102 | 3.787 | 0.96152 | 0.00029424
| 368.15 | 800000 | 4208.9849 | 3792.0496 | 962.2178 | 0.00029747 | 95 | 7.8954 | 4.209 | 3.792 | 0.96222 | 0.00029747
| 367.15 | 800000 | 4207.8384 | 3797.1453 | 962.9112 | 0.00030077 | 94 | 7.8954 | 4.2078 | 3.7971 | 0.96291 | 0.00030077
| 366.15 | 800000 | 4206.7134 | 3802.2476 | 963.5999 | 0.00030412 | 93 | 7.8954 | 4.2067 | 3.8022 | 0.9636 | 0.00030412
| 365.15 | 800000 | 4205.6089 | 3807.356 | 964.2838 | 0.00030755 | 92 | 7.8954 | 4.2056 | 3.8074 | 0.96428 | 0.00030755
| 364.15 | 800000 | 4204.5259 | 3812.4705 | 964.963 | 0.00031104 | 91 | 7.8954 | 4.2045 | 3.8125 | 0.96496 | 0.00031104
| 363.15 | 800000 | 4203.4639 | 3817.5908 | 965.6375 | 0.0003146 | 90 | 7.8954 | 4.2035 | 3.8176 | 0.96564 | 0.0003146
| 362.15 | 800000 | 4202.4224 | 3822.7168 | 966.3071 | 0.00031823 | 89 | 7.8954 | 4.2024 | 3.8227 | 0.96631 | 0.00031823
| 361.15 | 800000 | 4201.4023 | 3827.8479 | 966.972 | 0.00032194 | 88 | 7.8954 | 4.2014 | 3.8278 | 0.96697 | 0.00032194
| 360.15 | 800000 | 4200.4023 | 3832.9839 | 967.6321 | 0.00032573 | 87 | 7.8954 | 4.2004 | 3.833 | 0.96763 | 0.00032573
| 359.15 | 800000 | 4199.4238 | 3838.1245 | 968.2872 | 0.00032959 | 86 | 7.8954 | 4.1994 | 3.8381 | 0.96829 | 0.00032959
| 358.15 | 800000 | 4198.4658 | 3843.2698 | 968.9376 | 0.00033353 | 85 | 7.8954 | 4.1985 | 3.8433 | 0.96894 | 0.00033353
| 357.15 | 800000 | 4197.5283 | 3848.4187 | 969.583 | 0.00033756 | 84 | 7.8954 | 4.1975 | 3.8484 | 0.96958 | 0.00033756
| 356.15 | 800000 | 4196.6113 | 3853.5713 | 970.2234 | 0.00034167 | 83 | 7.8954 | 4.1966 | 3.8536 | 0.97022 | 0.00034167
| 355.15 | 800000 | 4195.7153 | 3858.7273 | 970.859 | 0.00034587 | 82 | 7.8954 | 4.1957 | 3.8587 | 0.97086 | 0.00034587
| 354.15 | 800000 | 4194.8398 | 3863.8862 | 971.4895 | 0.00035016 | 81 | 7.8954 | 4.1948 | 3.8639 | 0.97149 | 0.00035016
| 353.15 | 800000 | 4193.9849 | 3869.0476 | 972.1151 | 0.00035454 | 80 | 7.8954 | 4.194 | 3.869 | 0.97212 | 0.00035454
| 352.15 | 800000 | 4193.1504 | 3874.2112 | 972.7355 | 0.00035901 | 79 | 7.8954 | 4.1932 | 3.8742 | 0.97274 | 0.00035901
| 351.15 | 800000 | 4192.3369 | 3879.3765 | 973.3508 | 0.00036359 | 78 | 7.8954 | 4.1923 | 3.8794 | 0.97335 | 0.00036359
| 350.15 | 800000 | 4191.5435 | 3884.5432 | 973.9611 | 0.00036826 | 77 | 7.8954 | 4.1915 | 3.8845 | 0.97396 | 0.00036826
| 349.15 | 800000 | 4190.771 | 3889.7104 | 974.5662 | 0.00037304 | 76 | 7.8954 | 4.1908 | 3.8897 | 0.97457 | 0.00037304
| 348.15 | 800000 | 4190.0186 | 3894.8782 | 975.1661 | 0.00037793 | 75 | 7.8954 | 4.19 | 3.8949 | 0.97517 | 0.00037793
| 347.15 | 800000 | 4189.2871 | 3900.0457 | 975.7608 | 0.00038292 | 74 | 7.8954 | 4.1893 | 3.9 | 0.97576 | 0.00038292
| 346.15 | 800000 | 4188.5762 | 3905.2124 | 976.3502 | 0.00038803 | 73 | 7.8954 | 4.1886 | 3.9052 | 0.97635 | 0.00038803
| 345.15 | 800000 | 4187.8857 | 3910.3779 | 976.9344 | 0.00039326 | 72 | 7.8954 | 4.1879 | 3.9104 | 0.97693 | 0.00039326
| 344.15 | 800000 | 4187.2158 | 3915.5417 | 977.5132 | 0.0003986 | 71 | 7.8954 | 4.1872 | 3.9155 | 0.97751 | 0.0003986
| 343.15 | 800000 | 4186.5664 | 3920.7034 | 978.0865 | 0.00040407 | 70 | 7.8954 | 4.1866 | 3.9207 | 0.97809 | 0.00040407
| 342.15 | 800000 | 4185.9375 | 3925.8618 | 978.6545 | 0.00040967 | 69 | 7.8954 | 4.1859 | 3.9259 | 0.97865 | 0.00040967
| 341.15 | 800000 | 4185.3296 | 3931.0168 | 979.2171 | 0.0004154 | 68 | 7.8954 | 4.1853 | 3.931 | 0.97922 | 0.0004154
| 340.15 | 800000 | 4184.7422 | 3936.1675 | 979.7741 | 0.00042127 | 67 | 7.8954 | 4.1847 | 3.9362 | 0.97977 | 0.00042127
| 339.15 | 800000 | 4184.1753 | 3941.3132 | 980.3256 | 0.00042728 | 66 | 7.8954 | 4.1842 | 3.9413 | 0.98033 | 0.00042728
| 338.15 | 800000 | 4183.6289 | 3946.4536 | 980.8714 | 0.00043343 | 65 | 7.8954 | 4.1836 | 3.9465 | 0.98087 | 0.00043343
| 337.15 | 800000 | 4183.1035 | 3951.5874 | 981.4116 | 0.00043974 | 64 | 7.8954 | 4.1831 | 3.9516 | 0.98141 | 0.00043974
| 336.15 | 800000 | 4182.5986 | 3956.7144 | 981.9462 | 0.0004462 | 63 | 7.8954 | 4.1826 | 3.9567 | 0.98195 | 0.0004462
| 335.15 | 800000 | 4182.1147 | 3961.8333 | 982.4749 | 0.00045282 | 62 | 7.8954 | 4.1821 | 3.9618 | 0.98247 | 0.00045282
| 334.15 | 800000 | 4181.6514 | 3966.9436 | 982.9979 | 0.0004596 | 61 | 7.8954 | 4.1817 | 3.9669 | 0.983 | 0.0004596
| 333.15 | 800000 | 4181.209 | 3972.0444 | 983.515 | 0.00046656 | 60 | 7.8954 | 4.1812 | 3.972 | 0.98351 | 0.00046656
| 332.15 | 800000 | 4180.7876 | 3977.135 | 984.0262 | 0.00047369 | 59 | 7.8954 | 4.1808 | 3.9771 | 0.98403 | 0.00047369
| 331.15 | 800000 | 4180.3867 | 3982.2141 | 984.5314 | 0.00048101 | 58 | 7.8954 | 4.1804 | 3.9822 | 0.98453 | 0.00048101
| 330.15 | 800000 | 4180.0068 | 3987.2812 | 985.0306 | 0.00048852 | 57 | 7.8954 | 4.18 | 3.9873 | 0.98503 | 0.00048852
| 329.15 | 800000 | 4179.6479 | 3992.3354 | 985.5237 | 0.00049622 | 56 | 7.8954 | 4.1796 | 3.9923 | 0.98552 | 0.00049622
| 328.15 | 800000 | 4179.3105 | 3997.3752 | 986.0107 | 0.00050412 | 55 | 7.8954 | 4.1793 | 3.9974 | 0.98601 | 0.00050412
| 327.15 | 800000 | 4178.9937 | 4002.4001 | 986.4915 | 0.00051224 | 54 | 7.8954 | 4.179 | 4.0024 | 0.98649 | 0.00051224
| 326.15 | 800000 | 4178.6982 | 4007.4087 | 986.966 | 0.00052058 | 53 | 7.8954 | 4.1787 | 4.0074 | 0.98697 | 0.00052058
| 325.15 | 800000 | 4178.4238 | 4012.4001 | 987.4341 | 0.00052914 | 52 | 7.8954 | 4.1784 | 4.0124 | 0.98743 | 0.00052914
| 324.15 | 800000 | 4178.1709 | 4017.3733 | 987.8959 | 0.00053793 | 51 | 7.8954 | 4.1782 | 4.0174 | 0.9879 | 0.00053793
| 323.15 | 800000 | 4177.9395 | 4022.3269 | 988.3511 | 0.00054697 | 50 | 7.8954 | 4.1779 | 4.0223 | 0.98835 | 0.00054697
| 322.15 | 800000 | 4177.7295 | 4027.26 | 988.7998 | 0.00055627 | 49 | 7.8954 | 4.1777 | 4.0273 | 0.9888 | 0.00055627
| 321.15 | 800000 | 4177.541 | 4032.1711 | 989.2419 | 0.00056582 | 48 | 7.8954 | 4.1775 | 4.0322 | 0.98924 | 0.00056582
| 320.15 | 800000 | 4177.3745 | 4037.0591 | 989.6772 | 0.00057565 | 47 | 7.8954 | 4.1774 | 4.0371 | 0.98968 | 0.00057565
| 319.15 | 800000 | 4177.23 | 4041.9229 | 990.1058 | 0.00058576 | 46 | 7.8954 | 4.1772 | 4.0419 | 0.99011 | 0.00058576
| 318.15 | 800000 | 4177.1074 | 4046.7607 | 990.5275 | 0.00059616 | 45 | 7.8954 | 4.1771 | 4.0468 | 0.99053 | 0.00059616
| 317.15 | 800000 | 4177.0068 | 4051.5715 | 990.9423 | 0.00060687 | 44 | 7.8954 | 4.177 | 4.0516 | 0.99094 | 0.00060687
| 316.15 | 800000 | 4176.9292 | 4056.354 | 991.3499 | 0.0006179 | 43 | 7.8954 | 4.1769 | 4.0564 | 0.99135 | 0.0006179
| 315.15 | 800000 | 4176.874 | 4061.1067 | 991.7505 | 0.00062926 | 42 | 7.8954 | 4.1769 | 4.0611 | 0.99175 | 0.00062926
| 314.15 | 800000 | 4176.8418 | 4065.8281 | 992.1438 | 0.00064097 | 41 | 7.8954 | 4.1768 | 4.0658 | 0.99214 | 0.00064097
| 313.15 | 800000 | 4176.833 | 4070.5166 | 992.5298 | 0.00065303 | 40 | 7.8954 | 4.1768 | 4.0705 | 0.99253 | 0.00065303
| 312.15 | 800000 | 4176.8477 | 4075.1711 | 992.9083 | 0.00066547 | 39 | 7.8954 | 4.1768 | 4.0752 | 0.99291 | 0.00066547
| 311.15 | 800000 | 4176.8867 | 4079.7896 | 993.2793 | 0.00067831 | 38 | 7.8954 | 4.1769 | 4.0798 | 0.99328 | 0.00067831
| 310.15 | 800000 | 4176.9497 | 4084.3708 | 993.6427 | 0.00069154 | 37 | 7.8954 | 4.1769 | 4.0844 | 0.99364 | 0.00069154
| 309.15 | 800000 | 4177.0381 | 4088.9133 | 993.9984 | 0.00070521 | 36 | 7.8954 | 4.177 | 4.0889 | 0.994 | 0.00070521
| 308.15 | 800000 | 4177.1519 | 4093.415 | 994.3461 | 0.00071932 | 35 | 7.8954 | 4.1772 | 4.0934 | 0.99435 | 0.00071932
| 307.15 | 800000 | 4177.292 | 4097.875 | 994.6859 | 0.00073389 | 34 | 7.8954 | 4.1773 | 4.0979 | 0.99469 | 0.00073389
| 306.15 | 800000 | 4177.4585 | 4102.2905 | 995.0175 | 0.00074895 | 33 | 7.8954 | 4.1775 | 4.1023 | 0.99502 | 0.00074895
| 305.15 | 800000 | 4177.6533 | 4106.6611 | 995.3409 | 0.00076452 | 32 | 7.8954 | 4.1777 | 4.1067 | 0.99534 | 0.00076452
| 304.15 | 800000 | 4177.8765 | 4110.9844 | 995.6559 | 0.00078062 | 31 | 7.8954 | 4.1779 | 4.111 | 0.99566 | 0.00078062
| 303.15 | 800000 | 4178.1294 | 4115.2588 | 995.9625 | 0.00079728 | 30 | 7.8954 | 4.1781 | 4.1153 | 0.99596 | 0.00079728
| 302.15 | 800000 | 4178.4126 | 4119.4824 | 996.2604 | 0.00081452 | 29 | 7.8954 | 4.1784 | 4.1195 | 0.99626 | 0.00081452
| 301.15 | 800000 | 4178.7285 | 4123.6543 | 996.5495 | 0.00083237 | 28 | 7.8954 | 4.1787 | 4.1237 | 0.99655 | 0.00083237
| 300.15 | 800000 | 4179.0776 | 4127.772 | 996.8297 | 0.00085087 | 27 | 7.8954 | 4.1791 | 4.1278 | 0.99683 | 0.00085087
| 299.15 | 800000 | 4179.4619 | 4131.834 | 997.1006 | 0.00087004 | 26 | 7.8954 | 4.1795 | 4.1318 | 0.9971 | 0.00087004
| 298.15 | 800000 | 4179.8828 | 4135.8389 | 997.3624 | 0.00088992 | 25 | 7.8954 | 4.1799 | 4.1358 | 0.99736 | 0.00088992
| 297.15 | 800000 | 4180.3433 | 4139.7847 | 997.6147 | 0.00091054 | 24 | 7.8954 | 4.1803 | 4.1398 | 0.99761 | 0.00091054
| 296.15 | 800000 | 4180.8447 | 4143.6699 | 997.8573 | 0.00093195 | 23 | 7.8954 | 4.1808 | 4.1437 | 0.99786 | 0.00093195
| 295.15 | 800000 | 4181.3901 | 4147.4927 | 998.0901 | 0.00095418 | 22 | 7.8954 | 4.1814 | 4.1475 | 0.99809 | 0.00095418
| 294.15 | 800000 | 4181.9824 | 4151.252 | 998.3129 | 0.00097729 | 21 | 7.8954 | 4.182 | 4.1513 | 0.99831 | 0.00097729
| 293.15 | 800000 | 4182.624 | 4154.9458 | 998.5255 | 0.0010013 | 20 | 7.8954 | 4.1826 | 4.1549 | 0.99853 | 0.0010013
| 292.15 | 800000 | 4183.3193 | 4158.5728 | 998.7275 | 0.0010263 | 19 | 7.8954 | 4.1833 | 4.1586 | 0.99873 | 0.0010263
| 291.15 | 800000 | 4184.0723 | 4162.1318 | 998.919 | 0.0010523 | 18 | 7.8954 | 4.1841 | 4.1621 | 0.99892 | 0.0010523
| 290.15 | 800000 | 4184.8867 | 4165.6216 | 999.0995 | 0.0010794 | 17 | 7.8954 | 4.1849 | 4.1656 | 0.9991 | 0.0010794
| 289.15 | 800000 | 4185.7676 | 4169.04 | 999.2689 | 0.0011076 | 16 | 7.8954 | 4.1858 | 4.169 | 0.99927 | 0.0011076
| 288.15 | 800000 | 4186.7207 | 4172.3872 | 999.4268 | 0.0011371 | 15 | 7.8954 | 4.1867 | 4.1724 | 0.99943 | 0.0011371
| 287.15 | 800000 | 4187.7524 | 4175.6616 | 999.5731 | 0.0011678 | 14 | 7.8954 | 4.1878 | 4.1757 | 0.99957 | 0.0011678
| 286.15 | 800000 | 4188.8687 | 4178.8618 | 999.7073 | 0.0011999 | 13 | 7.8954 | 4.1889 | 4.1789 | 0.99971 | 0.0011999
| 285.15 | 800000 | 4190.0771 | 4181.9878 | 999.8293 | 0.0012334 | 12 | 7.8954 | 4.1901 | 4.182 | 0.99983 | 0.0012334
| 284.15 | 800000 | 4191.3867 | 4185.0391 | 999.9387 | 0.0012684 | 11 | 7.8954 | 4.1914 | 4.185 | 0.99994 | 0.0012684
| 283.15 | 800000 | 4192.8062 | 4188.0146 | 1000.0351 | 0.0013051 | 10 | 7.8954 | 4.1928 | 4.188 | 1 | 0.0013051
| 282.15 | 800000 | 4194.3457 | 4190.9146 | 1000.1182 | 0.0013435 | 9 | 7.8954 | 4.1943 | 4.1909 | 1.0001 | 0.0013435
| 281.15 | 800000 | 4196.0166 | 4193.7383 | 1000.1877 | 0.0013838 | 8 | 7.8954 | 4.196 | 4.1937 | 1.0002 | 0.0013838
| 280.15 | 800000 | 4197.832 | 4196.4868 | 1000.2432 | 0.001426 | 7 | 7.8954 | 4.1978 | 4.1965 | 1.0002 | 0.001426
| 279.15 | 800000 | 4199.8052 | 4199.1602 | 1000.2841 | 0.0014704 | 6 | 7.8954 | 4.1998 | 4.1992 | 1.0003 | 0.0014704
| 278.15 | 800000 | 4201.9517 | 4201.7593 | 1000.3102 | 0.001517 | 5 | 7.8954 | 4.202 | 4.2018 | 1.0003 | 0.001517
| 277.15 | 800000 | 4204.2891 | 4204.2847 | 1000.3209 | 0.001566 | 4 | 7.8954 | 4.2043 | 4.2043 | 1.0003 | 0.001566
| 276.15 | 800000 | 4206.8354 | 4206.7373 | 1000.3157 | 0.0016176 | 3 | 7.8954 | 4.2068 | 4.2067 | 1.0003 | 0.0016176
| 275.15 | 800000 | 4209.6128 | 4209.1196 | 1000.2941 | 0.0016719 | 2 | 7.8954 | 4.2096 | 4.2091 | 1.0003 | 0.0016719
| 274.15 | 800000 | 4212.6431 | 4211.4326 | 1000.2556 | 0.0017292 | 0.99999 | 7.8954 | 4.2126 | 4.2114 | 1.0003 | 0.0017292
| 273.15 | 800000 | 4215.9526 | 4213.6782 | 1000.1995 | 0.0017898 | -6.1035e-06 | 7.8954 | 4.216 | 4.2137 | 1.0002 | 0.0017898
| 473.15 | 700000 | 2246.842 | 1652.7654 | 3.3334 | 1.5989e-05 | 200 | 6.9084 | 2.2468 | 1.6528 | 0.0033334 | 1.5989e-05
| 472.15 | 700000 | 2250.895 | 1655.0199 | 3.3418 | 1.5946e-05 | 199 | 6.9084 | 2.2509 | 1.655 | 0.0033418 | 1.5946e-05
| 471.15 | 700000 | 2255.0527 | 1657.3405 | 3.3502 | 1.5904e-05 | 198 | 6.9084 | 2.2551 | 1.6573 | 0.0033502 | 1.5904e-05
| 470.15 | 700000 | 2259.3201 | 1659.7301 | 3.3586 | 1.5862e-05 | 197 | 6.9084 | 2.2593 | 1.6597 | 0.0033586 | 1.5862e-05
| 469.15 | 700000 | 2263.7014 | 1662.1921 | 3.3671 | 1.582e-05 | 196 | 6.9084 | 2.2637 | 1.6622 | 0.0033671 | 1.582e-05
| 468.15 | 700000 | 2268.2024 | 1664.7302 | 3.3757 | 1.5777e-05 | 195 | 6.9084 | 2.2682 | 1.6647 | 0.0033757 | 1.5777e-05
| 467.15 | 700000 | 2272.8289 | 1667.3483 | 3.3844 | 1.5735e-05 | 194 | 6.9084 | 2.2728 | 1.6673 | 0.0033844 | 1.5735e-05
| 466.15 | 700000 | 2277.5869 | 1670.0509 | 3.393 | 1.5693e-05 | 193 | 6.9084 | 2.2776 | 1.6701 | 0.003393 | 1.5693e-05
| 465.15 | 700000 | 2282.4841 | 1672.8429 | 3.4018 | 1.5651e-05 | 192 | 6.9084 | 2.2825 | 1.6728 | 0.0034018 | 1.5651e-05
| 464.15 | 700000 | 2287.5281 | 1675.7296 | 3.4106 | 1.5608e-05 | 191 | 6.9084 | 2.2875 | 1.6757 | 0.0034106 | 1.5608e-05
| 463.15 | 700000 | 2292.7275 | 1678.7174 | 3.4195 | 1.5566e-05 | 190 | 6.9084 | 2.2927 | 1.6787 | 0.0034195 | 1.5566e-05
| 462.15 | 700000 | 2298.0918 | 1681.8129 | 3.4284 | 1.5524e-05 | 189 | 6.9084 | 2.2981 | 1.6818 | 0.0034284 | 1.5524e-05
| 461.15 | 700000 | 2303.6321 | 1685.0237 | 3.4374 | 1.5482e-05 | 188 | 6.9084 | 2.3036 | 1.685 | 0.0034374 | 1.5482e-05
| 460.15 | 700000 | 2309.3599 | 1688.3583 | 3.4465 | 1.5439e-05 | 187 | 6.9084 | 2.3094 | 1.6884 | 0.0034465 | 1.5439e-05
| 459.15 | 700000 | 2315.2886 | 1691.826 | 3.4556 | 1.5397e-05 | 186 | 6.9084 | 2.3153 | 1.6918 | 0.0034556 | 1.5397e-05
| 458.15 | 700000 | 2321.4333 | 1695.4379 | 3.4648 | 1.5355e-05 | 185 | 6.9084 | 2.3214 | 1.6954 | 0.0034648 | 1.5355e-05
| 457.15 | 700000 | 2327.811 | 1699.2056 | 3.4741 | 1.5313e-05 | 184 | 6.9084 | 2.3278 | 1.6992 | 0.0034741 | 1.5313e-05
| 456.15 | 700000 | 2334.4399 | 1703.1427 | 3.4835 | 1.527e-05 | 183 | 6.9084 | 2.3344 | 1.7031 | 0.0034835 | 1.527e-05
| 455.15 | 700000 | 2341.3416 | 1707.2646 | 3.4929 | 1.5228e-05 | 182 | 6.9084 | 2.3413 | 1.7073 | 0.0034929 | 1.5228e-05
| 454.15 | 700000 | 2348.5393 | 1711.5883 | 3.5024 | 1.5186e-05 | 181 | 6.9084 | 2.3485 | 1.7116 | 0.0035024 | 1.5186e-05
| 453.15 | 700000 | 2356.0605 | 1716.1333 | 3.5119 | 1.5144e-05 | 180 | 6.9084 | 2.3561 | 1.7161 | 0.0035119 | 1.5144e-05
| 452.15 | 700000 | 2363.9353 | 1720.9214 | 3.5216 | 1.5101e-05 | 179 | 6.9084 | 2.3639 | 1.7209 | 0.0035216 | 1.5101e-05
| 451.15 | 700000 | 2372.1975 | 1725.9775 | 3.5313 | 1.5059e-05 | 178 | 6.9084 | 2.3722 | 1.726 | 0.0035313 | 1.5059e-05
| 450.15 | 700000 | 2380.8862 | 1731.3297 | 3.5411 | 1.5017e-05 | 177 | 6.9084 | 2.3809 | 1.7313 | 0.0035411 | 1.5017e-05
| 449.15 | 700000 | 2390.0454 | 1737.0096 | 3.5509 | 1.4975e-05 | 176 | 6.9084 | 2.39 | 1.737 | 0.0035509 | 1.4975e-05
| 448.15 | 700000 | 2399.7244 | 1743.0536 | 3.5609 | 1.4932e-05 | 175 | 6.9084 | 2.3997 | 1.7431 | 0.0035609 | 1.4932e-05
| 447.15 | 700000 | 2409.9797 | 1749.5023 | 3.5709 | 1.489e-05 | 174 | 6.9084 | 2.41 | 1.7495 | 0.0035709 | 1.489e-05
| 446.15 | 700000 | 2420.8752 | 1756.4023 | 3.5811 | 1.4848e-05 | 173 | 6.9084 | 2.4209 | 1.7564 | 0.0035811 | 1.4848e-05
| 445.15 | 700000 | 2432.4839 | 1763.8062 | 3.5913 | 1.4805e-05 | 172 | 6.9084 | 2.4325 | 1.7638 | 0.0035913 | 1.4805e-05
| 444.15 | 700000 | 2444.8882 | 1771.7737 | 3.6016 | 1.4763e-05 | 171 | 6.9084 | 2.4449 | 1.7718 | 0.0036016 | 1.4763e-05
| 443.15 | 700000 | 2458.1821 | 1780.3729 | 3.612 | 1.4721e-05 | 170 | 6.9084 | 2.4582 | 1.7804 | 0.003612 | 1.4721e-05
| 442.15 | 700000 | 2472.4724 | 1789.6812 | 3.6225 | 1.4679e-05 | 169 | 6.9084 | 2.4725 | 1.7897 | 0.0036225 | 1.4679e-05
| 441.15 | 700000 | 2487.8813 | 1799.786 | 3.6332 | 1.4636e-05 | 168 | 6.9084 | 2.4879 | 1.7998 | 0.0036332 | 1.4636e-05
| 440.15 | 700000 | 2504.5471 | 1810.7874 | 3.6439 | 1.4594e-05 | 167 | 6.9084 | 2.5045 | 1.8108 | 0.0036439 | 1.4594e-05
| 439.15 | 700000 | 2522.6282 | 1822.7986 | 3.6547 | 1.4552e-05 | 166 | 6.9084 | 2.5226 | 1.8228 | 0.0036547 | 1.4552e-05
| 438.15 | 700000 | 2542.3047 | 1835.9487 | 3.6657 | 1.4509e-05 | 165 | 6.9084 | 2.5423 | 1.8359 | 0.0036657 | 1.4509e-05
| 437.15 | 700000 | 4349.9971 | 3464.1316 | 903.5156 | 0.0001658 | 164 | 6.9084 | 4.35 | 3.4641 | 0.90352 | 0.0001658
| 436.15 | 700000 | 4346.8428 | 3468.48 | 904.5187 | 0.00016689 | 163 | 6.9084 | 4.3468 | 3.4685 | 0.90452 | 0.00016689
| 435.15 | 700000 | 4343.7314 | 3472.8423 | 905.517 | 0.000168 | 162 | 6.9084 | 4.3437 | 3.4728 | 0.90552 | 0.000168
| 434.15 | 700000 | 4340.6626 | 3477.2185 | 906.5106 | 0.00016912 | 161 | 6.9084 | 4.3407 | 3.4772 | 0.90651 | 0.00016912
| 433.15 | 700000 | 4337.6357 | 3481.6082 | 907.4995 | 0.00017026 | 160 | 6.9084 | 4.3376 | 3.4816 | 0.9075 | 0.00017026
| 432.15 | 700000 | 4334.6504 | 3486.0115 | 908.4837 | 0.00017141 | 159 | 6.9084 | 4.3347 | 3.486 | 0.90848 | 0.00017141
| 431.15 | 700000 | 4331.7056 | 3490.4282 | 909.4633 | 0.00017258 | 158 | 6.9084 | 4.3317 | 3.4904 | 0.90946 | 0.00017258
| 430.15 | 700000 | 4328.8008 | 3494.8584 | 910.4382 | 0.00017376 | 157 | 6.9084 | 4.3288 | 3.4949 | 0.91044 | 0.00017376
| 429.15 | 700000 | 4325.9355 | 3499.3018 | 911.4084 | 0.00017496 | 156 | 6.9084 | 4.3259 | 3.4993 | 0.91141 | 0.00017496
| 428.15 | 700000 | 4323.1094 | 3503.7583 | 912.3741 | 0.00017618 | 155 | 6.9084 | 4.3231 | 3.5038 | 0.91237 | 0.00017618
| 427.15 | 700000 | 4320.3213 | 3508.228 | 913.3352 | 0.00017741 | 154 | 6.9084 | 4.3203 | 3.5082 | 0.91334 | 0.00017741
| 426.15 | 700000 | 4317.5713 | 3512.7109 | 914.2917 | 0.00017866 | 153 | 6.9084 | 4.3176 | 3.5127 | 0.91429 | 0.00017866
| 425.15 | 700000 | 4314.8589 | 3517.2065 | 915.2436 | 0.00017993 | 152 | 6.9084 | 4.3149 | 3.5172 | 0.91524 | 0.00017993
| 424.15 | 700000 | 4312.1826 | 3521.7151 | 916.191 | 0.00018121 | 151 | 6.9084 | 4.3122 | 3.5217 | 0.91619 | 0.00018121
| 423.15 | 700000 | 4309.543 | 3526.2366 | 917.1339 | 0.00018252 | 150 | 6.9084 | 4.3095 | 3.5262 | 0.91713 | 0.00018252
| 422.15 | 700000 | 4306.939 | 3530.7705 | 918.0722 | 0.00018384 | 149 | 6.9084 | 4.3069 | 3.5308 | 0.91807 | 0.00018384
| 421.15 | 700000 | 4304.3706 | 3535.3171 | 919.006 | 0.00018518 | 148 | 6.9084 | 4.3044 | 3.5353 | 0.91901 | 0.00018518
| 420.15 | 700000 | 4301.8369 | 3539.8762 | 919.9354 | 0.00018654 | 147 | 6.9084 | 4.3018 | 3.5399 | 0.91994 | 0.00018654
| 419.15 | 700000 | 4299.3374 | 3544.448 | 920.8602 | 0.00018792 | 146 | 6.9084 | 4.2993 | 3.5444 | 0.92086 | 0.00018792
| 418.15 | 700000 | 4296.8716 | 3549.032 | 921.7806 | 0.00018932 | 145 | 6.9084 | 4.2969 | 3.549 | 0.92178 | 0.00018932
| 417.15 | 700000 | 4294.4395 | 3553.6282 | 922.6965 | 0.00019074 | 144 | 6.9084 | 4.2944 | 3.5536 | 0.9227 | 0.00019074
| 416.15 | 700000 | 4292.0405 | 3558.2368 | 923.608 | 0.00019218 | 143 | 6.9084 | 4.292 | 3.5582 | 0.92361 | 0.00019218
| 415.15 | 700000 | 4289.6738 | 3562.8574 | 924.515 | 0.00019364 | 142 | 6.9084 | 4.2897 | 3.5629 | 0.92451 | 0.00019364
| 414.15 | 700000 | 4287.3394 | 3567.4902 | 925.4175 | 0.00019512 | 141 | 6.9084 | 4.2873 | 3.5675 | 0.92542 | 0.00019512
| 413.15 | 700000 | 4285.0366 | 3572.1348 | 926.3157 | 0.00019663 | 140 | 6.9084 | 4.285 | 3.5721 | 0.92632 | 0.00019663
| 412.15 | 700000 | 4282.7651 | 3576.7915 | 927.2094 | 0.00019816 | 139 | 6.9084 | 4.2828 | 3.5768 | 0.92721 | 0.00019816
| 411.15 | 700000 | 4280.5244 | 3581.46 | 928.0988 | 0.00019971 | 138 | 6.9084 | 4.2805 | 3.5815 | 0.9281 | 0.00019971
| 410.15 | 700000 | 4278.3145 | 3586.1401 | 928.9836 | 0.00020128 | 137 | 6.9084 | 4.2783 | 3.5861 | 0.92898 | 0.00020128
| 409.15 | 700000 | 4276.1348 | 3590.832 | 929.8641 | 0.00020288 | 136 | 6.9084 | 4.2761 | 3.5908 | 0.92986 | 0.00020288
| 408.15 | 700000 | 4273.9849 | 3595.5356 | 930.7402 | 0.0002045 | 135 | 6.9084 | 4.274 | 3.5955 | 0.93074 | 0.0002045
| 407.15 | 700000 | 4271.8647 | 3600.2505 | 931.612 | 0.00020615 | 134 | 6.9084 | 4.2719 | 3.6003 | 0.93161 | 0.00020615
| 406.15 | 700000 | 4269.7729 | 3604.9771 | 932.4793 | 0.00020783 | 133 | 6.9084 | 4.2698 | 3.605 | 0.93248 | 0.00020783
| 405.15 | 700000 | 4267.7104 | 3609.7151 | 933.3423 | 0.00020953 | 132 | 6.9084 | 4.2677 | 3.6097 | 0.93334 | 0.00020953
| 404.15 | 700000 | 4265.6763 | 3614.4641 | 934.2009 | 0.00021125 | 131 | 6.9084 | 4.2657 | 3.6145 | 0.9342 | 0.00021125
| 403.15 | 700000 | 4263.6704 | 3619.2246 | 935.0551 | 0.00021301 | 130 | 6.9084 | 4.2637 | 3.6192 | 0.93506 | 0.00021301
| 402.15 | 700000 | 4261.6919 | 3623.9961 | 935.9048 | 0.00021479 | 129 | 6.9084 | 4.2617 | 3.624 | 0.9359 | 0.00021479
| 401.15 | 700000 | 4259.7412 | 3628.7788 | 936.7503 | 0.0002166 | 128 | 6.9084 | 4.2597 | 3.6288 | 0.93675 | 0.0002166
| 400.15 | 700000 | 4257.8179 | 3633.5725 | 937.5914 | 0.00021844 | 127 | 6.9084 | 4.2578 | 3.6336 | 0.93759 | 0.00021844
| 399.15 | 700000 | 4255.9209 | 3638.3772 | 938.428 | 0.00022031 | 126 | 6.9084 | 4.2559 | 3.6384 | 0.93843 | 0.00022031
| 398.15 | 700000 | 4254.0508 | 3643.1924 | 939.2604 | 0.00022221 | 125 | 6.9084 | 4.2541 | 3.6432 | 0.93926 | 0.00022221
| 397.15 | 700000 | 4252.207 | 3648.0186 | 940.0883 | 0.00022414 | 124 | 6.9084 | 4.2522 | 3.648 | 0.94009 | 0.00022414
| 396.15 | 700000 | 4250.3896 | 3652.8555 | 940.9119 | 0.0002261 | 123 | 6.9084 | 4.2504 | 3.6529 | 0.94091 | 0.0002261
| 395.15 | 700000 | 4248.5977 | 3657.7029 | 941.7311 | 0.00022809 | 122 | 6.9084 | 4.2486 | 3.6577 | 0.94173 | 0.00022809
| 394.15 | 700000 | 4246.8311 | 3662.5608 | 942.5459 | 0.00023012 | 121 | 6.9084 | 4.2468 | 3.6626 | 0.94255 | 0.00023012
| 393.15 | 700000 | 4245.0903 | 3667.4292 | 943.3563 | 0.00023218 | 120 | 6.9084 | 4.2451 | 3.6674 | 0.94336 | 0.00023218
| 392.15 | 700000 | 4243.374 | 3672.3079 | 944.1624 | 0.00023428 | 119 | 6.9084 | 4.2434 | 3.6723 | 0.94416 | 0.00023428
| 391.15 | 700000 | 4241.6831 | 3677.1968 | 944.9641 | 0.00023641 | 118 | 6.9084 | 4.2417 | 3.6772 | 0.94496 | 0.00023641
| 390.15 | 700000 | 4240.0166 | 3682.0957 | 945.7613 | 0.00023858 | 117 | 6.9084 | 4.24 | 3.6821 | 0.94576 | 0.00023858
| 389.15 | 700000 | 4238.3745 | 3687.0049 | 946.5541 | 0.00024079 | 116 | 6.9084 | 4.2384 | 3.687 | 0.94655 | 0.00024079
| 388.15 | 700000 | 4236.7563 | 3691.9238 | 947.3426 | 0.00024303 | 115 | 6.9084 | 4.2368 | 3.6919 | 0.94734 | 0.00024303
| 387.15 | 700000 | 4235.1626 | 3696.8528 | 948.1266 | 0.00024531 | 114 | 6.9084 | 4.2352 | 3.6969 | 0.94813 | 0.00024531
| 386.15 | 700000 | 4233.5923 | 3701.7913 | 948.9062 | 0.00024763 | 113 | 6.9084 | 4.2336 | 3.7018 | 0.94891 | 0.00024763
| 385.15 | 700000 | 4232.0454 | 3706.7395 | 949.6815 | 0.00025 | 112 | 6.9084 | 4.232 | 3.7067 | 0.94968 | 0.00025
| 384.15 | 700000 | 4230.5225 | 3711.6973 | 950.4522 | 0.0002524 | 111 | 6.9084 | 4.2305 | 3.7117 | 0.95045 | 0.0002524
| 383.15 | 700000 | 4229.0225 | 3716.6643 | 951.2185 | 0.00025485 | 110 | 6.9084 | 4.229 | 3.7167 | 0.95122 | 0.00025485
| 382.15 | 700000 | 4227.5454 | 3721.6406 | 951.9803 | 0.00025734 | 109 | 6.9084 | 4.2275 | 3.7216 | 0.95198 | 0.00025734
| 381.15 | 700000 | 4226.0913 | 3726.6262 | 952.7377 | 0.00025987 | 108 | 6.9084 | 4.2261 | 3.7266 | 0.95274 | 0.00025987
| 380.15 | 700000 | 4224.6602 | 3731.6208 | 953.4907 | 0.00026246 | 107 | 6.9084 | 4.2247 | 3.7316 | 0.95349 | 0.00026246
| 379.15 | 700000 | 4223.2515 | 3736.6243 | 954.2391 | 0.00026508 | 106 | 6.9084 | 4.2233 | 3.7366 | 0.95424 | 0.00026508
| 378.15 | 700000 | 4221.8652 | 3741.6365 | 954.983 | 0.00026776 | 105 | 6.9084 | 4.2219 | 3.7416 | 0.95498 | 0.00026776
| 377.15 | 700000 | 4220.5015 | 3746.6572 | 955.7224 | 0.00027049 | 104 | 6.9084 | 4.2205 | 3.7467 | 0.95572 | 0.00027049
| 376.15 | 700000 | 4219.1597 | 3751.6863 | 956.4573 | 0.00027326 | 103 | 6.9084 | 4.2192 | 3.7517 | 0.95646 | 0.00027326
| 375.15 | 700000 | 4217.8398 | 3756.7239 | 957.1876 | 0.00027609 | 102 | 6.9084 | 4.2178 | 3.7567 | 0.95719 | 0.00027609
| 374.15 | 700000 | 4216.5425 | 3761.7695 | 957.9135 | 0.00027897 | 101 | 6.9084 | 4.2165 | 3.7618 | 0.95791 | 0.00027897
| 373.15 | 700000 | 4215.2666 | 3766.8232 | 958.6346 | 0.00028191 | 100 | 6.9084 | 4.2153 | 3.7668 | 0.95863 | 0.00028191
| 372.15 | 700000 | 4214.0122 | 3771.8845 | 959.3513 | 0.0002849 | 99 | 6.9084 | 4.214 | 3.7719 | 0.95935 | 0.0002849
| 371.15 | 700000 | 4212.7798 | 3776.9534 | 960.0634 | 0.00028794 | 98 | 6.9084 | 4.2128 | 3.777 | 0.96006 | 0.00028794
| 370.15 | 700000 | 4211.5684 | 3782.0298 | 960.7708 | 0.00029105 | 97 | 6.9084 | 4.2116 | 3.782 | 0.96077 | 0.00029105
| 369.15 | 700000 | 4210.3789 | 3787.1135 | 961.4736 | 0.00029422 | 96 | 6.9084 | 4.2104 | 3.7871 | 0.96147 | 0.00029422
| 368.15 | 700000 | 4209.2104 | 3792.2041 | 962.1717 | 0.00029745 | 95 | 6.9084 | 4.2092 | 3.7922 | 0.96217 | 0.00029745
| 367.15 | 700000 | 4208.0635 | 3797.3015 | 962.8652 | 0.00030074 | 94 | 6.9084 | 4.2081 | 3.7973 | 0.96287 | 0.00030074
| 366.15 | 700000 | 4206.9375 | 3802.4053 | 963.5539 | 0.0003041 | 93 | 6.9084 | 4.2069 | 3.8024 | 0.96355 | 0.0003041
| 365.15 | 700000 | 4205.833 | 3807.5156 | 964.238 | 0.00030752 | 92 | 6.9084 | 4.2058 | 3.8075 | 0.96424 | 0.00030752
| 364.15 | 700000 | 4204.749 | 3812.6318 | 964.9173 | 0.00031101 | 91 | 6.9084 | 4.2047 | 3.8126 | 0.96492 | 0.00031101
| 363.15 | 700000 | 4203.6865 | 3817.7539 | 965.5919 | 0.00031457 | 90 | 6.9084 | 4.2037 | 3.8178 | 0.96559 | 0.00031457
| 362.15 | 700000 | 4202.6445 | 3822.8816 | 966.2617 | 0.00031821 | 89 | 6.9084 | 4.2026 | 3.8229 | 0.96626 | 0.00031821
| 361.15 | 700000 | 4201.6235 | 3828.0146 | 966.9266 | 0.00032192 | 88 | 6.9084 | 4.2016 | 3.828 | 0.96693 | 0.00032192
| 360.15 | 700000 | 4200.6235 | 3833.1526 | 967.5868 | 0.0003257 | 87 | 6.9084 | 4.2006 | 3.8332 | 0.96759 | 0.0003257
| 359.15 | 700000 | 4199.6445 | 3838.2952 | 968.2421 | 0.00032956 | 86 | 6.9084 | 4.1996 | 3.8383 | 0.96824 | 0.00032956
| 358.15 | 700000 | 4198.686 | 3843.4419 | 968.8925 | 0.00033351 | 85 | 6.9084 | 4.1987 | 3.8434 | 0.96889 | 0.00033351
| 357.15 | 700000 | 4197.748 | 3848.593 | 969.538 | 0.00033753 | 84 | 6.9084 | 4.1977 | 3.8486 | 0.96954 | 0.00033753
| 356.15 | 700000 | 4196.8311 | 3853.7476 | 970.1786 | 0.00034164 | 83 | 6.9084 | 4.1968 | 3.8537 | 0.97018 | 0.00034164
| 355.15 | 700000 | 4195.9346 | 3858.9055 | 970.8141 | 0.00034584 | 82 | 6.9084 | 4.1959 | 3.8589 | 0.97081 | 0.00034584
| 354.15 | 700000 | 4195.0586 | 3864.0664 | 971.4448 | 0.00035013 | 81 | 6.9084 | 4.1951 | 3.8641 | 0.97144 | 0.00035013
| 353.15 | 700000 | 4194.2036 | 3869.2297 | 972.0704 | 0.00035451 | 80 | 6.9084 | 4.1942 | 3.8692 | 0.97207 | 0.00035451
| 352.15 | 700000 | 4193.3691 | 3874.3955 | 972.6909 | 0.00035899 | 79 | 6.9084 | 4.1934 | 3.8744 | 0.97269 | 0.00035899
| 351.15 | 700000 | 4192.5552 | 3879.5627 | 973.3064 | 0.00036356 | 78 | 6.9084 | 4.1926 | 3.8796 | 0.97331 | 0.00036356
| 350.15 | 700000 | 4191.7617 | 3884.7314 | 973.9167 | 0.00036824 | 77 | 6.9084 | 4.1918 | 3.8847 | 0.97392 | 0.00036824
| 349.15 | 700000 | 4190.9888 | 3889.9009 | 974.5219 | 0.00037302 | 76 | 6.9084 | 4.191 | 3.8899 | 0.97452 | 0.00037302
| 348.15 | 700000 | 4190.2368 | 3895.0706 | 975.1219 | 0.0003779 | 75 | 6.9084 | 4.1902 | 3.8951 | 0.97512 | 0.0003779
| 347.15 | 700000 | 4189.5054 | 3900.2402 | 975.7166 | 0.0003829 | 74 | 6.9084 | 4.1895 | 3.9002 | 0.97572 | 0.0003829
| 346.15 | 700000 | 4188.7939 | 3905.4092 | 976.3061 | 0.00038801 | 73 | 6.9084 | 4.1888 | 3.9054 | 0.97631 | 0.00038801
| 345.15 | 700000 | 4188.104 | 3910.5769 | 976.8903 | 0.00039323 | 72 | 6.9084 | 4.1881 | 3.9106 | 0.97689 | 0.00039323
| 344.15 | 700000 | 4187.4341 | 3915.7432 | 977.4692 | 0.00039858 | 71 | 6.9084 | 4.1874 | 3.9157 | 0.97747 | 0.00039858
| 343.15 | 700000 | 4186.7847 | 3920.9067 | 978.0426 | 0.00040405 | 70 | 6.9084 | 4.1868 | 3.9209 | 0.97804 | 0.00040405
| 342.15 | 700000 | 4186.1562 | 3926.0676 | 978.6107 | 0.00040965 | 69 | 6.9084 | 4.1862 | 3.9261 | 0.97861 | 0.00040965
| 341.15 | 700000 | 4185.5483 | 3931.2249 | 979.1732 | 0.00041538 | 68 | 6.9084 | 4.1855 | 3.9312 | 0.97917 | 0.00041538
| 340.15 | 700000 | 4184.9609 | 3936.3779 | 979.7303 | 0.00042125 | 67 | 6.9084 | 4.185 | 3.9364 | 0.97973 | 0.00042125
| 339.15 | 700000 | 4184.3945 | 3941.5261 | 980.2818 | 0.00042726 | 66 | 6.9084 | 4.1844 | 3.9415 | 0.98028 | 0.00042726
| 338.15 | 700000 | 4183.8486 | 3946.6687 | 980.8277 | 0.00043341 | 65 | 6.9084 | 4.1838 | 3.9467 | 0.98083 | 0.00043341
| 337.15 | 700000 | 4183.3237 | 3951.8049 | 981.368 | 0.00043972 | 64 | 6.9084 | 4.1833 | 3.9518 | 0.98137 | 0.00043972
| 336.15 | 700000 | 4182.8193 | 3956.9341 | 981.9025 | 0.00044617 | 63 | 6.9084 | 4.1828 | 3.9569 | 0.9819 | 0.00044617
| 335.15 | 700000 | 4182.3359 | 3962.0557 | 982.4313 | 0.00045279 | 62 | 6.9084 | 4.1823 | 3.9621 | 0.98243 | 0.00045279
| 334.15 | 700000 | 4181.873 | 3967.1685 | 982.9543 | 0.00045958 | 61 | 6.9084 | 4.1819 | 3.9672 | 0.98295 | 0.00045958
| 333.15 | 700000 | 4181.4312 | 3972.2717 | 983.4714 | 0.00046654 | 60 | 6.9084 | 4.1814 | 3.9723 | 0.98347 | 0.00046654
| 332.15 | 700000 | 4181.0103 | 3977.365 | 983.9827 | 0.00047367 | 59 | 6.9084 | 4.181 | 3.9774 | 0.98398 | 0.00047367
| 331.15 | 700000 | 4180.6099 | 3982.4468 | 984.4879 | 0.00048099 | 58 | 6.9084 | 4.1806 | 3.9824 | 0.98449 | 0.00048099
| 330.15 | 700000 | 4180.231 | 3987.5164 | 984.9872 | 0.00048849 | 57 | 6.9084 | 4.1802 | 3.9875 | 0.98499 | 0.00048849
| 329.15 | 700000 | 4179.873 | 3992.573 | 985.4803 | 0.0004962 | 56 | 6.9084 | 4.1799 | 3.9926 | 0.98548 | 0.0004962
| 328.15 | 700000 | 4179.5361 | 3997.6157 | 985.9673 | 0.0005041 | 55 | 6.9084 | 4.1795 | 3.9976 | 0.98597 | 0.0005041
| 327.15 | 700000 | 4179.2202 | 4002.6433 | 986.4481 | 0.00051222 | 54 | 6.9084 | 4.1792 | 4.0026 | 0.98645 | 0.00051222
| 326.15 | 700000 | 4178.9258 | 4007.6545 | 986.9225 | 0.00052056 | 53 | 6.9084 | 4.1789 | 4.0077 | 0.98692 | 0.00052056
| 325.15 | 700000 | 4178.6523 | 4012.6487 | 987.3907 | 0.00052912 | 52 | 6.9084 | 4.1787 | 4.0126 | 0.98739 | 0.00052912
| 324.15 | 700000 | 4178.4004 | 4017.6248 | 987.8525 | 0.00053792 | 51 | 6.9084 | 4.1784 | 4.0176 | 0.98785 | 0.00053792
| 323.15 | 700000 | 4178.1704 | 4022.5811 | 988.3077 | 0.00054696 | 50 | 6.9084 | 4.1782 | 4.0226 | 0.98831 | 0.00054696
| 322.15 | 700000 | 4177.9614 | 4027.5168 | 988.7564 | 0.00055625 | 49 | 6.9084 | 4.178 | 4.0275 | 0.98876 | 0.00055625
| 321.15 | 700000 | 4177.7744 | 4032.4309 | 989.1984 | 0.0005658 | 48 | 6.9084 | 4.1778 | 4.0324 | 0.9892 | 0.0005658
| 320.15 | 700000 | 4177.6089 | 4037.3218 | 989.6338 | 0.00057563 | 47 | 6.9084 | 4.1776 | 4.0373 | 0.98963 | 0.00057563
| 319.15 | 700000 | 4177.4658 | 4042.1885 | 990.0623 | 0.00058574 | 46 | 6.9084 | 4.1775 | 4.0422 | 0.99006 | 0.00058574
| 318.15 | 700000 | 4177.3447 | 4047.0293 | 990.484 | 0.00059615 | 45 | 6.9084 | 4.1773 | 4.047 | 0.99048 | 0.00059615
| 317.15 | 700000 | 4177.2456 | 4051.843 | 990.8987 | 0.00060686 | 44 | 6.9084 | 4.1772 | 4.0518 | 0.9909 | 0.00060686
| 316.15 | 700000 | 4177.1694 | 4056.6287 | 991.3063 | 0.00061789 | 43 | 6.9084 | 4.1772 | 4.0566 | 0.99131 | 0.00061789
| 315.15 | 700000 | 4177.1162 | 4061.3843 | 991.7068 | 0.00062925 | 42 | 6.9084 | 4.1771 | 4.0614 | 0.99171 | 0.00062925
| 314.15 | 700000 | 4177.0854 | 4066.1086 | 992.1001 | 0.00064096 | 41 | 6.9084 | 4.1771 | 4.0661 | 0.9921 | 0.00064096
| 313.15 | 700000 | 4177.0786 | 4070.8005 | 992.4861 | 0.00065303 | 40 | 6.9084 | 4.1771 | 4.0708 | 0.99249 | 0.00065303
| 312.15 | 700000 | 4177.0952 | 4075.458 | 992.8646 | 0.00066547 | 39 | 6.9084 | 4.1771 | 4.0755 | 0.99286 | 0.00066547
| 311.15 | 700000 | 4177.1362 | 4080.0798 | 993.2355 | 0.0006783 | 38 | 6.9084 | 4.1771 | 4.0801 | 0.99324 | 0.0006783
| 310.15 | 700000 | 4177.2017 | 4084.6643 | 993.5988 | 0.00069154 | 37 | 6.9084 | 4.1772 | 4.0847 | 0.9936 | 0.00069154
| 309.15 | 700000 | 4177.292 | 4089.21 | 993.9544 | 0.00070521 | 36 | 6.9084 | 4.1773 | 4.0892 | 0.99395 | 0.00070521
| 308.15 | 700000 | 4177.4082 | 4093.7151 | 994.3021 | 0.00071932 | 35 | 6.9084 | 4.1774 | 4.0937 | 0.9943 | 0.00071932
| 307.15 | 700000 | 4177.5508 | 4098.1782 | 994.6418 | 0.00073389 | 34 | 6.9084 | 4.1776 | 4.0982 | 0.99464 | 0.00073389
| 306.15 | 700000 | 4177.7202 | 4102.5972 | 994.9734 | 0.00074896 | 33 | 6.9084 | 4.1777 | 4.1026 | 0.99497 | 0.00074896
| 305.15 | 700000 | 4177.9175 | 4106.9712 | 995.2967 | 0.00076453 | 32 | 6.9084 | 4.1779 | 4.107 | 0.9953 | 0.00076453
| 304.15 | 700000 | 4178.1436 | 4111.2979 | 995.6116 | 0.00078063 | 31 | 6.9084 | 4.1781 | 4.1113 | 0.99561 | 0.00078063
| 303.15 | 700000 | 4178.3994 | 4115.5757 | 995.9181 | 0.00079729 | 30 | 6.9084 | 4.1784 | 4.1156 | 0.99592 | 0.00079729
| 302.15 | 700000 | 4178.686 | 4119.8032 | 996.2159 | 0.00081453 | 29 | 6.9084 | 4.1787 | 4.1198 | 0.99622 | 0.00081453
| 301.15 | 700000 | 4179.0049 | 4123.9785 | 996.5049 | 0.00083239 | 28 | 6.9084 | 4.179 | 4.124 | 0.9965 | 0.00083239
| 300.15 | 700000 | 4179.3574 | 4128.1001 | 996.7849 | 0.00085089 | 27 | 6.9084 | 4.1794 | 4.1281 | 0.99678 | 0.00085089
| 299.15 | 700000 | 4179.7456 | 4132.166 | 997.0558 | 0.00087006 | 26 | 6.9084 | 4.1797 | 4.1322 | 0.99706 | 0.00087006
| 298.15 | 700000 | 4180.1704 | 4136.1743 | 997.3174 | 0.00088994 | 25 | 6.9084 | 4.1802 | 4.1362 | 0.99732 | 0.00088994
| 297.15 | 700000 | 4180.6348 | 4140.124 | 997.5696 | 0.00091057 | 24 | 6.9084 | 4.1806 | 4.1401 | 0.99757 | 0.00091057
| 296.15 | 700000 | 4181.1406 | 4144.0132 | 997.8121 | 0.00093198 | 23 | 6.9084 | 4.1811 | 4.144 | 0.99781 | 0.00093198
| 295.15 | 700000 | 4181.6904 | 4147.8403 | 998.0447 | 0.00095422 | 22 | 6.9084 | 4.1817 | 4.1478 | 0.99804 | 0.00095422
| 294.15 | 700000 | 4182.2871 | 4151.6035 | 998.2674 | 0.00097733 | 21 | 6.9084 | 4.1823 | 4.1516 | 0.99827 | 0.00097733
| 293.15 | 700000 | 4182.9341 | 4155.3018 | 998.4798 | 0.0010013 | 20 | 6.9084 | 4.1829 | 4.1553 | 0.99848 | 0.0010013
| 292.15 | 700000 | 4183.6343 | 4158.9331 | 998.6817 | 0.0010263 | 19 | 6.9084 | 4.1836 | 4.1589 | 0.99868 | 0.0010263
| 291.15 | 700000 | 4184.3926 | 4162.4966 | 998.873 | 0.0010524 | 18 | 6.9084 | 4.1844 | 4.1625 | 0.99887 | 0.0010524
| 290.15 | 700000 | 4185.2129 | 4165.9902 | 999.0533 | 0.0010794 | 17 | 6.9084 | 4.1852 | 4.166 | 0.99905 | 0.0010794
| 289.15 | 700000 | 4186.1001 | 4169.4141 | 999.2225 | 0.0011077 | 16 | 6.9084 | 4.1861 | 4.1694 | 0.99922 | 0.0011077
| 288.15 | 700000 | 4187.0596 | 4172.7656 | 999.3802 | 0.0011371 | 15 | 6.9084 | 4.1871 | 4.1728 | 0.99938 | 0.0011371
| 287.15 | 700000 | 4188.0977 | 4176.0444 | 999.5262 | 0.0011679 | 14 | 6.9084 | 4.1881 | 4.176 | 0.99953 | 0.0011679
| 286.15 | 700000 | 4189.2212 | 4179.25 | 999.6603 | 0.0011999 | 13 | 6.9084 | 4.1892 | 4.1792 | 0.99966 | 0.0011999
| 285.15 | 700000 | 4190.4375 | 4182.3813 | 999.782 | 0.0012335 | 12 | 6.9084 | 4.1904 | 4.1824 | 0.99978 | 0.0012335
| 284.15 | 700000 | 4191.7554 | 4185.4375 | 999.8912 | 0.0012685 | 11 | 6.9084 | 4.1918 | 4.1854 | 0.99989 | 0.0012685
| 283.15 | 700000 | 4193.1831 | 4188.4185 | 999.9874 | 0.0013052 | 10 | 6.9084 | 4.1932 | 4.1884 | 0.99999 | 0.0013052
| 282.15 | 700000 | 4194.7314 | 4191.3237 | 1000.0703 | 0.0013436 | 9 | 6.9084 | 4.1947 | 4.1913 | 1.0001 | 0.0013436
| 281.15 | 700000 | 4196.4121 | 4194.1538 | 1000.1395 | 0.0013839 | 8 | 6.9084 | 4.1964 | 4.1942 | 1.0001 | 0.0013839
| 280.15 | 700000 | 4198.2373 | 4196.9082 | 1000.1946 | 0.0014262 | 7 | 6.9084 | 4.1982 | 4.1969 | 1.0002 | 0.0014262
| 279.15 | 700000 | 4200.2212 | 4199.5879 | 1000.2353 | 0.0014705 | 6 | 6.9084 | 4.2002 | 4.1996 | 1.0002 | 0.0014705
| 278.15 | 700000 | 4202.3794 | 4202.1934 | 1000.261 | 0.0015171 | 5 | 6.9084 | 4.2024 | 4.2022 | 1.0003 | 0.0015171
| 277.15 | 700000 | 4204.7285 | 4204.7251 | 1000.2714 | 0.0015661 | 4 | 6.9084 | 4.2047 | 4.2047 | 1.0003 | 0.0015661
| 276.15 | 700000 | 4207.2881 | 4207.1851 | 1000.2659 | 0.0016177 | 3 | 6.9084 | 4.2073 | 4.2072 | 1.0003 | 0.0016177
| 275.15 | 700000 | 4210.0786 | 4209.5742 | 1000.244 | 0.0016721 | 2 | 6.9084 | 4.2101 | 4.2096 | 1.0002 | 0.0016721
| 274.15 | 700000 | 4213.124 | 4211.895 | 1000.2051 | 0.0017295 | 0.99999 | 6.9084 | 4.2131 | 4.2119 | 1.0002 | 0.0017295
| 273.15 | 700000 | 4216.4492 | 4214.1484 | 1000.1487 | 0.00179 | -6.1035e-06 | 6.9084 | 4.2164 | 4.2141 | 1.0001 | 0.00179
| 473.15 | 600000 | 2194.2478 | 1623.5461 | 2.84 | 1.602e-05 | 200 | 5.9215 | 2.1942 | 1.6235 | 0.00284 | 1.602e-05
| 472.15 | 600000 | 2197.3921 | 1625.2689 | 2.8469 | 1.5978e-05 | 199 | 5.9215 | 2.1974 | 1.6253 | 0.0028469 | 1.5978e-05
| 471.15 | 600000 | 2200.6128 | 1627.04 | 2.8539 | 1.5936e-05 | 198 | 5.9215 | 2.2006 | 1.627 | 0.0028539 | 1.5936e-05
| 470.15 | 600000 | 2203.9131 | 1628.8613 | 2.8609 | 1.5894e-05 | 197 | 5.9215 | 2.2039 | 1.6289 | 0.0028609 | 1.5894e-05
| 469.15 | 600000 | 2207.2952 | 1630.7346 | 2.8679 | 1.5852e-05 | 196 | 5.9215 | 2.2073 | 1.6307 | 0.0028679 | 1.5852e-05
| 468.15 | 600000 | 2210.7622 | 1632.6615 | 2.875 | 1.581e-05 | 195 | 5.9215 | 2.2108 | 1.6327 | 0.002875 | 1.581e-05
| 467.15 | 600000 | 2214.3171 | 1634.6443 | 2.8822 | 1.5769e-05 | 194 | 5.9215 | 2.2143 | 1.6346 | 0.0028822 | 1.5769e-05
| 466.15 | 600000 | 2217.9634 | 1636.6852 | 2.8894 | 1.5727e-05 | 193 | 5.9215 | 2.218 | 1.6367 | 0.0028894 | 1.5727e-05
| 465.15 | 600000 | 2221.7043 | 1638.7865 | 2.8966 | 1.5685e-05 | 192 | 5.9215 | 2.2217 | 1.6388 | 0.0028966 | 1.5685e-05
| 464.15 | 600000 | 2225.5442 | 1640.951 | 2.9039 | 1.5643e-05 | 191 | 5.9215 | 2.2255 | 1.641 | 0.0029039 | 1.5643e-05
| 463.15 | 600000 | 2229.4868 | 1643.1816 | 2.9112 | 1.5601e-05 | 190 | 5.9215 | 2.2295 | 1.6432 | 0.0029112 | 1.5601e-05
| 462.15 | 600000 | 2233.5374 | 1645.4814 | 2.9186 | 1.5559e-05 | 189 | 5.9215 | 2.2335 | 1.6455 | 0.0029186 | 1.5559e-05
| 461.15 | 600000 | 2237.7004 | 1647.854 | 2.9261 | 1.5517e-05 | 188 | 5.9215 | 2.2377 | 1.6479 | 0.0029261 | 1.5517e-05
| 460.15 | 600000 | 2241.9819 | 1650.3031 | 2.9335 | 1.5475e-05 | 187 | 5.9215 | 2.242 | 1.6503 | 0.0029335 | 1.5475e-05
| 459.15 | 600000 | 2246.3877 | 1652.8333 | 2.9411 | 1.5433e-05 | 186 | 5.9215 | 2.2464 | 1.6528 | 0.0029411 | 1.5433e-05
| 458.15 | 600000 | 2250.9248 | 1655.4491 | 2.9486 | 1.5391e-05 | 185 | 5.9215 | 2.2509 | 1.6554 | 0.0029486 | 1.5391e-05
| 457.15 | 600000 | 2255.6008 | 1658.1559 | 2.9563 | 1.535e-05 | 184 | 5.9215 | 2.2556 | 1.6582 | 0.0029563 | 1.535e-05
| 456.15 | 600000 | 2260.4238 | 1660.9595 | 2.964 | 1.5308e-05 | 183 | 5.9215 | 2.2604 | 1.661 | 0.002964 | 1.5308e-05
| 455.15 | 600000 | 2265.4028 | 1663.8667 | 2.9717 | 1.5266e-05 | 182 | 5.9215 | 2.2654 | 1.6639 | 0.0029717 | 1.5266e-05
| 454.15 | 600000 | 2270.5488 | 1666.8845 | 2.9795 | 1.5224e-05 | 181 | 5.9215 | 2.2705 | 1.6669 | 0.0029795 | 1.5224e-05
| 453.15 | 600000 | 2275.8726 | 1670.0215 | 2.9874 | 1.5182e-05 | 180 | 5.9215 | 2.2759 | 1.67 | 0.0029874 | 1.5182e-05
| 452.15 | 600000 | 2281.3875 | 1673.2867 | 2.9953 | 1.514e-05 | 179 | 5.9215 | 2.2814 | 1.6733 | 0.0029953 | 1.514e-05
| 451.15 | 600000 | 2287.1077 | 1676.6907 | 3.0032 | 1.5098e-05 | 178 | 5.9215 | 2.2871 | 1.6767 | 0.0030032 | 1.5098e-05
| 450.15 | 600000 | 2293.0491 | 1680.2449 | 3.0113 | 1.5056e-05 | 177 | 5.9215 | 2.293 | 1.6802 | 0.0030113 | 1.5056e-05
| 449.15 | 600000 | 2299.2302 | 1683.9626 | 3.0193 | 1.5015e-05 | 176 | 5.9215 | 2.2992 | 1.684 | 0.0030193 | 1.5015e-05
| 448.15 | 600000 | 2305.6716 | 1687.8588 | 3.0275 | 1.4973e-05 | 175 | 5.9215 | 2.3057 | 1.6879 | 0.0030275 | 1.4973e-05
| 447.15 | 600000 | 2312.396 | 1691.95 | 3.0357 | 1.4931e-05 | 174 | 5.9215 | 2.3124 | 1.6919 | 0.0030357 | 1.4931e-05
| 446.15 | 600000 | 2319.4292 | 1696.2552 | 3.0439 | 1.4889e-05 | 173 | 5.9215 | 2.3194 | 1.6963 | 0.0030439 | 1.4889e-05
| 445.15 | 600000 | 2326.801 | 1700.7961 | 3.0523 | 1.4847e-05 | 172 | 5.9215 | 2.3268 | 1.7008 | 0.0030523 | 1.4847e-05
| 444.15 | 600000 | 2334.5447 | 1705.5967 | 3.0607 | 1.4805e-05 | 171 | 5.9215 | 2.3345 | 1.7056 | 0.0030607 | 1.4805e-05
| 443.15 | 600000 | 2342.6975 | 1710.6844 | 3.0691 | 1.4764e-05 | 170 | 5.9215 | 2.3427 | 1.7107 | 0.0030691 | 1.4764e-05
| 442.15 | 600000 | 2351.3022 | 1716.0907 | 3.0777 | 1.4722e-05 | 169 | 5.9215 | 2.3513 | 1.7161 | 0.0030777 | 1.4722e-05
| 441.15 | 600000 | 2360.4072 | 1721.8508 | 3.0863 | 1.468e-05 | 168 | 5.9215 | 2.3604 | 1.7219 | 0.0030863 | 1.468e-05
| 440.15 | 600000 | 2370.0676 | 1728.0049 | 3.095 | 1.4638e-05 | 167 | 5.9215 | 2.3701 | 1.728 | 0.003095 | 1.4638e-05
| 439.15 | 600000 | 2380.3457 | 1734.5985 | 3.1037 | 1.4596e-05 | 166 | 5.9215 | 2.3803 | 1.7346 | 0.0031037 | 1.4596e-05
| 438.15 | 600000 | 2391.3125 | 1741.6836 | 3.1125 | 1.4554e-05 | 165 | 5.9215 | 2.3913 | 1.7417 | 0.0031125 | 1.4554e-05
| 437.15 | 600000 | 2403.0488 | 1749.319 | 3.1214 | 1.4513e-05 | 164 | 5.9215 | 2.403 | 1.7493 | 0.0031214 | 1.4513e-05
| 436.15 | 600000 | 2415.6465 | 1757.5718 | 3.1304 | 1.4471e-05 | 163 | 5.9215 | 2.4156 | 1.7576 | 0.0031304 | 1.4471e-05
| 435.15 | 600000 | 2429.2104 | 1766.5179 | 3.1395 | 1.4429e-05 | 162 | 5.9215 | 2.4292 | 1.7665 | 0.0031395 | 1.4429e-05
| 434.15 | 600000 | 2443.8601 | 1776.2445 | 3.1487 | 1.4387e-05 | 161 | 5.9215 | 2.4439 | 1.7762 | 0.0031487 | 1.4387e-05
| 433.15 | 600000 | 2459.7312 | 1786.8497 | 3.1579 | 1.4345e-05 | 160 | 5.9215 | 2.4597 | 1.7868 | 0.0031579 | 1.4345e-05
| 432.15 | 600000 | 2476.9795 | 1798.4462 | 3.1672 | 1.4304e-05 | 159 | 5.9215 | 2.477 | 1.7984 | 0.0031672 | 1.4304e-05
| 431.15 | 600000 | 4332.0571 | 3490.5159 | 909.4041 | 0.00017256 | 158 | 5.9215 | 4.3321 | 3.4905 | 0.9094 | 0.00017256
| 430.15 | 600000 | 4329.1489 | 3494.9465 | 910.3793 | 0.00017374 | 157 | 5.9215 | 4.3291 | 3.4949 | 0.91038 | 0.00017374
| 429.15 | 600000 | 4326.2803 | 3499.3906 | 911.3499 | 0.00017494 | 156 | 5.9215 | 4.3263 | 3.4994 | 0.91135 | 0.00017494
| 428.15 | 600000 | 4323.4502 | 3503.8477 | 912.3158 | 0.00017615 | 155 | 5.9215 | 4.3235 | 3.5038 | 0.91232 | 0.00017615
| 427.15 | 600000 | 4320.6592 | 3508.3181 | 913.2772 | 0.00017739 | 154 | 5.9215 | 4.3207 | 3.5083 | 0.91328 | 0.00017739
| 426.15 | 600000 | 4317.9058 | 3512.8013 | 914.234 | 0.00017864 | 153 | 5.9215 | 4.3179 | 3.5128 | 0.91423 | 0.00017864
| 425.15 | 600000 | 4315.1895 | 3517.2976 | 915.1862 | 0.0001799 | 152 | 5.9215 | 4.3152 | 3.5173 | 0.91519 | 0.0001799
| 424.15 | 600000 | 4312.5103 | 3521.8069 | 916.1339 | 0.00018119 | 151 | 5.9215 | 4.3125 | 3.5218 | 0.91613 | 0.00018119
| 423.15 | 600000 | 4309.8677 | 3526.3289 | 917.077 | 0.00018249 | 150 | 5.9215 | 4.3099 | 3.5263 | 0.91708 | 0.00018249
| 422.15 | 600000 | 4307.2607 | 3530.8635 | 918.0156 | 0.00018381 | 149 | 5.9215 | 4.3073 | 3.5309 | 0.91802 | 0.00018381
| 421.15 | 600000 | 4304.689 | 3535.4109 | 918.9498 | 0.00018515 | 148 | 5.9215 | 4.3047 | 3.5354 | 0.91895 | 0.00018515
| 420.15 | 600000 | 4302.1523 | 3539.9707 | 919.8793 | 0.00018651 | 147 | 5.9215 | 4.3022 | 3.54 | 0.91988 | 0.00018651
| 419.15 | 600000 | 4299.6499 | 3544.543 | 920.8044 | 0.00018789 | 146 | 5.9215 | 4.2996 | 3.5445 | 0.9208 | 0.00018789
| 418.15 | 600000 | 4297.1816 | 3549.1277 | 921.7251 | 0.00018929 | 145 | 5.9215 | 4.2972 | 3.5491 | 0.92173 | 0.00018929
| 417.15 | 600000 | 4294.7466 | 3553.7249 | 922.6412 | 0.00019071 | 144 | 5.9215 | 4.2947 | 3.5537 | 0.92264 | 0.00019071
| 416.15 | 600000 | 4292.3447 | 3558.334 | 923.553 | 0.00019215 | 143 | 5.9215 | 4.2923 | 3.5583 | 0.92355 | 0.00019215
| 415.15 | 600000 | 4289.9751 | 3562.9556 | 924.4603 | 0.00019361 | 142 | 5.9215 | 4.29 | 3.563 | 0.92446 | 0.00019361
| 414.15 | 600000 | 4287.6382 | 3567.5889 | 925.3631 | 0.0001951 | 141 | 5.9215 | 4.2876 | 3.5676 | 0.92536 | 0.0001951
| 413.15 | 600000 | 4285.333 | 3572.2346 | 926.2615 | 0.0001966 | 140 | 5.9215 | 4.2853 | 3.5722 | 0.92626 | 0.0001966
| 412.15 | 600000 | 4283.0591 | 3576.8918 | 927.1555 | 0.00019813 | 139 | 5.9215 | 4.2831 | 3.5769 | 0.92716 | 0.00019813
| 411.15 | 600000 | 4280.8159 | 3581.5613 | 928.045 | 0.00019968 | 138 | 5.9215 | 4.2808 | 3.5816 | 0.92804 | 0.00019968
| 410.15 | 600000 | 4278.6035 | 3586.2422 | 928.9301 | 0.00020126 | 137 | 5.9215 | 4.2786 | 3.5862 | 0.92893 | 0.00020126
| 409.15 | 600000 | 4276.4214 | 3590.9351 | 929.8109 | 0.00020285 | 136 | 5.9215 | 4.2764 | 3.5909 | 0.92981 | 0.00020285
| 408.15 | 600000 | 4274.2695 | 3595.6394 | 930.6872 | 0.00020448 | 135 | 5.9215 | 4.2743 | 3.5956 | 0.93069 | 0.00020448
| 407.15 | 600000 | 4272.1465 | 3600.3555 | 931.5591 | 0.00020613 | 134 | 5.9215 | 4.2721 | 3.6004 | 0.93156 | 0.00020613
| 406.15 | 600000 | 4270.0532 | 3605.0828 | 932.4267 | 0.0002078 | 133 | 5.9215 | 4.2701 | 3.6051 | 0.93243 | 0.0002078
| 405.15 | 600000 | 4267.9883 | 3609.8218 | 933.2899 | 0.0002095 | 132 | 5.9215 | 4.268 | 3.6098 | 0.93329 | 0.0002095
| 404.15 | 600000 | 4265.9521 | 3614.5718 | 934.1487 | 0.00021123 | 131 | 5.9215 | 4.266 | 3.6146 | 0.93415 | 0.00021123
| 403.15 | 600000 | 4263.9438 | 3619.3333 | 935.0031 | 0.00021298 | 130 | 5.9215 | 4.2639 | 3.6193 | 0.935 | 0.00021298
| 402.15 | 600000 | 4261.9634 | 3624.1057 | 935.8531 | 0.00021476 | 129 | 5.9215 | 4.262 | 3.6241 | 0.93585 | 0.00021476
| 401.15 | 600000 | 4260.0107 | 3628.8894 | 936.6988 | 0.00021657 | 128 | 5.9215 | 4.26 | 3.6289 | 0.9367 | 0.00021657
| 400.15 | 600000 | 4258.085 | 3633.6841 | 937.54 | 0.00021841 | 127 | 5.9215 | 4.2581 | 3.6337 | 0.93754 | 0.00021841
| 399.15 | 600000 | 4256.1865 | 3638.4897 | 938.377 | 0.00022028 | 126 | 5.9215 | 4.2562 | 3.6385 | 0.93838 | 0.00022028
| 398.15 | 600000 | 4254.3145 | 3643.3062 | 939.2095 | 0.00022218 | 125 | 5.9215 | 4.2543 | 3.6433 | 0.93921 | 0.00022218
| 397.15 | 600000 | 4252.4692 | 3648.1335 | 940.0376 | 0.00022411 | 124 | 5.9215 | 4.2525 | 3.6481 | 0.94004 | 0.00022411
| 396.15 | 600000 | 4250.6494 | 3652.9714 | 940.8614 | 0.00022607 | 123 | 5.9215 | 4.2506 | 3.653 | 0.94086 | 0.00022607
| 395.15 | 600000 | 4248.856 | 3657.8198 | 941.6808 | 0.00022807 | 122 | 5.9215 | 4.2489 | 3.6578 | 0.94168 | 0.00022807
| 394.15 | 600000 | 4247.0879 | 3662.679 | 942.4958 | 0.0002301 | 121 | 5.9215 | 4.2471 | 3.6627 | 0.9425 | 0.0002301
| 393.15 | 600000 | 4245.3452 | 3667.5486 | 943.3064 | 0.00023216 | 120 | 5.9215 | 4.2453 | 3.6675 | 0.94331 | 0.00023216
| 392.15 | 600000 | 4243.6274 | 3672.4282 | 944.1126 | 0.00023425 | 119 | 5.9215 | 4.2436 | 3.6724 | 0.94411 | 0.00023425
| 391.15 | 600000 | 4241.9351 | 3677.3184 | 944.9144 | 0.00023639 | 118 | 5.9215 | 4.2419 | 3.6773 | 0.94491 | 0.00023639
| 390.15 | 600000 | 4240.2671 | 3682.2188 | 945.7119 | 0.00023855 | 117 | 5.9215 | 4.2403 | 3.6822 | 0.94571 | 0.00023855
| 389.15 | 600000 | 4238.623 | 3687.1289 | 946.5049 | 0.00024076 | 116 | 5.9215 | 4.2386 | 3.6871 | 0.9465 | 0.00024076
| 388.15 | 600000 | 4237.0039 | 3692.0493 | 947.2935 | 0.000243 | 115 | 5.9215 | 4.237 | 3.692 | 0.94729 | 0.000243
| 387.15 | 600000 | 4235.4082 | 3696.9792 | 948.0778 | 0.00024528 | 114 | 5.9215 | 4.2354 | 3.697 | 0.94808 | 0.00024528
| 386.15 | 600000 | 4233.8369 | 3701.9192 | 948.8575 | 0.00024761 | 113 | 5.9215 | 4.2338 | 3.7019 | 0.94886 | 0.00024761
| 385.15 | 600000 | 4232.2891 | 3706.8687 | 949.6329 | 0.00024997 | 112 | 5.9215 | 4.2323 | 3.7069 | 0.94963 | 0.00024997
| 384.15 | 600000 | 4230.7642 | 3711.8276 | 950.4037 | 0.00025237 | 111 | 5.9215 | 4.2308 | 3.7118 | 0.9504 | 0.00025237
| 383.15 | 600000 | 4229.2632 | 3716.7961 | 951.1702 | 0.00025482 | 110 | 5.9215 | 4.2293 | 3.7168 | 0.95117 | 0.00025482
| 382.15 | 600000 | 4227.7852 | 3721.7739 | 951.9323 | 0.00025731 | 109 | 5.9215 | 4.2278 | 3.7218 | 0.95193 | 0.00025731
| 381.15 | 600000 | 4226.3296 | 3726.7607 | 952.6898 | 0.00025985 | 108 | 5.9215 | 4.2263 | 3.7268 | 0.95269 | 0.00025985
| 380.15 | 600000 | 4224.8975 | 3731.7568 | 953.4429 | 0.00026243 | 107 | 5.9215 | 4.2249 | 3.7318 | 0.95344 | 0.00026243
| 379.15 | 600000 | 4223.4878 | 3736.7617 | 954.1914 | 0.00026506 | 106 | 5.9215 | 4.2235 | 3.7368 | 0.95419 | 0.00026506
| 378.15 | 600000 | 4222.1001 | 3741.7754 | 954.9355 | 0.00026773 | 105 | 5.9215 | 4.2221 | 3.7418 | 0.95494 | 0.00026773
| 377.15 | 600000 | 4220.7354 | 3746.7976 | 955.675 | 0.00027046 | 104 | 5.9215 | 4.2207 | 3.7468 | 0.95568 | 0.00027046
| 376.15 | 600000 | 4219.3926 | 3751.8281 | 956.4101 | 0.00027323 | 103 | 5.9215 | 4.2194 | 3.7518 | 0.95641 | 0.00027323
| 375.15 | 600000 | 4218.0718 | 3756.8672 | 957.1406 | 0.00027606 | 102 | 5.9215 | 4.2181 | 3.7569 | 0.95714 | 0.00027606
| 374.15 | 600000 | 4216.7729 | 3761.9143 | 957.8665 | 0.00027894 | 101 | 5.9215 | 4.2168 | 3.7619 | 0.95787 | 0.00027894
| 373.15 | 600000 | 4215.4966 | 3766.9695 | 958.5878 | 0.00028188 | 100 | 5.9215 | 4.2155 | 3.767 | 0.95859 | 0.00028188
| 372.15 | 600000 | 4214.2412 | 3772.0325 | 959.3046 | 0.00028487 | 99 | 5.9215 | 4.2142 | 3.772 | 0.9593 | 0.00028487
| 371.15 | 600000 | 4213.0078 | 3777.103 | 960.0168 | 0.00028792 | 98 | 5.9215 | 4.213 | 3.7771 | 0.96002 | 0.00028792
| 370.15 | 600000 | 4211.7959 | 3782.1812 | 960.7244 | 0.00029102 | 97 | 5.9215 | 4.2118 | 3.7822 | 0.96072 | 0.00029102
| 369.15 | 600000 | 4210.6055 | 3787.2664 | 961.4272 | 0.00029419 | 96 | 5.9215 | 4.2106 | 3.7873 | 0.96143 | 0.00029419
| 368.15 | 600000 | 4209.4365 | 3792.3586 | 962.1255 | 0.00029742 | 95 | 5.9215 | 4.2094 | 3.7924 | 0.96213 | 0.00029742
| 367.15 | 600000 | 4208.2886 | 3797.4575 | 962.8191 | 0.00030071 | 94 | 5.9215 | 4.2083 | 3.7975 | 0.96282 | 0.00030071
| 366.15 | 600000 | 4207.1621 | 3802.5632 | 963.508 | 0.00030407 | 93 | 5.9215 | 4.2072 | 3.8026 | 0.96351 | 0.00030407
| 365.15 | 600000 | 4206.0566 | 3807.6753 | 964.1921 | 0.00030749 | 92 | 5.9215 | 4.2061 | 3.8077 | 0.96419 | 0.00030749
| 364.15 | 600000 | 4204.9722 | 3812.7932 | 964.8716 | 0.00031098 | 91 | 5.9215 | 4.205 | 3.8128 | 0.96487 | 0.00031098
| 363.15 | 600000 | 4203.9092 | 3817.9172 | 965.5463 | 0.00031455 | 90 | 5.9215 | 4.2039 | 3.8179 | 0.96555 | 0.00031455
| 362.15 | 600000 | 4202.8667 | 3823.0466 | 966.2161 | 0.00031818 | 89 | 5.9215 | 4.2029 | 3.823 | 0.96622 | 0.00031818
| 361.15 | 600000 | 4201.8452 | 3828.1814 | 966.8812 | 0.00032189 | 88 | 5.9215 | 4.2018 | 3.8282 | 0.96688 | 0.00032189
| 360.15 | 600000 | 4200.8447 | 3833.321 | 967.5415 | 0.00032567 | 87 | 5.9215 | 4.2008 | 3.8333 | 0.96754 | 0.00032567
| 359.15 | 600000 | 4199.8652 | 3838.4656 | 968.1969 | 0.00032954 | 86 | 5.9215 | 4.1999 | 3.8385 | 0.9682 | 0.00032954
| 358.15 | 600000 | 4198.9062 | 3843.6143 | 968.8474 | 0.00033348 | 85 | 5.9215 | 4.1989 | 3.8436 | 0.96885 | 0.00033348
| 357.15 | 600000 | 4197.9678 | 3848.7671 | 969.493 | 0.00033751 | 84 | 5.9215 | 4.198 | 3.8488 | 0.96949 | 0.00033751
| 356.15 | 600000 | 4197.0508 | 3853.9238 | 970.1337 | 0.00034162 | 83 | 5.9215 | 4.1971 | 3.8539 | 0.97013 | 0.00034162
| 355.15 | 600000 | 4196.1538 | 3859.0837 | 970.7693 | 0.00034582 | 82 | 5.9215 | 4.1962 | 3.8591 | 0.97077 | 0.00034582
| 354.15 | 600000 | 4195.2778 | 3864.2466 | 971.4001 | 0.0003501 | 81 | 5.9215 | 4.1953 | 3.8642 | 0.9714 | 0.0003501
| 353.15 | 600000 | 4194.4224 | 3869.4119 | 972.0258 | 0.00035449 | 80 | 5.9215 | 4.1944 | 3.8694 | 0.97203 | 0.00035449
| 352.15 | 600000 | 4193.5874 | 3874.5796 | 972.6464 | 0.00035896 | 79 | 5.9215 | 4.1936 | 3.8746 | 0.97265 | 0.00035896
| 351.15 | 600000 | 4192.7734 | 3879.749 | 973.2619 | 0.00036354 | 78 | 5.9215 | 4.1928 | 3.8797 | 0.97326 | 0.00036354
| 350.15 | 600000 | 4191.98 | 3884.9197 | 973.8723 | 0.00036821 | 77 | 5.9215 | 4.192 | 3.8849 | 0.97387 | 0.00036821
| 349.15 | 600000 | 4191.207 | 3890.0913 | 974.4775 | 0.00037299 | 76 | 5.9215 | 4.1912 | 3.8901 | 0.97448 | 0.00037299
| 348.15 | 600000 | 4190.4551 | 3895.2632 | 975.0776 | 0.00037788 | 75 | 5.9215 | 4.1905 | 3.8953 | 0.97508 | 0.00037788
| 347.15 | 600000 | 4189.7236 | 3900.4348 | 975.6724 | 0.00038287 | 74 | 5.9215 | 4.1897 | 3.9004 | 0.97567 | 0.00038287
| 346.15 | 600000 | 4189.0122 | 3905.6062 | 976.262 | 0.00038798 | 73 | 5.9215 | 4.189 | 3.9056 | 0.97626 | 0.00038798
| 345.15 | 600000 | 4188.3223 | 3910.7761 | 976.8463 | 0.00039321 | 72 | 5.9215 | 4.1883 | 3.9108 | 0.97685 | 0.00039321
| 344.15 | 600000 | 4187.6523 | 3915.9443 | 977.4251 | 0.00039855 | 71 | 5.9215 | 4.1877 | 3.9159 | 0.97743 | 0.00039855
| 343.15 | 600000 | 4187.0034 | 3921.1104 | 977.9987 | 0.00040402 | 70 | 5.9215 | 4.187 | 3.9211 | 0.978 | 0.00040402
| 342.15 | 600000 | 4186.375 | 3926.2734 | 978.5668 | 0.00040962 | 69 | 5.9215 | 4.1864 | 3.9263 | 0.97857 | 0.00040962
| 341.15 | 600000 | 4185.7671 | 3931.4329 | 979.1294 | 0.00041536 | 68 | 5.9215 | 4.1858 | 3.9314 | 0.97913 | 0.00041536
| 340.15 | 600000 | 4185.1802 | 3936.5884 | 979.6865 | 0.00042122 | 67 | 5.9215 | 4.1852 | 3.9366 | 0.97969 | 0.00042122
| 339.15 | 600000 | 4184.6143 | 3941.7388 | 980.238 | 0.00042723 | 66 | 5.9215 | 4.1846 | 3.9417 | 0.98024 | 0.00042723
| 338.15 | 600000 | 4184.0688 | 3946.8838 | 980.784 | 0.00043339 | 65 | 5.9215 | 4.1841 | 3.9469 | 0.98078 | 0.00043339
| 337.15 | 600000 | 4183.5439 | 3952.0225 | 981.3243 | 0.00043969 | 64 | 5.9215 | 4.1835 | 3.952 | 0.98132 | 0.00043969
| 336.15 | 600000 | 4183.04 | 3957.1543 | 981.8589 | 0.00044615 | 63 | 5.9215 | 4.183 | 3.9572 | 0.98186 | 0.00044615
| 335.15 | 600000 | 4182.5571 | 3962.2781 | 982.3877 | 0.00045277 | 62 | 5.9215 | 4.1826 | 3.9623 | 0.98239 | 0.00045277
| 334.15 | 600000 | 4182.0947 | 3967.3936 | 982.9107 | 0.00045956 | 61 | 5.9215 | 4.1821 | 3.9674 | 0.98291 | 0.00045956
| 333.15 | 600000 | 4181.6533 | 3972.4993 | 983.4279 | 0.00046651 | 60 | 5.9215 | 4.1817 | 3.9725 | 0.98343 | 0.00046651
| 332.15 | 600000 | 4181.2329 | 3977.595 | 983.9391 | 0.00047365 | 59 | 5.9215 | 4.1812 | 3.9776 | 0.98394 | 0.00047365
| 331.15 | 600000 | 4180.8335 | 3982.6794 | 984.4444 | 0.00048097 | 58 | 5.9215 | 4.1808 | 3.9827 | 0.98444 | 0.00048097
| 330.15 | 600000 | 4180.4551 | 3987.7517 | 984.9437 | 0.00048847 | 57 | 5.9215 | 4.1805 | 3.9878 | 0.98494 | 0.00048847
| 329.15 | 600000 | 4180.0981 | 3992.811 | 985.4368 | 0.00049618 | 56 | 5.9215 | 4.1801 | 3.9928 | 0.98544 | 0.00049618
| 328.15 | 600000 | 4179.7617 | 3997.8562 | 985.9238 | 0.00050408 | 55 | 5.9215 | 4.1798 | 3.9979 | 0.98592 | 0.00050408
| 327.15 | 600000 | 4179.4468 | 4002.8865 | 986.4046 | 0.0005122 | 54 | 5.9215 | 4.1794 | 4.0029 | 0.9864 | 0.0005122
| 326.15 | 600000 | 4179.1533 | 4007.9004 | 986.8792 | 0.00052054 | 53 | 5.9215 | 4.1792 | 4.0079 | 0.98688 | 0.00052054
| 325.15 | 600000 | 4178.8813 | 4012.8975 | 987.3473 | 0.0005291 | 52 | 5.9215 | 4.1789 | 4.0129 | 0.98735 | 0.0005291
| 324.15 | 600000 | 4178.6304 | 4017.876 | 987.809 | 0.0005379 | 51 | 5.9215 | 4.1786 | 4.0179 | 0.98781 | 0.0005379
| 323.15 | 600000 | 4178.4009 | 4022.8354 | 988.2643 | 0.00054694 | 50 | 5.9215 | 4.1784 | 4.0228 | 0.98826 | 0.00054694
| 322.15 | 600000 | 4178.1934 | 4027.7739 | 988.713 | 0.00055623 | 49 | 5.9215 | 4.1782 | 4.0278 | 0.98871 | 0.00055623
| 321.15 | 600000 | 4178.0073 | 4032.6909 | 989.155 | 0.00056579 | 48 | 5.9215 | 4.178 | 4.0327 | 0.98915 | 0.00056579
| 320.15 | 600000 | 4177.8438 | 4037.5847 | 989.5903 | 0.00057562 | 47 | 5.9215 | 4.1778 | 4.0376 | 0.98959 | 0.00057562
| 319.15 | 600000 | 4177.7017 | 4042.4541 | 990.0188 | 0.00058573 | 46 | 5.9215 | 4.1777 | 4.0425 | 0.99002 | 0.00058573
| 318.15 | 600000 | 4177.582 | 4047.2979 | 990.4405 | 0.00059614 | 45 | 5.9215 | 4.1776 | 4.0473 | 0.99044 | 0.00059614
| 317.15 | 600000 | 4177.4849 | 4052.1147 | 990.8552 | 0.00060685 | 44 | 5.9215 | 4.1775 | 4.0521 | 0.99086 | 0.00060685
| 316.15 | 600000 | 4177.4102 | 4056.9033 | 991.2628 | 0.00061788 | 43 | 5.9215 | 4.1774 | 4.0569 | 0.99126 | 0.00061788
| 315.15 | 600000 | 4177.3584 | 4061.6619 | 991.6632 | 0.00062924 | 42 | 5.9215 | 4.1774 | 4.0617 | 0.99166 | 0.00062924
| 314.15 | 600000 | 4177.3296 | 4066.3894 | 992.0565 | 0.00064095 | 41 | 5.9215 | 4.1773 | 4.0664 | 0.99206 | 0.00064095
| 313.15 | 600000 | 4177.3247 | 4071.0845 | 992.4423 | 0.00065302 | 40 | 5.9215 | 4.1773 | 4.0711 | 0.99244 | 0.00065302
| 312.15 | 600000 | 4177.3433 | 4075.7451 | 992.8208 | 0.00066546 | 39 | 5.9215 | 4.1773 | 4.0757 | 0.99282 | 0.00066546
| 311.15 | 600000 | 4177.3862 | 4080.3701 | 993.1917 | 0.0006783 | 38 | 5.9215 | 4.1774 | 4.0804 | 0.99319 | 0.0006783
| 310.15 | 600000 | 4177.4536 | 4084.9578 | 993.555 | 0.00069154 | 37 | 5.9215 | 4.1775 | 4.085 | 0.99355 | 0.00069154
| 309.15 | 600000 | 4177.5464 | 4089.5066 | 993.9105 | 0.00070521 | 36 | 5.9215 | 4.1775 | 4.0895 | 0.99391 | 0.00070521
| 308.15 | 600000 | 4177.665 | 4094.0151 | 994.2581 | 0.00071932 | 35 | 5.9215 | 4.1777 | 4.094 | 0.99426 | 0.00071932
| 307.15 | 600000 | 4177.8101 | 4098.4814 | 994.5977 | 0.0007339 | 34 | 5.9215 | 4.1778 | 4.0985 | 0.9946 | 0.0007339
| 306.15 | 600000 | 4177.9819 | 4102.9043 | 994.9292 | 0.00074896 | 33 | 5.9215 | 4.178 | 4.1029 | 0.99493 | 0.00074896
| 305.15 | 600000 | 4178.1816 | 4107.2817 | 995.2524 | 0.00076453 | 32 | 5.9215 | 4.1782 | 4.1073 | 0.99525 | 0.00076453
| 304.15 | 600000 | 4178.4106 | 4111.6118 | 995.5673 | 0.00078064 | 31 | 5.9215 | 4.1784 | 4.1116 | 0.99557 | 0.00078064
| 303.15 | 600000 | 4178.6694 | 4115.8931 | 995.8737 | 0.0007973 | 30 | 5.9215 | 4.1787 | 4.1159 | 0.99587 | 0.0007973
| 302.15 | 600000 | 4178.9595 | 4120.1245 | 996.1714 | 0.00081454 | 29 | 5.9215 | 4.179 | 4.1201 | 0.99617 | 0.00081454
| 301.15 | 600000 | 4179.2817 | 4124.3032 | 996.4603 | 0.0008324 | 28 | 5.9215 | 4.1793 | 4.1243 | 0.99646 | 0.0008324
| 300.15 | 600000 | 4179.6377 | 4128.4282 | 996.7402 | 0.0008509 | 27 | 5.9215 | 4.1796 | 4.1284 | 0.99674 | 0.0008509
| 299.15 | 600000 | 4180.0293 | 4132.498 | 997.0109 | 0.00087008 | 26 | 5.9215 | 4.18 | 4.1325 | 0.99701 | 0.00087008
| 298.15 | 600000 | 4180.458 | 4136.5103 | 997.2725 | 0.00088997 | 25 | 5.9215 | 4.1805 | 4.1365 | 0.99727 | 0.00088997
| 297.15 | 600000 | 4180.9268 | 4140.4639 | 997.5245 | 0.0009106 | 24 | 5.9215 | 4.1809 | 4.1405 | 0.99752 | 0.0009106
| 296.15 | 600000 | 4181.4365 | 4144.3569 | 997.7668 | 0.00093201 | 23 | 5.9215 | 4.1814 | 4.1444 | 0.99777 | 0.00093201
| 295.15 | 600000 | 4181.9907 | 4148.188 | 997.9993 | 0.00095425 | 22 | 5.9215 | 4.182 | 4.1482 | 0.998 | 0.00095425
| 294.15 | 600000 | 4182.5923 | 4151.9556 | 998.2219 | 0.00097736 | 21 | 5.9215 | 4.1826 | 4.152 | 0.99822 | 0.00097736
| 293.15 | 600000 | 4183.2441 | 4155.6577 | 998.4341 | 0.0010014 | 20 | 5.9215 | 4.1832 | 4.1557 | 0.99843 | 0.0010014
| 292.15 | 600000 | 4183.9497 | 4159.2935 | 998.6359 | 0.0010264 | 19 | 5.9215 | 4.1839 | 4.1593 | 0.99864 | 0.0010264
| 291.15 | 600000 | 4184.7134 | 4162.8613 | 998.827 | 0.0010524 | 18 | 5.9215 | 4.1847 | 4.1629 | 0.99883 | 0.0010524
| 290.15 | 600000 | 4185.5396 | 4166.3599 | 999.0071 | 0.0010795 | 17 | 5.9215 | 4.1855 | 4.1664 | 0.99901 | 0.0010795
| 289.15 | 600000 | 4186.4326 | 4169.7876 | 999.1761 | 0.0011077 | 16 | 5.9215 | 4.1864 | 4.1698 | 0.99918 | 0.0011077
| 288.15 | 600000 | 4187.3989 | 4173.144 | 999.3336 | 0.0011372 | 15 | 5.9215 | 4.1874 | 4.1731 | 0.99933 | 0.0011372
| 287.15 | 600000 | 4188.4438 | 4176.4282 | 999.4794 | 0.0011679 | 14 | 5.9215 | 4.1884 | 4.1764 | 0.99948 | 0.0011679
| 286.15 | 600000 | 4189.5742 | 4179.6387 | 999.6133 | 0.0012 | 13 | 5.9215 | 4.1896 | 4.1796 | 0.99961 | 0.0012
| 285.15 | 600000 | 4190.7983 | 4182.7749 | 999.7348 | 0.0012336 | 12 | 5.9215 | 4.1908 | 4.1828 | 0.99973 | 0.0012336
| 284.15 | 600000 | 4192.124 | 4185.8364 | 999.8437 | 0.0012686 | 11 | 5.9215 | 4.1921 | 4.1858 | 0.99984 | 0.0012686
| 283.15 | 600000 | 4193.5601 | 4188.8228 | 999.9396 | 0.0013053 | 10 | 5.9215 | 4.1936 | 4.1888 | 0.99994 | 0.0013053
| 282.15 | 600000 | 4195.1177 | 4191.7339 | 1000.0223 | 0.0013438 | 9 | 5.9215 | 4.1951 | 4.1917 | 1 | 0.0013438
| 281.15 | 600000 | 4196.8076 | 4194.5693 | 1000.0912 | 0.0013841 | 8 | 5.9215 | 4.1968 | 4.1946 | 1.0001 | 0.0013841
| 280.15 | 600000 | 4198.6431 | 4197.3301 | 1000.1461 | 0.0014263 | 7 | 5.9215 | 4.1986 | 4.1973 | 1.0001 | 0.0014263
| 279.15 | 600000 | 4200.6377 | 4200.0156 | 1000.1865 | 0.0014707 | 6 | 5.9215 | 4.2006 | 4.2 | 1.0002 | 0.0014707
| 278.15 | 600000 | 4202.8071 | 4202.6274 | 1000.212 | 0.0015173 | 5 | 5.9215 | 4.2028 | 4.2026 | 1.0002 | 0.0015173
| 277.15 | 600000 | 4205.1689 | 4205.166 | 1000.222 | 0.0015663 | 4 | 5.9215 | 4.2052 | 4.2052 | 1.0002 | 0.0015663
| 276.15 | 600000 | 4207.7412 | 4207.6328 | 1000.2162 | 0.0016179 | 3 | 5.9215 | 4.2077 | 4.2076 | 1.0002 | 0.0016179
| 275.15 | 600000 | 4210.5454 | 4210.0293 | 1000.1939 | 0.0016723 | 2 | 5.9215 | 4.2105 | 4.21 | 1.0002 | 0.0016723
| 274.15 | 600000 | 4213.605 | 4212.3574 | 1000.1547 | 0.0017297 | 0.99999 | 5.9215 | 4.2136 | 4.2124 | 1.0002 | 0.0017297
| 273.15 | 600000 | 4216.9458 | 4214.6191 | 1000.0978 | 0.0017903 | -6.1035e-06 | 5.9215 | 4.2169 | 4.2146 | 1.0001 | 0.0017903
| 473.15 | 500000 | 2144.8416 | 1595.8622 | 2.3528 | 1.6052e-05 | 200 | 4.9346 | 2.1448 | 1.5959 | 0.0023528 | 1.6052e-05
| 472.15 | 500000 | 2147.189 | 1597.1145 | 2.3583 | 1.601e-05 | 199 | 4.9346 | 2.1472 | 1.5971 | 0.0023583 | 1.601e-05
| 471.15 | 500000 | 2149.5933 | 1598.403 | 2.364 | 1.5968e-05 | 198 | 4.9346 | 2.1496 | 1.5984 | 0.002364 | 1.5968e-05
| 470.15 | 500000 | 2152.0559 | 1599.7289 | 2.3696 | 1.5927e-05 | 197 | 4.9346 | 2.1521 | 1.5997 | 0.0023696 | 1.5927e-05
| 469.15 | 500000 | 2154.5784 | 1601.093 | 2.3753 | 1.5885e-05 | 196 | 4.9346 | 2.1546 | 1.6011 | 0.0023753 | 1.5885e-05
| 468.15 | 500000 | 2157.1626 | 1602.4966 | 2.381 | 1.5843e-05 | 195 | 4.9346 | 2.1572 | 1.6025 | 0.002381 | 1.5843e-05
| 467.15 | 500000 | 2159.8098 | 1603.9407 | 2.3868 | 1.5802e-05 | 194 | 4.9346 | 2.1598 | 1.6039 | 0.0023868 | 1.5802e-05
| 466.15 | 500000 | 2162.5225 | 1605.4264 | 2.3926 | 1.576e-05 | 193 | 4.9346 | 2.1625 | 1.6054 | 0.0023926 | 1.576e-05
| 465.15 | 500000 | 2165.302 | 1606.9551 | 2.3984 | 1.5719e-05 | 192 | 4.9346 | 2.1653 | 1.607 | 0.0023984 | 1.5719e-05
| 464.15 | 500000 | 2168.1506 | 1608.528 | 2.4043 | 1.5677e-05 | 191 | 4.9346 | 2.1682 | 1.6085 | 0.0024043 | 1.5677e-05
| 463.15 | 500000 | 2171.0706 | 1610.1467 | 2.4102 | 1.5636e-05 | 190 | 4.9346 | 2.1711 | 1.6101 | 0.0024102 | 1.5636e-05
| 462.15 | 500000 | 2174.064 | 1611.8127 | 2.4161 | 1.5594e-05 | 189 | 4.9346 | 2.1741 | 1.6118 | 0.0024161 | 1.5594e-05
| 461.15 | 500000 | 2177.1335 | 1613.5276 | 2.4221 | 1.5552e-05 | 188 | 4.9346 | 2.1771 | 1.6135 | 0.0024221 | 1.5552e-05
| 460.15 | 500000 | 2180.282 | 1615.2933 | 2.4281 | 1.5511e-05 | 187 | 4.9346 | 2.1803 | 1.6153 | 0.0024281 | 1.5511e-05
| 459.15 | 500000 | 2183.512 | 1617.1117 | 2.4341 | 1.5469e-05 | 186 | 4.9346 | 2.1835 | 1.6171 | 0.0024341 | 1.5469e-05
| 458.15 | 500000 | 2186.8269 | 1618.9849 | 2.4402 | 1.5428e-05 | 185 | 4.9346 | 2.1868 | 1.619 | 0.0024402 | 1.5428e-05
| 457.15 | 500000 | 2190.2297 | 1620.9152 | 2.4464 | 1.5386e-05 | 184 | 4.9346 | 2.1902 | 1.6209 | 0.0024464 | 1.5386e-05
| 456.15 | 500000 | 2193.7244 | 1622.905 | 2.4525 | 1.5345e-05 | 183 | 4.9346 | 2.1937 | 1.6229 | 0.0024525 | 1.5345e-05
| 455.15 | 500000 | 2197.3149 | 1624.9573 | 2.4587 | 1.5303e-05 | 182 | 4.9346 | 2.1973 | 1.625 | 0.0024587 | 1.5303e-05
| 454.15 | 500000 | 2201.0054 | 1627.0748 | 2.465 | 1.5262e-05 | 181 | 4.9346 | 2.201 | 1.6271 | 0.002465 | 1.5262e-05
| 453.15 | 500000 | 2204.8008 | 1629.2612 | 2.4712 | 1.522e-05 | 180 | 4.9346 | 2.2048 | 1.6293 | 0.0024712 | 1.522e-05
| 452.15 | 500000 | 2208.7063 | 1631.52 | 2.4776 | 1.5179e-05 | 179 | 4.9346 | 2.2087 | 1.6315 | 0.0024776 | 1.5179e-05
| 451.15 | 500000 | 2212.7275 | 1633.8552 | 2.4839 | 1.5137e-05 | 178 | 4.9346 | 2.2127 | 1.6339 | 0.0024839 | 1.5137e-05
| 450.15 | 500000 | 2216.8711 | 1636.2714 | 2.4903 | 1.5096e-05 | 177 | 4.9346 | 2.2169 | 1.6363 | 0.0024903 | 1.5096e-05
| 449.15 | 500000 | 2221.144 | 1638.7734 | 2.4968 | 1.5054e-05 | 176 | 4.9346 | 2.2211 | 1.6388 | 0.0024968 | 1.5054e-05
| 448.15 | 500000 | 2225.5537 | 1641.3672 | 2.5033 | 1.5013e-05 | 175 | 4.9346 | 2.2256 | 1.6414 | 0.0025033 | 1.5013e-05
| 447.15 | 500000 | 2230.1094 | 1644.0587 | 2.5098 | 1.4972e-05 | 174 | 4.9346 | 2.2301 | 1.6441 | 0.0025098 | 1.4972e-05
| 446.15 | 500000 | 2234.8203 | 1646.8551 | 2.5164 | 1.493e-05 | 173 | 4.9346 | 2.2348 | 1.6469 | 0.0025164 | 1.493e-05
| 445.15 | 500000 | 2239.6975 | 1649.764 | 2.523 | 1.4889e-05 | 172 | 4.9346 | 2.2397 | 1.6498 | 0.002523 | 1.4889e-05
| 444.15 | 500000 | 2244.7532 | 1652.7944 | 2.5297 | 1.4847e-05 | 171 | 4.9346 | 2.2448 | 1.6528 | 0.0025297 | 1.4847e-05
| 443.15 | 500000 | 2250.0007 | 1655.9562 | 2.5364 | 1.4806e-05 | 170 | 4.9346 | 2.25 | 1.656 | 0.0025364 | 1.4806e-05
| 442.15 | 500000 | 2255.4556 | 1659.2603 | 2.5432 | 1.4765e-05 | 169 | 4.9346 | 2.2555 | 1.6593 | 0.0025432 | 1.4765e-05
| 441.15 | 500000 | 2261.1348 | 1662.7194 | 2.55 | 1.4723e-05 | 168 | 4.9346 | 2.2611 | 1.6627 | 0.00255 | 1.4723e-05
| 440.15 | 500000 | 2267.0576 | 1666.3477 | 2.5569 | 1.4682e-05 | 167 | 4.9346 | 2.2671 | 1.6663 | 0.0025569 | 1.4682e-05
| 439.15 | 500000 | 2273.2458 | 1670.161 | 2.5638 | 1.464e-05 | 166 | 4.9346 | 2.2732 | 1.6702 | 0.0025638 | 1.464e-05
| 438.15 | 500000 | 2279.7244 | 1674.1777 | 2.5708 | 1.4599e-05 | 165 | 4.9346 | 2.2797 | 1.6742 | 0.0025708 | 1.4599e-05
| 437.15 | 500000 | 2286.521 | 1678.4181 | 2.5778 | 1.4558e-05 | 164 | 4.9346 | 2.2865 | 1.6784 | 0.0025778 | 1.4558e-05
| 436.15 | 500000 | 2293.6672 | 1682.9054 | 2.5849 | 1.4516e-05 | 163 | 4.9346 | 2.2937 | 1.6829 | 0.0025849 | 1.4516e-05
| 435.15 | 500000 | 2301.1987 | 1687.6661 | 2.592 | 1.4475e-05 | 162 | 4.9346 | 2.3012 | 1.6877 | 0.002592 | 1.4475e-05
| 434.15 | 500000 | 2309.1565 | 1692.73 | 2.5992 | 1.4434e-05 | 161 | 4.9346 | 2.3092 | 1.6927 | 0.0025992 | 1.4434e-05
| 433.15 | 500000 | 2317.5862 | 1698.1311 | 2.6065 | 1.4392e-05 | 160 | 4.9346 | 2.3176 | 1.6981 | 0.0026065 | 1.4392e-05
| 432.15 | 500000 | 2326.5403 | 1703.908 | 2.6138 | 1.4351e-05 | 159 | 4.9346 | 2.3265 | 1.7039 | 0.0026138 | 1.4351e-05
| 431.15 | 500000 | 2336.0786 | 1710.1046 | 2.6212 | 1.431e-05 | 158 | 4.9346 | 2.3361 | 1.7101 | 0.0026212 | 1.431e-05
| 430.15 | 500000 | 2346.269 | 1716.7708 | 2.6286 | 1.4268e-05 | 157 | 4.9346 | 2.3463 | 1.7168 | 0.0026286 | 1.4268e-05
| 429.15 | 500000 | 2357.1887 | 1723.9633 | 2.6361 | 1.4227e-05 | 156 | 4.9346 | 2.3572 | 1.724 | 0.0026361 | 1.4227e-05
| 428.15 | 500000 | 2368.9258 | 1731.7468 | 2.6437 | 1.4186e-05 | 155 | 4.9346 | 2.3689 | 1.7317 | 0.0026437 | 1.4186e-05
| 427.15 | 500000 | 2381.5808 | 1740.1951 | 2.6513 | 1.4145e-05 | 154 | 4.9346 | 2.3816 | 1.7402 | 0.0026513 | 1.4145e-05
| 426.15 | 500000 | 2395.2681 | 1749.3918 | 2.659 | 1.4103e-05 | 153 | 4.9346 | 2.3953 | 1.7494 | 0.002659 | 1.4103e-05
| 425.15 | 500000 | 2410.1187 | 1759.4326 | 2.6668 | 1.4062e-05 | 152 | 4.9346 | 2.4101 | 1.7594 | 0.0026668 | 1.4062e-05
| 424.15 | 500000 | 4312.8384 | 3521.8987 | 916.0768 | 0.00018116 | 151 | 4.9346 | 4.3128 | 3.5219 | 0.91608 | 0.00018116
| 423.15 | 500000 | 4310.1924 | 3526.4211 | 917.0202 | 0.00018247 | 150 | 4.9346 | 4.3102 | 3.5264 | 0.91702 | 0.00018247
| 422.15 | 500000 | 4307.5825 | 3530.9565 | 917.959 | 0.00018379 | 149 | 4.9346 | 4.3076 | 3.531 | 0.91796 | 0.00018379
| 421.15 | 500000 | 4305.0078 | 3535.5046 | 918.8934 | 0.00018513 | 148 | 4.9346 | 4.305 | 3.5355 | 0.91889 | 0.00018513
| 420.15 | 500000 | 4302.4683 | 3540.0652 | 919.8233 | 0.00018649 | 147 | 4.9346 | 4.3025 | 3.5401 | 0.91982 | 0.00018649
| 419.15 | 500000 | 4299.9629 | 3544.6382 | 920.7487 | 0.00018787 | 146 | 4.9346 | 4.3 | 3.5446 | 0.92075 | 0.00018787
| 418.15 | 500000 | 4297.4917 | 3549.2236 | 921.6696 | 0.00018927 | 145 | 4.9346 | 4.2975 | 3.5492 | 0.92167 | 0.00018927
| 417.15 | 500000 | 4295.0537 | 3553.8213 | 922.586 | 0.00019069 | 144 | 4.9346 | 4.2951 | 3.5538 | 0.92259 | 0.00019069
| 416.15 | 500000 | 4292.6489 | 3558.4314 | 923.498 | 0.00019213 | 143 | 4.9346 | 4.2926 | 3.5584 | 0.9235 | 0.00019213
| 415.15 | 500000 | 4290.2773 | 3563.0535 | 924.4055 | 0.00019359 | 142 | 4.9346 | 4.2903 | 3.5631 | 0.92441 | 0.00019359
| 414.15 | 500000 | 4287.9375 | 3567.688 | 925.3086 | 0.00019507 | 141 | 4.9346 | 4.2879 | 3.5677 | 0.92531 | 0.00019507
| 413.15 | 500000 | 4285.6294 | 3572.3342 | 926.2072 | 0.00019658 | 140 | 4.9346 | 4.2856 | 3.5723 | 0.92621 | 0.00019658
| 412.15 | 500000 | 4283.353 | 3576.9924 | 927.1014 | 0.0001981 | 139 | 4.9346 | 4.2834 | 3.577 | 0.9271 | 0.0001981
| 411.15 | 500000 | 4281.1079 | 3581.6626 | 927.9912 | 0.00019966 | 138 | 4.9346 | 4.2811 | 3.5817 | 0.92799 | 0.00019966
| 410.15 | 500000 | 4278.8931 | 3586.3445 | 928.8766 | 0.00020123 | 137 | 4.9346 | 4.2789 | 3.5863 | 0.92888 | 0.00020123
| 409.15 | 500000 | 4276.7085 | 3591.0381 | 929.7576 | 0.00020283 | 136 | 4.9346 | 4.2767 | 3.591 | 0.92976 | 0.00020283
| 408.15 | 500000 | 4274.5537 | 3595.7434 | 930.6342 | 0.00020445 | 135 | 4.9346 | 4.2746 | 3.5957 | 0.93063 | 0.00020445
| 407.15 | 500000 | 4272.4287 | 3600.4602 | 931.5063 | 0.0002061 | 134 | 4.9346 | 4.2724 | 3.6005 | 0.93151 | 0.0002061
| 406.15 | 500000 | 4270.333 | 3605.1887 | 932.3741 | 0.00020777 | 133 | 4.9346 | 4.2703 | 3.6052 | 0.93237 | 0.00020777
| 405.15 | 500000 | 4268.2661 | 3609.9285 | 933.2375 | 0.00020947 | 132 | 4.9346 | 4.2683 | 3.6099 | 0.93324 | 0.00020947
| 404.15 | 500000 | 4266.2275 | 3614.6794 | 934.0965 | 0.0002112 | 131 | 4.9346 | 4.2662 | 3.6147 | 0.9341 | 0.0002112
| 403.15 | 500000 | 4264.2173 | 3619.4419 | 934.9511 | 0.00021295 | 130 | 4.9346 | 4.2642 | 3.6194 | 0.93495 | 0.00021295
| 402.15 | 500000 | 4262.2354 | 3624.2153 | 935.8013 | 0.00021474 | 129 | 4.9346 | 4.2622 | 3.6242 | 0.9358 | 0.00021474
| 401.15 | 500000 | 4260.2803 | 3629 | 936.6472 | 0.00021655 | 128 | 4.9346 | 4.2603 | 3.629 | 0.93665 | 0.00021655
| 400.15 | 500000 | 4258.353 | 3633.7959 | 937.4887 | 0.00021839 | 127 | 4.9346 | 4.2584 | 3.6338 | 0.93749 | 0.00021839
| 399.15 | 500000 | 4256.4521 | 3638.6025 | 938.3258 | 0.00022025 | 126 | 4.9346 | 4.2565 | 3.6386 | 0.93833 | 0.00022025
| 398.15 | 500000 | 4254.5786 | 3643.4199 | 939.1585 | 0.00022215 | 125 | 4.9346 | 4.2546 | 3.6434 | 0.93916 | 0.00022215
| 397.15 | 500000 | 4252.731 | 3648.2483 | 939.9869 | 0.00022408 | 124 | 4.9346 | 4.2527 | 3.6482 | 0.93999 | 0.00022408
| 396.15 | 500000 | 4250.9097 | 3653.0874 | 940.8109 | 0.00022605 | 123 | 4.9346 | 4.2509 | 3.6531 | 0.94081 | 0.00022605
| 395.15 | 500000 | 4249.1147 | 3657.937 | 941.6304 | 0.00022804 | 122 | 4.9346 | 4.2491 | 3.6579 | 0.94163 | 0.00022804
| 394.15 | 500000 | 4247.3447 | 3662.7971 | 942.4456 | 0.00023007 | 121 | 4.9346 | 4.2473 | 3.6628 | 0.94245 | 0.00023007
| 393.15 | 500000 | 4245.6006 | 3667.6677 | 943.2564 | 0.00023213 | 120 | 4.9346 | 4.2456 | 3.6677 | 0.94326 | 0.00023213
| 392.15 | 500000 | 4243.8813 | 3672.5488 | 944.0628 | 0.00023423 | 119 | 4.9346 | 4.2439 | 3.6725 | 0.94406 | 0.00023423
| 391.15 | 500000 | 4242.187 | 3677.4402 | 944.8648 | 0.00023636 | 118 | 4.9346 | 4.2422 | 3.6774 | 0.94486 | 0.00023636
| 390.15 | 500000 | 4240.5176 | 3682.3416 | 945.6624 | 0.00023853 | 117 | 4.9346 | 4.2405 | 3.6823 | 0.94566 | 0.00023853
| 389.15 | 500000 | 4238.8721 | 3687.2532 | 946.4556 | 0.00024073 | 116 | 4.9346 | 4.2389 | 3.6873 | 0.94646 | 0.00024073
| 388.15 | 500000 | 4237.2515 | 3692.1746 | 947.2444 | 0.00024298 | 115 | 4.9346 | 4.2373 | 3.6922 | 0.94724 | 0.00024298
| 387.15 | 500000 | 4235.6548 | 3697.106 | 948.0288 | 0.00024526 | 114 | 4.9346 | 4.2357 | 3.6971 | 0.94803 | 0.00024526
| 386.15 | 500000 | 4234.0815 | 3702.0471 | 948.8088 | 0.00024758 | 113 | 4.9346 | 4.2341 | 3.702 | 0.94881 | 0.00024758
| 385.15 | 500000 | 4232.5322 | 3706.998 | 949.5843 | 0.00024994 | 112 | 4.9346 | 4.2325 | 3.707 | 0.94958 | 0.00024994
| 384.15 | 500000 | 4231.0063 | 3711.9583 | 950.3553 | 0.00025235 | 111 | 4.9346 | 4.231 | 3.712 | 0.95036 | 0.00025235
| 383.15 | 500000 | 4229.5039 | 3716.9282 | 951.1219 | 0.00025479 | 110 | 4.9346 | 4.2295 | 3.7169 | 0.95112 | 0.00025479
| 382.15 | 500000 | 4228.0244 | 3721.9072 | 951.8842 | 0.00025728 | 109 | 4.9346 | 4.228 | 3.7219 | 0.95188 | 0.00025728
| 381.15 | 500000 | 4226.5684 | 3726.8955 | 952.6418 | 0.00025982 | 108 | 4.9346 | 4.2266 | 3.7269 | 0.95264 | 0.00025982
| 380.15 | 500000 | 4225.1348 | 3731.8928 | 953.395 | 0.0002624 | 107 | 4.9346 | 4.2251 | 3.7319 | 0.9534 | 0.0002624
| 379.15 | 500000 | 4223.7236 | 3736.8992 | 954.1437 | 0.00026503 | 106 | 4.9346 | 4.2237 | 3.7369 | 0.95414 | 0.00026503
| 378.15 | 500000 | 4222.3354 | 3741.9143 | 954.8879 | 0.00026771 | 105 | 4.9346 | 4.2223 | 3.7419 | 0.95489 | 0.00026771
| 377.15 | 500000 | 4220.9692 | 3746.938 | 955.6277 | 0.00027043 | 104 | 4.9346 | 4.221 | 3.7469 | 0.95563 | 0.00027043
| 376.15 | 500000 | 4219.6255 | 3751.9702 | 956.3629 | 0.00027321 | 103 | 4.9346 | 4.2196 | 3.752 | 0.95636 | 0.00027321
| 375.15 | 500000 | 4218.3037 | 3757.0107 | 957.0934 | 0.00027604 | 102 | 4.9346 | 4.2183 | 3.757 | 0.95709 | 0.00027604
| 374.15 | 500000 | 4217.0044 | 3762.0593 | 957.8195 | 0.00027892 | 101 | 4.9346 | 4.217 | 3.7621 | 0.95782 | 0.00027892
| 373.15 | 500000 | 4215.7266 | 3767.116 | 958.541 | 0.00028185 | 100 | 4.9346 | 4.2157 | 3.7671 | 0.95854 | 0.00028185
| 372.15 | 500000 | 4214.4707 | 3772.1807 | 959.2579 | 0.00028484 | 99 | 4.9346 | 4.2145 | 3.7722 | 0.95926 | 0.00028484
| 371.15 | 500000 | 4213.2363 | 3777.2527 | 959.9702 | 0.00028789 | 98 | 4.9346 | 4.2132 | 3.7773 | 0.95997 | 0.00028789
| 370.15 | 500000 | 4212.0234 | 3782.3323 | 960.6779 | 0.000291 | 97 | 4.9346 | 4.212 | 3.7823 | 0.96068 | 0.000291
| 369.15 | 500000 | 4210.8325 | 3787.4192 | 961.3809 | 0.00029416 | 96 | 4.9346 | 4.2108 | 3.7874 | 0.96138 | 0.00029416
| 368.15 | 500000 | 4209.6626 | 3792.5132 | 962.0793 | 0.00029739 | 95 | 4.9346 | 4.2097 | 3.7925 | 0.96208 | 0.00029739
| 367.15 | 500000 | 4208.5142 | 3797.6138 | 962.773 | 0.00030068 | 94 | 4.9346 | 4.2085 | 3.7976 | 0.96277 | 0.00030068
| 366.15 | 500000 | 4207.3867 | 3802.7212 | 963.462 | 0.00030404 | 93 | 4.9346 | 4.2074 | 3.8027 | 0.96346 | 0.00030404
| 365.15 | 500000 | 4206.2808 | 3807.835 | 964.1463 | 0.00030747 | 92 | 4.9346 | 4.2063 | 3.8078 | 0.96415 | 0.00030747
| 364.15 | 500000 | 4205.1958 | 3812.9546 | 964.8259 | 0.00031096 | 91 | 4.9346 | 4.2052 | 3.813 | 0.96483 | 0.00031096
| 363.15 | 500000 | 4204.1318 | 3818.0803 | 965.5006 | 0.00031452 | 90 | 4.9346 | 4.2041 | 3.8181 | 0.9655 | 0.00031452
| 362.15 | 500000 | 4203.0889 | 3823.2117 | 966.1707 | 0.00031815 | 89 | 4.9346 | 4.2031 | 3.8232 | 0.96617 | 0.00031815
| 361.15 | 500000 | 4202.0669 | 3828.3481 | 966.8358 | 0.00032186 | 88 | 4.9346 | 4.2021 | 3.8283 | 0.96684 | 0.00032186
| 360.15 | 500000 | 4201.0659 | 3833.4897 | 967.4962 | 0.00032565 | 87 | 4.9346 | 4.2011 | 3.8335 | 0.9675 | 0.00032565
| 359.15 | 500000 | 4200.0859 | 3838.636 | 968.1517 | 0.00032951 | 86 | 4.9346 | 4.2001 | 3.8386 | 0.96815 | 0.00032951
| 358.15 | 500000 | 4199.1265 | 3843.7866 | 968.8023 | 0.00033345 | 85 | 4.9346 | 4.1991 | 3.8438 | 0.9688 | 0.00033345
| 357.15 | 500000 | 4198.188 | 3848.9414 | 969.448 | 0.00033748 | 84 | 4.9346 | 4.1982 | 3.8489 | 0.96945 | 0.00033748
| 356.15 | 500000 | 4197.2705 | 3854.1001 | 970.0887 | 0.00034159 | 83 | 4.9346 | 4.1973 | 3.8541 | 0.97009 | 0.00034159
| 355.15 | 500000 | 4196.373 | 3859.262 | 970.7245 | 0.00034579 | 82 | 4.9346 | 4.1964 | 3.8593 | 0.97072 | 0.00034579
| 354.15 | 500000 | 4195.4971 | 3864.4268 | 971.3553 | 0.00035008 | 81 | 4.9346 | 4.1955 | 3.8644 | 0.97136 | 0.00035008
| 353.15 | 500000 | 4194.6411 | 3869.5942 | 971.9811 | 0.00035446 | 80 | 4.9346 | 4.1946 | 3.8696 | 0.97198 | 0.00035446
| 352.15 | 500000 | 4193.8066 | 3874.7639 | 972.6017 | 0.00035894 | 79 | 4.9346 | 4.1938 | 3.8748 | 0.9726 | 0.00035894
| 351.15 | 500000 | 4192.9922 | 3879.9353 | 973.2173 | 0.00036351 | 78 | 4.9346 | 4.193 | 3.8799 | 0.97322 | 0.00036351
| 350.15 | 500000 | 4192.1987 | 3885.1079 | 973.8279 | 0.00036818 | 77 | 4.9346 | 4.1922 | 3.8851 | 0.97383 | 0.00036818
| 349.15 | 500000 | 4191.4258 | 3890.2817 | 974.4332 | 0.00037296 | 76 | 4.9346 | 4.1914 | 3.8903 | 0.97443 | 0.00037296
| 348.15 | 500000 | 4190.6733 | 3895.4558 | 975.0333 | 0.00037785 | 75 | 4.9346 | 4.1907 | 3.8955 | 0.97503 | 0.00037785
| 347.15 | 500000 | 4189.9419 | 3900.6296 | 975.6282 | 0.00038285 | 74 | 4.9346 | 4.1899 | 3.9006 | 0.97563 | 0.00038285
| 346.15 | 500000 | 4189.231 | 3905.803 | 976.2178 | 0.00038796 | 73 | 4.9346 | 4.1892 | 3.9058 | 0.97622 | 0.00038796
| 345.15 | 500000 | 4188.5405 | 3910.9753 | 976.8021 | 0.00039318 | 72 | 4.9346 | 4.1885 | 3.911 | 0.9768 | 0.00039318
| 344.15 | 500000 | 4187.8711 | 3916.1458 | 977.3811 | 0.00039853 | 71 | 4.9346 | 4.1879 | 3.9161 | 0.97738 | 0.00039853
| 343.15 | 500000 | 4187.2222 | 3921.314 | 977.9547 | 0.000404 | 70 | 4.9346 | 4.1872 | 3.9213 | 0.97795 | 0.000404
| 342.15 | 500000 | 4186.5938 | 3926.4792 | 978.5228 | 0.0004096 | 69 | 4.9346 | 4.1866 | 3.9265 | 0.97852 | 0.0004096
| 341.15 | 500000 | 4185.9863 | 3931.6411 | 979.0855 | 0.00041533 | 68 | 4.9346 | 4.186 | 3.9316 | 0.97909 | 0.00041533
| 340.15 | 500000 | 4185.3999 | 3936.7988 | 979.6427 | 0.0004212 | 67 | 4.9346 | 4.1854 | 3.9368 | 0.97964 | 0.0004212
| 339.15 | 500000 | 4184.834 | 3941.9517 | 980.1943 | 0.00042721 | 66 | 4.9346 | 4.1848 | 3.942 | 0.98019 | 0.00042721
| 338.15 | 500000 | 4184.2886 | 3947.0991 | 980.7403 | 0.00043336 | 65 | 4.9346 | 4.1843 | 3.9471 | 0.98074 | 0.00043336
| 337.15 | 500000 | 4183.7642 | 3952.2402 | 981.2806 | 0.00043967 | 64 | 4.9346 | 4.1838 | 3.9522 | 0.98128 | 0.00043967
| 336.15 | 500000 | 4183.2607 | 3957.3743 | 981.8152 | 0.00044613 | 63 | 4.9346 | 4.1833 | 3.9574 | 0.98182 | 0.00044613
| 335.15 | 500000 | 4182.7783 | 3962.5007 | 982.3441 | 0.00045275 | 62 | 4.9346 | 4.1828 | 3.9625 | 0.98234 | 0.00045275
| 334.15 | 500000 | 4182.3164 | 3967.6187 | 982.8671 | 0.00045953 | 61 | 4.9346 | 4.1823 | 3.9676 | 0.98287 | 0.00045953
| 333.15 | 500000 | 4181.876 | 3972.7271 | 983.3843 | 0.00046649 | 60 | 4.9346 | 4.1819 | 3.9727 | 0.98338 | 0.00046649
| 332.15 | 500000 | 4181.4561 | 3977.8252 | 983.8956 | 0.00047363 | 59 | 4.9346 | 4.1815 | 3.9778 | 0.9839 | 0.00047363
| 331.15 | 500000 | 4181.0571 | 3982.9121 | 984.4009 | 0.00048094 | 58 | 4.9346 | 4.1811 | 3.9829 | 0.9844 | 0.00048094
| 330.15 | 500000 | 4180.6797 | 3987.9871 | 984.9002 | 0.00048845 | 57 | 4.9346 | 4.1807 | 3.988 | 0.9849 | 0.00048845
| 329.15 | 500000 | 4180.3232 | 3993.0488 | 985.3934 | 0.00049616 | 56 | 4.9346 | 4.1803 | 3.993 | 0.98539 | 0.00049616
| 328.15 | 500000 | 4179.9878 | 3998.0969 | 985.8804 | 0.00050406 | 55 | 4.9346 | 4.18 | 3.9981 | 0.98588 | 0.00050406
| 327.15 | 500000 | 4179.6738 | 4003.1296 | 986.3611 | 0.00051218 | 54 | 4.9346 | 4.1797 | 4.0031 | 0.98636 | 0.00051218
| 326.15 | 500000 | 4179.3813 | 4008.1465 | 986.8357 | 0.00052052 | 53 | 4.9346 | 4.1794 | 4.0081 | 0.98684 | 0.00052052
| 325.15 | 500000 | 4179.1099 | 4013.1462 | 987.3038 | 0.00052908 | 52 | 4.9346 | 4.1791 | 4.0131 | 0.9873 | 0.00052908
| 324.15 | 500000 | 4178.8604 | 4018.1277 | 987.7656 | 0.00053788 | 51 | 4.9346 | 4.1789 | 4.0181 | 0.98777 | 0.00053788
| 323.15 | 500000 | 4178.6318 | 4023.0896 | 988.2208 | 0.00054692 | 50 | 4.9346 | 4.1786 | 4.0231 | 0.98822 | 0.00054692
| 322.15 | 500000 | 4178.4253 | 4028.0312 | 988.6695 | 0.00055622 | 49 | 4.9346 | 4.1784 | 4.028 | 0.98867 | 0.00055622
| 321.15 | 500000 | 4178.2407 | 4032.9509 | 989.1115 | 0.00056577 | 48 | 4.9346 | 4.1782 | 4.033 | 0.98911 | 0.00056577
| 320.15 | 500000 | 4178.0781 | 4037.8474 | 989.5468 | 0.0005756 | 47 | 4.9346 | 4.1781 | 4.0378 | 0.98955 | 0.0005756
| 319.15 | 500000 | 4177.9375 | 4042.72 | 989.9753 | 0.00058571 | 46 | 4.9346 | 4.1779 | 4.0427 | 0.98998 | 0.00058571
| 318.15 | 500000 | 4177.8193 | 4047.5667 | 990.3969 | 0.00059612 | 45 | 4.9346 | 4.1778 | 4.0476 | 0.9904 | 0.00059612
| 317.15 | 500000 | 4177.7236 | 4052.3865 | 990.8116 | 0.00060684 | 44 | 4.9346 | 4.1777 | 4.0524 | 0.99081 | 0.00060684
| 316.15 | 500000 | 4177.6504 | 4057.178 | 991.2192 | 0.00061787 | 43 | 4.9346 | 4.1777 | 4.0572 | 0.99122 | 0.00061787
| 315.15 | 500000 | 4177.6006 | 4061.9399 | 991.6196 | 0.00062923 | 42 | 4.9346 | 4.1776 | 4.0619 | 0.99162 | 0.00062923
| 314.15 | 500000 | 4177.5737 | 4066.6704 | 992.0128 | 0.00064094 | 41 | 4.9346 | 4.1776 | 4.0667 | 0.99201 | 0.00064094
| 313.15 | 500000 | 4177.5703 | 4071.3684 | 992.3986 | 0.00065301 | 40 | 4.9346 | 4.1776 | 4.0714 | 0.9924 | 0.00065301
| 312.15 | 500000 | 4177.5913 | 4076.0322 | 992.777 | 0.00066545 | 39 | 4.9346 | 4.1776 | 4.076 | 0.99278 | 0.00066545
| 311.15 | 500000 | 4177.6362 | 4080.6604 | 993.1479 | 0.00067829 | 38 | 4.9346 | 4.1776 | 4.0807 | 0.99315 | 0.00067829
| 310.15 | 500000 | 4177.7056 | 4085.2515 | 993.5111 | 0.00069153 | 37 | 4.9346 | 4.1777 | 4.0853 | 0.99351 | 0.00069153
| 309.15 | 500000 | 4177.8008 | 4089.8037 | 993.8665 | 0.0007052 | 36 | 4.9346 | 4.1778 | 4.0898 | 0.99387 | 0.0007052
| 308.15 | 500000 | 4177.9219 | 4094.3154 | 994.2141 | 0.00071932 | 35 | 4.9346 | 4.1779 | 4.0943 | 0.99421 | 0.00071932
| 307.15 | 500000 | 4178.0688 | 4098.7852 | 994.5536 | 0.0007339 | 34 | 4.9346 | 4.1781 | 4.0988 | 0.99455 | 0.0007339
| 306.15 | 500000 | 4178.2437 | 4103.2114 | 994.8851 | 0.00074896 | 33 | 4.9346 | 4.1782 | 4.1032 | 0.99489 | 0.00074896
| 305.15 | 500000 | 4178.4463 | 4107.5918 | 995.2082 | 0.00076454 | 32 | 4.9346 | 4.1784 | 4.1076 | 0.99521 | 0.00076454
| 304.15 | 500000 | 4178.6782 | 4111.9258 | 995.523 | 0.00078064 | 31 | 4.9346 | 4.1787 | 4.1119 | 0.99552 | 0.00078064
| 303.15 | 500000 | 4178.9399 | 4116.2109 | 995.8293 | 0.00079731 | 30 | 4.9346 | 4.1789 | 4.1162 | 0.99583 | 0.00079731
| 302.15 | 500000 | 4179.2329 | 4120.4453 | 996.1268 | 0.00081456 | 29 | 4.9346 | 4.1792 | 4.1204 | 0.99613 | 0.00081456
| 301.15 | 500000 | 4179.5586 | 4124.6279 | 996.4156 | 0.00083242 | 28 | 4.9346 | 4.1796 | 4.1246 | 0.99642 | 0.00083242
| 300.15 | 500000 | 4179.918 | 4128.7568 | 996.6954 | 0.00085092 | 27 | 4.9346 | 4.1799 | 4.1288 | 0.9967 | 0.00085092
| 299.15 | 500000 | 4180.3135 | 4132.8301 | 996.9661 | 0.0008701 | 26 | 4.9346 | 4.1803 | 4.1328 | 0.99697 | 0.0008701
| 298.15 | 500000 | 4180.7461 | 4136.8462 | 997.2275 | 0.00088999 | 25 | 4.9346 | 4.1807 | 4.1368 | 0.99723 | 0.00088999
| 297.15 | 500000 | 4181.2188 | 4140.8037 | 997.4794 | 0.00091062 | 24 | 4.9346 | 4.1812 | 4.1408 | 0.99748 | 0.00091062
| 296.15 | 500000 | 4181.7329 | 4144.7012 | 997.7216 | 0.00093204 | 23 | 4.9346 | 4.1817 | 4.1447 | 0.99772 | 0.00093204
| 295.15 | 500000 | 4182.2915 | 4148.5361 | 997.954 | 0.00095429 | 22 | 4.9346 | 4.1823 | 4.1485 | 0.99795 | 0.00095429
| 294.15 | 500000 | 4182.8975 | 4152.3076 | 998.1763 | 0.0009774 | 21 | 4.9346 | 4.1829 | 4.1523 | 0.99818 | 0.0009774
| 293.15 | 500000 | 4183.5542 | 4156.0142 | 998.3884 | 0.0010014 | 20 | 4.9346 | 4.1836 | 4.156 | 0.99839 | 0.0010014
| 292.15 | 500000 | 4184.2651 | 4159.6543 | 998.59 | 0.0010264 | 19 | 4.9346 | 4.1843 | 4.1597 | 0.99859 | 0.0010264
| 291.15 | 500000 | 4185.0347 | 4163.2261 | 998.7809 | 0.0010525 | 18 | 4.9346 | 4.185 | 4.1632 | 0.99878 | 0.0010525
| 290.15 | 500000 | 4185.8662 | 4166.7295 | 998.9609 | 0.0010796 | 17 | 4.9346 | 4.1859 | 4.1667 | 0.99896 | 0.0010796
| 289.15 | 500000 | 4186.7656 | 4170.1621 | 999.1297 | 0.0011078 | 16 | 4.9346 | 4.1868 | 4.1702 | 0.99913 | 0.0011078
| 288.15 | 500000 | 4187.7383 | 4173.5229 | 999.287 | 0.0011373 | 15 | 4.9346 | 4.1877 | 4.1735 | 0.99929 | 0.0011373
| 287.15 | 500000 | 4188.79 | 4176.812 | 999.4326 | 0.001168 | 14 | 4.9346 | 4.1888 | 4.1768 | 0.99943 | 0.001168
| 286.15 | 500000 | 4189.9277 | 4180.0273 | 999.5662 | 0.0012001 | 13 | 4.9346 | 4.1899 | 4.18 | 0.99957 | 0.0012001
| 285.15 | 500000 | 4191.1592 | 4183.1685 | 999.6876 | 0.0012337 | 12 | 4.9346 | 4.1912 | 4.1832 | 0.99969 | 0.0012337
| 284.15 | 500000 | 4192.4927 | 4186.2354 | 999.7962 | 0.0012687 | 11 | 4.9346 | 4.1925 | 4.1862 | 0.9998 | 0.0012687
| 283.15 | 500000 | 4193.9375 | 4189.2271 | 999.8919 | 0.0013054 | 10 | 4.9346 | 4.1939 | 4.1892 | 0.99989 | 0.0013054
| 282.15 | 500000 | 4195.5044 | 4192.1436 | 999.9743 | 0.0013439 | 9 | 4.9346 | 4.1955 | 4.1921 | 0.99997 | 0.0013439
| 281.15 | 500000 | 4197.2041 | 4194.9854 | 1000.043 | 0.0013842 | 8 | 4.9346 | 4.1972 | 4.195 | 1 | 0.0013842
| 280.15 | 500000 | 4199.0493 | 4197.752 | 1000.0976 | 0.0014265 | 7 | 4.9346 | 4.199 | 4.1978 | 1.0001 | 0.0014265
| 279.15 | 500000 | 4201.0547 | 4200.4438 | 1000.1377 | 0.0014708 | 6 | 4.9346 | 4.2011 | 4.2004 | 1.0001 | 0.0014708
| 278.15 | 500000 | 4203.2358 | 4203.062 | 1000.1628 | 0.0015175 | 5 | 4.9346 | 4.2032 | 4.2031 | 1.0002 | 0.0015175
| 277.15 | 500000 | 4205.6094 | 4205.6074 | 1000.1726 | 0.0015665 | 4 | 4.9346 | 4.2056 | 4.2056 | 1.0002 | 0.0015665
| 276.15 | 500000 | 4208.1943 | 4208.0811 | 1000.1664 | 0.0016181 | 3 | 4.9346 | 4.2082 | 4.2081 | 1.0002 | 0.0016181
| 275.15 | 500000 | 4211.0127 | 4210.4849 | 1000.1438 | 0.0016725 | 2 | 4.9346 | 4.211 | 4.2105 | 1.0001 | 0.0016725
| 274.15 | 500000 | 4214.0869 | 4212.8203 | 1000.1042 | 0.0017299 | 0.99999 | 4.9346 | 4.2141 | 4.2128 | 1.0001 | 0.0017299
| 273.15 | 500000 | 4217.4429 | 4215.0898 | 1000.0471 | 0.0017905 | -6.1035e-06 | 4.9346 | 4.2174 | 4.2151 | 1 | 0.0017905
| 473.15 | 400000 | 2098.3909 | 1569.6083 | 1.8715 | 1.6083e-05 | 200 | 3.9477 | 2.0984 | 1.5696 | 0.0018715 | 1.6083e-05
| 472.15 | 400000 | 2100.0264 | 1570.4331 | 1.8758 | 1.6042e-05 | 199 | 3.9477 | 2.1 | 1.5704 | 0.0018758 | 1.6042e-05
| 471.15 | 400000 | 2101.7034 | 1571.285 | 1.8802 | 1.6e-05 | 198 | 3.9477 | 2.1017 | 1.5713 | 0.0018802 | 1.6e-05
| 470.15 | 400000 | 2103.4229 | 1572.1647 | 1.8845 | 1.5959e-05 | 197 | 3.9477 | 2.1034 | 1.5722 | 0.0018845 | 1.5959e-05
| 469.15 | 400000 | 2105.1855 | 1573.0726 | 1.889 | 1.5918e-05 | 196 | 3.9477 | 2.1052 | 1.5731 | 0.001889 | 1.5918e-05
| 468.15 | 400000 | 2106.9929 | 1574.0095 | 1.8934 | 1.5876e-05 | 195 | 3.9477 | 2.107 | 1.574 | 0.0018934 | 1.5876e-05
| 467.15 | 400000 | 2108.8457 | 1574.976 | 1.8978 | 1.5835e-05 | 194 | 3.9477 | 2.1088 | 1.575 | 0.0018978 | 1.5835e-05
| 466.15 | 400000 | 2110.7451 | 1575.9729 | 1.9023 | 1.5794e-05 | 193 | 3.9477 | 2.1107 | 1.576 | 0.0019023 | 1.5794e-05
| 465.15 | 400000 | 2112.6924 | 1577.0007 | 1.9068 | 1.5753e-05 | 192 | 3.9477 | 2.1127 | 1.577 | 0.0019068 | 1.5753e-05
| 464.15 | 400000 | 2114.6885 | 1578.0604 | 1.9114 | 1.5711e-05 | 191 | 3.9477 | 2.1147 | 1.5781 | 0.0019114 | 1.5711e-05
| 463.15 | 400000 | 2116.7346 | 1579.1528 | 1.9159 | 1.567e-05 | 190 | 3.9477 | 2.1167 | 1.5792 | 0.0019159 | 1.567e-05
| 462.15 | 400000 | 2118.832 | 1580.2786 | 1.9205 | 1.5629e-05 | 189 | 3.9477 | 2.1188 | 1.5803 | 0.0019205 | 1.5629e-05
| 461.15 | 400000 | 2120.9824 | 1581.4387 | 1.9251 | 1.5588e-05 | 188 | 3.9477 | 2.121 | 1.5814 | 0.0019251 | 1.5588e-05
| 460.15 | 400000 | 2123.1868 | 1582.634 | 1.9298 | 1.5547e-05 | 187 | 3.9477 | 2.1232 | 1.5826 | 0.0019298 | 1.5547e-05
| 459.15 | 400000 | 2125.4468 | 1583.8655 | 1.9344 | 1.5505e-05 | 186 | 3.9477 | 2.1254 | 1.5839 | 0.0019344 | 1.5505e-05
| 458.15 | 400000 | 2127.7639 | 1585.1342 | 1.9391 | 1.5464e-05 | 185 | 3.9477 | 2.1278 | 1.5851 | 0.0019391 | 1.5464e-05
| 457.15 | 400000 | 2130.1396 | 1586.4412 | 1.9439 | 1.5423e-05 | 184 | 3.9477 | 2.1301 | 1.5864 | 0.0019439 | 1.5423e-05
| 456.15 | 400000 | 2132.5762 | 1587.7875 | 1.9486 | 1.5382e-05 | 183 | 3.9477 | 2.1326 | 1.5878 | 0.0019486 | 1.5382e-05
| 455.15 | 400000 | 2135.0747 | 1589.1746 | 1.9534 | 1.5341e-05 | 182 | 3.9477 | 2.1351 | 1.5892 | 0.0019534 | 1.5341e-05
| 454.15 | 400000 | 2137.6377 | 1590.6035 | 1.9582 | 1.53e-05 | 181 | 3.9477 | 2.1376 | 1.5906 | 0.0019582 | 1.53e-05
| 453.15 | 400000 | 2140.2668 | 1592.0758 | 1.963 | 1.5258e-05 | 180 | 3.9477 | 2.1403 | 1.5921 | 0.001963 | 1.5258e-05
| 452.15 | 400000 | 2142.9646 | 1593.5929 | 1.9679 | 1.5217e-05 | 179 | 3.9477 | 2.143 | 1.5936 | 0.0019679 | 1.5217e-05
| 451.15 | 400000 | 2145.7332 | 1595.1564 | 1.9728 | 1.5176e-05 | 178 | 3.9477 | 2.1457 | 1.5952 | 0.0019728 | 1.5176e-05
| 450.15 | 400000 | 2148.5752 | 1596.7681 | 1.9777 | 1.5135e-05 | 177 | 3.9477 | 2.1486 | 1.5968 | 0.0019777 | 1.5135e-05
| 449.15 | 400000 | 2151.4932 | 1598.4298 | 1.9827 | 1.5094e-05 | 176 | 3.9477 | 2.1515 | 1.5984 | 0.0019827 | 1.5094e-05
| 448.15 | 400000 | 2154.4905 | 1600.1436 | 1.9876 | 1.5053e-05 | 175 | 3.9477 | 2.1545 | 1.6001 | 0.0019876 | 1.5053e-05
| 447.15 | 400000 | 2157.5701 | 1601.9117 | 1.9927 | 1.5012e-05 | 174 | 3.9477 | 2.1576 | 1.6019 | 0.0019927 | 1.5012e-05
| 446.15 | 400000 | 2160.7356 | 1603.7366 | 1.9977 | 1.4971e-05 | 173 | 3.9477 | 2.1607 | 1.6037 | 0.0019977 | 1.4971e-05
| 445.15 | 400000 | 2163.9905 | 1605.6208 | 2.0028 | 1.493e-05 | 172 | 3.9477 | 2.164 | 1.6056 | 0.0020028 | 1.493e-05
| 444.15 | 400000 | 2167.3394 | 1607.5675 | 2.0079 | 1.4889e-05 | 171 | 3.9477 | 2.1673 | 1.6076 | 0.0020079 | 1.4889e-05
| 443.15 | 400000 | 2170.7864 | 1609.5797 | 2.013 | 1.4848e-05 | 170 | 3.9477 | 2.1708 | 1.6096 | 0.002013 | 1.4848e-05
| 442.15 | 400000 | 2174.3369 | 1611.6613 | 2.0182 | 1.4807e-05 | 169 | 3.9477 | 2.1743 | 1.6117 | 0.0020182 | 1.4807e-05
| 441.15 | 400000 | 2177.9963 | 1613.8158 | 2.0234 | 1.4766e-05 | 168 | 3.9477 | 2.178 | 1.6138 | 0.0020234 | 1.4766e-05
| 440.15 | 400000 | 2181.771 | 1616.048 | 2.0287 | 1.4725e-05 | 167 | 3.9477 | 2.1818 | 1.616 | 0.0020287 | 1.4725e-05
| 439.15 | 400000 | 2185.6675 | 1618.3625 | 2.034 | 1.4684e-05 | 166 | 3.9477 | 2.1857 | 1.6184 | 0.002034 | 1.4684e-05
| 438.15 | 400000 | 2189.6934 | 1620.7651 | 2.0393 | 1.4643e-05 | 165 | 3.9477 | 2.1897 | 1.6208 | 0.0020393 | 1.4643e-05
| 437.15 | 400000 | 2193.8574 | 1623.2618 | 2.0446 | 1.4602e-05 | 164 | 3.9477 | 2.1939 | 1.6233 | 0.0020446 | 1.4602e-05
| 436.15 | 400000 | 2198.1685 | 1625.8596 | 2.05 | 1.4561e-05 | 163 | 3.9477 | 2.1982 | 1.6259 | 0.00205 | 1.4561e-05
| 435.15 | 400000 | 2202.6377 | 1628.5659 | 2.0554 | 1.4521e-05 | 162 | 3.9477 | 2.2026 | 1.6286 | 0.0020554 | 1.4521e-05
| 434.15 | 400000 | 2207.2764 | 1631.3896 | 2.0609 | 1.448e-05 | 161 | 3.9477 | 2.2073 | 1.6314 | 0.0020609 | 1.448e-05
| 433.15 | 400000 | 2212.0981 | 1634.3405 | 2.0664 | 1.4439e-05 | 160 | 3.9477 | 2.2121 | 1.6343 | 0.0020664 | 1.4439e-05
| 432.15 | 400000 | 2217.1179 | 1637.4293 | 2.0719 | 1.4398e-05 | 159 | 3.9477 | 2.2171 | 1.6374 | 0.0020719 | 1.4398e-05
| 431.15 | 400000 | 2222.3525 | 1640.6688 | 2.0775 | 1.4357e-05 | 158 | 3.9477 | 2.2224 | 1.6407 | 0.0020775 | 1.4357e-05
| 430.15 | 400000 | 2227.8208 | 1644.0729 | 2.0831 | 1.4316e-05 | 157 | 3.9477 | 2.2278 | 1.6441 | 0.0020831 | 1.4316e-05
| 429.15 | 400000 | 2233.5444 | 1647.6575 | 2.0888 | 1.4276e-05 | 156 | 3.9477 | 2.2335 | 1.6477 | 0.0020888 | 1.4276e-05
| 428.15 | 400000 | 2239.5476 | 1651.4406 | 2.0945 | 1.4235e-05 | 155 | 3.9477 | 2.2395 | 1.6514 | 0.0020945 | 1.4235e-05
| 427.15 | 400000 | 2245.8579 | 1655.4425 | 2.1002 | 1.4194e-05 | 154 | 3.9477 | 2.2459 | 1.6554 | 0.0021002 | 1.4194e-05
| 426.15 | 400000 | 2252.5068 | 1659.6866 | 2.106 | 1.4153e-05 | 153 | 3.9477 | 2.2525 | 1.6597 | 0.002106 | 1.4153e-05
| 425.15 | 400000 | 2259.5293 | 1664.1992 | 2.1118 | 1.4113e-05 | 152 | 3.9477 | 2.2595 | 1.6642 | 0.0021118 | 1.4113e-05
| 424.15 | 400000 | 2266.9663 | 1669.0103 | 2.1177 | 1.4072e-05 | 151 | 3.9477 | 2.267 | 1.669 | 0.0021177 | 1.4072e-05
| 423.15 | 400000 | 2274.863 | 1674.1537 | 2.1236 | 1.4031e-05 | 150 | 3.9477 | 2.2749 | 1.6742 | 0.0021236 | 1.4031e-05
| 422.15 | 400000 | 2283.2722 | 1679.6682 | 2.1296 | 1.399e-05 | 149 | 3.9477 | 2.2833 | 1.6797 | 0.0021296 | 1.399e-05
| 421.15 | 400000 | 2292.2532 | 1685.5981 | 2.1356 | 1.395e-05 | 148 | 3.9477 | 2.2923 | 1.6856 | 0.0021356 | 1.395e-05
| 420.15 | 400000 | 2301.8738 | 1691.9937 | 2.1417 | 1.3909e-05 | 147 | 3.9477 | 2.3019 | 1.692 | 0.0021417 | 1.3909e-05
| 419.15 | 400000 | 2312.2112 | 1698.912 | 2.1478 | 1.3868e-05 | 146 | 3.9477 | 2.3122 | 1.6989 | 0.0021478 | 1.3868e-05
| 418.15 | 400000 | 2323.354 | 1706.4185 | 2.154 | 1.3828e-05 | 145 | 3.9477 | 2.3234 | 1.7064 | 0.002154 | 1.3828e-05
| 417.15 | 400000 | 2335.4028 | 1714.5876 | 2.1602 | 1.3787e-05 | 144 | 3.9477 | 2.3354 | 1.7146 | 0.0021602 | 1.3787e-05
| 416.15 | 400000 | 4292.9541 | 3558.5288 | 923.443 | 0.0001921 | 143 | 3.9477 | 4.293 | 3.5585 | 0.92344 | 0.0001921
| 415.15 | 400000 | 4290.5791 | 3563.1516 | 924.3508 | 0.00019356 | 142 | 3.9477 | 4.2906 | 3.5632 | 0.92435 | 0.00019356
| 414.15 | 400000 | 4288.2368 | 3567.7869 | 925.2541 | 0.00019504 | 141 | 3.9477 | 4.2882 | 3.5678 | 0.92525 | 0.00019504
| 413.15 | 400000 | 4285.9263 | 3572.4338 | 926.153 | 0.00019655 | 140 | 3.9477 | 4.2859 | 3.5724 | 0.92615 | 0.00019655
| 412.15 | 400000 | 4283.6475 | 3577.093 | 927.0474 | 0.00019808 | 139 | 3.9477 | 4.2836 | 3.5771 | 0.92705 | 0.00019808
| 411.15 | 400000 | 4281.3994 | 3581.7639 | 927.9374 | 0.00019963 | 138 | 3.9477 | 4.2814 | 3.5818 | 0.92794 | 0.00019963
| 410.15 | 400000 | 4279.1826 | 3586.4468 | 928.8231 | 0.0002012 | 137 | 3.9477 | 4.2792 | 3.5864 | 0.92882 | 0.0002012
| 409.15 | 400000 | 4276.9956 | 3591.1411 | 929.7043 | 0.0002028 | 136 | 3.9477 | 4.277 | 3.5911 | 0.9297 | 0.0002028
| 408.15 | 400000 | 4274.8389 | 3595.8474 | 930.5811 | 0.00020443 | 135 | 3.9477 | 4.2748 | 3.5958 | 0.93058 | 0.00020443
| 407.15 | 400000 | 4272.7114 | 3600.5652 | 931.4534 | 0.00020607 | 134 | 3.9477 | 4.2727 | 3.6006 | 0.93145 | 0.00020607
| 406.15 | 400000 | 4270.6133 | 3605.2944 | 932.3215 | 0.00020775 | 133 | 3.9477 | 4.2706 | 3.6053 | 0.93232 | 0.00020775
| 405.15 | 400000 | 4268.5444 | 3610.0352 | 933.1851 | 0.00020945 | 132 | 3.9477 | 4.2685 | 3.61 | 0.93319 | 0.00020945
| 404.15 | 400000 | 4266.5034 | 3614.7871 | 934.0443 | 0.00021117 | 131 | 3.9477 | 4.2665 | 3.6148 | 0.93404 | 0.00021117
| 403.15 | 400000 | 4264.4912 | 3619.5505 | 934.8991 | 0.00021293 | 130 | 3.9477 | 4.2645 | 3.6196 | 0.9349 | 0.00021293
| 402.15 | 400000 | 4262.5068 | 3624.325 | 935.7496 | 0.00021471 | 129 | 3.9477 | 4.2625 | 3.6243 | 0.93575 | 0.00021471
| 401.15 | 400000 | 4260.5503 | 3629.1108 | 936.5956 | 0.00021652 | 128 | 3.9477 | 4.2606 | 3.6291 | 0.9366 | 0.00021652
| 400.15 | 400000 | 4258.6206 | 3633.9075 | 937.4373 | 0.00021836 | 127 | 3.9477 | 4.2586 | 3.6339 | 0.93744 | 0.00021836
| 399.15 | 400000 | 4256.7183 | 3638.7151 | 938.2747 | 0.00022023 | 126 | 3.9477 | 4.2567 | 3.6387 | 0.93827 | 0.00022023
| 398.15 | 400000 | 4254.8428 | 3643.5337 | 939.1075 | 0.00022213 | 125 | 3.9477 | 4.2548 | 3.6435 | 0.93911 | 0.00022213
| 397.15 | 400000 | 4252.9937 | 3648.363 | 939.9361 | 0.00022406 | 124 | 3.9477 | 4.253 | 3.6484 | 0.93994 | 0.00022406
| 396.15 | 400000 | 4251.1704 | 3653.2034 | 940.7603 | 0.00022602 | 123 | 3.9477 | 4.2512 | 3.6532 | 0.94076 | 0.00022602
| 395.15 | 400000 | 4249.3735 | 3658.054 | 941.58 | 0.00022801 | 122 | 3.9477 | 4.2494 | 3.6581 | 0.94158 | 0.00022801
| 394.15 | 400000 | 4247.6021 | 3662.9153 | 942.3954 | 0.00023004 | 121 | 3.9477 | 4.2476 | 3.6629 | 0.9424 | 0.00023004
| 393.15 | 400000 | 4245.856 | 3667.7871 | 943.2064 | 0.0002321 | 120 | 3.9477 | 4.2459 | 3.6678 | 0.94321 | 0.0002321
| 392.15 | 400000 | 4244.1353 | 3672.6694 | 944.013 | 0.0002342 | 119 | 3.9477 | 4.2441 | 3.6727 | 0.94401 | 0.0002342
| 391.15 | 400000 | 4242.4395 | 3677.5618 | 944.8152 | 0.00023633 | 118 | 3.9477 | 4.2424 | 3.6776 | 0.94482 | 0.00023633
| 390.15 | 400000 | 4240.7681 | 3682.4644 | 945.613 | 0.0002385 | 117 | 3.9477 | 4.2408 | 3.6825 | 0.94561 | 0.0002385
| 389.15 | 400000 | 4239.1216 | 3687.3772 | 946.4064 | 0.00024071 | 116 | 3.9477 | 4.2391 | 3.6874 | 0.94641 | 0.00024071
| 388.15 | 400000 | 4237.499 | 3692.3 | 947.1953 | 0.00024295 | 115 | 3.9477 | 4.2375 | 3.6923 | 0.9472 | 0.00024295
| 387.15 | 400000 | 4235.9009 | 3697.2327 | 947.9799 | 0.00024523 | 114 | 3.9477 | 4.2359 | 3.6972 | 0.94798 | 0.00024523
| 386.15 | 400000 | 4234.3267 | 3702.175 | 948.76 | 0.00024755 | 113 | 3.9477 | 4.2343 | 3.7022 | 0.94876 | 0.00024755
| 385.15 | 400000 | 4232.7759 | 3707.1272 | 949.5356 | 0.00024992 | 112 | 3.9477 | 4.2328 | 3.7071 | 0.94954 | 0.00024992
| 384.15 | 400000 | 4231.249 | 3712.0889 | 950.3069 | 0.00025232 | 111 | 3.9477 | 4.2312 | 3.7121 | 0.95031 | 0.00025232
| 383.15 | 400000 | 4229.7451 | 3717.0601 | 951.0737 | 0.00025477 | 110 | 3.9477 | 4.2297 | 3.7171 | 0.95107 | 0.00025477
| 382.15 | 400000 | 4228.2642 | 3722.0405 | 951.836 | 0.00025726 | 109 | 3.9477 | 4.2283 | 3.722 | 0.95184 | 0.00025726
| 381.15 | 400000 | 4226.8066 | 3727.0303 | 952.5939 | 0.00025979 | 108 | 3.9477 | 4.2268 | 3.727 | 0.95259 | 0.00025979
| 380.15 | 400000 | 4225.3721 | 3732.0291 | 953.3472 | 0.00026238 | 107 | 3.9477 | 4.2254 | 3.732 | 0.95335 | 0.00026238
| 379.15 | 400000 | 4223.96 | 3737.0366 | 954.0961 | 0.000265 | 106 | 3.9477 | 4.224 | 3.737 | 0.9541 | 0.000265
| 378.15 | 400000 | 4222.5703 | 3742.0532 | 954.8405 | 0.00026768 | 105 | 3.9477 | 4.2226 | 3.7421 | 0.95484 | 0.00026768
| 377.15 | 400000 | 4221.2036 | 3747.0784 | 955.5803 | 0.00027041 | 104 | 3.9477 | 4.2212 | 3.7471 | 0.95558 | 0.00027041
| 376.15 | 400000 | 4219.8584 | 3752.1121 | 956.3156 | 0.00027318 | 103 | 3.9477 | 4.2199 | 3.7521 | 0.95632 | 0.00027318
| 375.15 | 400000 | 4218.5361 | 3757.1541 | 957.0464 | 0.00027601 | 102 | 3.9477 | 4.2185 | 3.7572 | 0.95705 | 0.00027601
| 374.15 | 400000 | 4217.2354 | 3762.2043 | 957.7726 | 0.00027889 | 101 | 3.9477 | 4.2172 | 3.7622 | 0.95777 | 0.00027889
| 373.15 | 400000 | 4215.9565 | 3767.2625 | 958.4942 | 0.00028183 | 100 | 3.9477 | 4.216 | 3.7673 | 0.95849 | 0.00028183
| 372.15 | 400000 | 4214.6997 | 3772.3286 | 959.2112 | 0.00028482 | 99 | 3.9477 | 4.2147 | 3.7723 | 0.95921 | 0.00028482
| 371.15 | 400000 | 4213.4648 | 3777.4023 | 959.9236 | 0.00028786 | 98 | 3.9477 | 4.2135 | 3.7774 | 0.95992 | 0.00028786
| 370.15 | 400000 | 4212.2515 | 3782.4836 | 960.6315 | 0.00029097 | 97 | 3.9477 | 4.2123 | 3.7825 | 0.96063 | 0.00029097
| 369.15 | 400000 | 4211.0591 | 3787.5723 | 961.3347 | 0.00029414 | 96 | 3.9477 | 4.2111 | 3.7876 | 0.96133 | 0.00029414
| 368.15 | 400000 | 4209.8887 | 3792.6677 | 962.0331 | 0.00029737 | 95 | 3.9477 | 4.2099 | 3.7927 | 0.96203 | 0.00029737
| 367.15 | 400000 | 4208.7393 | 3797.7703 | 962.7269 | 0.00030066 | 94 | 3.9477 | 4.2087 | 3.7978 | 0.96273 | 0.00030066
| 366.15 | 400000 | 4207.6118 | 3802.8792 | 963.4161 | 0.00030401 | 93 | 3.9477 | 4.2076 | 3.8029 | 0.96342 | 0.00030401
| 365.15 | 400000 | 4206.5049 | 3807.9946 | 964.1005 | 0.00030744 | 92 | 3.9477 | 4.2065 | 3.808 | 0.9641 | 0.00030744
| 364.15 | 400000 | 4205.4194 | 3813.1162 | 964.7801 | 0.00031093 | 91 | 3.9477 | 4.2054 | 3.8131 | 0.96478 | 0.00031093
| 363.15 | 400000 | 4204.355 | 3818.2437 | 965.455 | 0.00031449 | 90 | 3.9477 | 4.2044 | 3.8182 | 0.96546 | 0.00031449
| 362.15 | 400000 | 4203.3115 | 3823.3767 | 966.1251 | 0.00031813 | 89 | 3.9477 | 4.2033 | 3.8234 | 0.96613 | 0.00031813
| 361.15 | 400000 | 4202.2891 | 3828.5149 | 966.7904 | 0.00032184 | 88 | 3.9477 | 4.2023 | 3.8285 | 0.96679 | 0.00032184
| 360.15 | 400000 | 4201.2876 | 3833.6584 | 967.4509 | 0.00032562 | 87 | 3.9477 | 4.2013 | 3.8337 | 0.96745 | 0.00032562
| 359.15 | 400000 | 4200.3071 | 3838.8066 | 968.1064 | 0.00032948 | 86 | 3.9477 | 4.2003 | 3.8388 | 0.96811 | 0.00032948
| 358.15 | 400000 | 4199.3472 | 3843.9592 | 968.7571 | 0.00033343 | 85 | 3.9477 | 4.1993 | 3.844 | 0.96876 | 0.00033343
| 357.15 | 400000 | 4198.4082 | 3849.116 | 969.403 | 0.00033745 | 84 | 3.9477 | 4.1984 | 3.8491 | 0.9694 | 0.00033745
| 356.15 | 400000 | 4197.4902 | 3854.2764 | 970.0438 | 0.00034156 | 83 | 3.9477 | 4.1975 | 3.8543 | 0.97004 | 0.00034156
| 355.15 | 400000 | 4196.5928 | 3859.4402 | 970.6797 | 0.00034576 | 82 | 3.9477 | 4.1966 | 3.8594 | 0.97068 | 0.00034576
| 354.15 | 400000 | 4195.7163 | 3864.6069 | 971.3105 | 0.00035005 | 81 | 3.9477 | 4.1957 | 3.8646 | 0.97131 | 0.00035005
| 353.15 | 400000 | 4194.8604 | 3869.7764 | 971.9364 | 0.00035443 | 80 | 3.9477 | 4.1949 | 3.8698 | 0.97194 | 0.00035443
| 352.15 | 400000 | 4194.0254 | 3874.948 | 972.5572 | 0.00035891 | 79 | 3.9477 | 4.194 | 3.8749 | 0.97256 | 0.00035891
| 351.15 | 400000 | 4193.2109 | 3880.1216 | 973.1729 | 0.00036348 | 78 | 3.9477 | 4.1932 | 3.8801 | 0.97317 | 0.00036348
| 350.15 | 400000 | 4192.417 | 3885.2964 | 973.7834 | 0.00036816 | 77 | 3.9477 | 4.1924 | 3.8853 | 0.97378 | 0.00036816
| 349.15 | 400000 | 4191.644 | 3890.4722 | 974.3888 | 0.00037294 | 76 | 3.9477 | 4.1916 | 3.8905 | 0.97439 | 0.00037294
| 348.15 | 400000 | 4190.8916 | 3895.6484 | 974.989 | 0.00037782 | 75 | 3.9477 | 4.1909 | 3.8956 | 0.97499 | 0.00037782
| 347.15 | 400000 | 4190.1602 | 3900.8245 | 975.584 | 0.00038282 | 74 | 3.9477 | 4.1902 | 3.9008 | 0.97558 | 0.00038282
| 346.15 | 400000 | 4189.4492 | 3906 | 976.1736 | 0.00038793 | 73 | 3.9477 | 4.1894 | 3.906 | 0.97617 | 0.00038793
| 345.15 | 400000 | 4188.7593 | 3911.1743 | 976.7581 | 0.00039316 | 72 | 3.9477 | 4.1888 | 3.9112 | 0.97676 | 0.00039316
| 344.15 | 400000 | 4188.0894 | 3916.3472 | 977.3371 | 0.0003985 | 71 | 3.9477 | 4.1881 | 3.9163 | 0.97734 | 0.0003985
| 343.15 | 400000 | 4187.4409 | 3921.5176 | 977.9107 | 0.00040397 | 70 | 3.9477 | 4.1874 | 3.9215 | 0.97791 | 0.00040397
| 342.15 | 400000 | 4186.813 | 3926.6853 | 978.4789 | 0.00040957 | 69 | 3.9477 | 4.1868 | 3.9267 | 0.97848 | 0.00040957
| 341.15 | 400000 | 4186.2056 | 3931.8494 | 979.0416 | 0.00041531 | 68 | 3.9477 | 4.1862 | 3.9318 | 0.97904 | 0.00041531
| 340.15 | 400000 | 4185.6191 | 3937.0095 | 979.5989 | 0.00042118 | 67 | 3.9477 | 4.1856 | 3.937 | 0.9796 | 0.00042118
| 339.15 | 400000 | 4185.0537 | 3942.1648 | 980.1505 | 0.00042718 | 66 | 3.9477 | 4.1851 | 3.9422 | 0.98015 | 0.00042718
| 338.15 | 400000 | 4184.5088 | 3947.3145 | 980.6965 | 0.00043334 | 65 | 3.9477 | 4.1845 | 3.9473 | 0.9807 | 0.00043334
| 337.15 | 400000 | 4183.9849 | 3952.458 | 981.2369 | 0.00043964 | 64 | 3.9477 | 4.184 | 3.9525 | 0.98124 | 0.00043964
| 336.15 | 400000 | 4183.4819 | 3957.5947 | 981.7715 | 0.0004461 | 63 | 3.9477 | 4.1835 | 3.9576 | 0.98177 | 0.0004461
| 335.15 | 400000 | 4182.9995 | 3962.7234 | 982.3005 | 0.00045273 | 62 | 3.9477 | 4.183 | 3.9627 | 0.9823 | 0.00045273
| 334.15 | 400000 | 4182.5386 | 3967.8438 | 982.8235 | 0.00045951 | 61 | 3.9477 | 4.1825 | 3.9678 | 0.98282 | 0.00045951
| 333.15 | 400000 | 4182.0981 | 3972.9546 | 983.3408 | 0.00046647 | 60 | 3.9477 | 4.1821 | 3.973 | 0.98334 | 0.00046647
| 332.15 | 400000 | 4181.6792 | 3978.0554 | 983.8521 | 0.0004736 | 59 | 3.9477 | 4.1817 | 3.9781 | 0.98385 | 0.0004736
| 331.15 | 400000 | 4181.2812 | 3983.145 | 984.3574 | 0.00048092 | 58 | 3.9477 | 4.1813 | 3.9831 | 0.98436 | 0.00048092
| 330.15 | 400000 | 4180.9043 | 3988.2224 | 984.8567 | 0.00048843 | 57 | 3.9477 | 4.1809 | 3.9882 | 0.98486 | 0.00048843
| 329.15 | 400000 | 4180.5483 | 3993.2869 | 985.3499 | 0.00049614 | 56 | 3.9477 | 4.1805 | 3.9933 | 0.98535 | 0.00049614
| 328.15 | 400000 | 4180.2139 | 3998.3374 | 985.8369 | 0.00050404 | 55 | 3.9477 | 4.1802 | 3.9983 | 0.98584 | 0.00050404
| 327.15 | 400000 | 4179.9009 | 4003.373 | 986.3177 | 0.00051216 | 54 | 3.9477 | 4.1799 | 4.0034 | 0.98632 | 0.00051216
| 326.15 | 400000 | 4179.6089 | 4008.3926 | 986.7922 | 0.0005205 | 53 | 3.9477 | 4.1796 | 4.0084 | 0.98679 | 0.0005205
| 325.15 | 400000 | 4179.3389 | 4013.395 | 987.2604 | 0.00052906 | 52 | 3.9477 | 4.1793 | 4.0134 | 0.98726 | 0.00052906
| 324.15 | 400000 | 4179.0898 | 4018.3792 | 987.7221 | 0.00053786 | 51 | 3.9477 | 4.1791 | 4.0184 | 0.98772 | 0.00053786
| 323.15 | 400000 | 4178.8628 | 4023.344 | 988.1774 | 0.0005469 | 50 | 3.9477 | 4.1789 | 4.0233 | 0.98818 | 0.0005469
| 322.15 | 400000 | 4178.6577 | 4028.2883 | 988.626 | 0.0005562 | 49 | 3.9477 | 4.1787 | 4.0283 | 0.98863 | 0.0005562
| 321.15 | 400000 | 4178.4741 | 4033.2109 | 989.068 | 0.00056576 | 48 | 3.9477 | 4.1785 | 4.0332 | 0.98907 | 0.00056576
| 320.15 | 400000 | 4178.313 | 4038.1106 | 989.5033 | 0.00057559 | 47 | 3.9477 | 4.1783 | 4.0381 | 0.9895 | 0.00057559
| 319.15 | 400000 | 4178.1738 | 4042.9858 | 989.9318 | 0.0005857 | 46 | 3.9477 | 4.1782 | 4.043 | 0.98993 | 0.0005857
| 318.15 | 400000 | 4178.0571 | 4047.8357 | 990.3534 | 0.00059611 | 45 | 3.9477 | 4.1781 | 4.0478 | 0.99035 | 0.00059611
| 317.15 | 400000 | 4177.9629 | 4052.6584 | 990.768 | 0.00060682 | 44 | 3.9477 | 4.178 | 4.0527 | 0.99077 | 0.00060682
| 316.15 | 400000 | 4177.8916 | 4057.4529 | 991.1755 | 0.00061786 | 43 | 3.9477 | 4.1779 | 4.0575 | 0.99118 | 0.00061786
| 315.15 | 400000 | 4177.8433 | 4062.2178 | 991.5759 | 0.00062922 | 42 | 3.9477 | 4.1778 | 4.0622 | 0.99158 | 0.00062922
| 314.15 | 400000 | 4177.8179 | 4066.9517 | 991.9691 | 0.00064093 | 41 | 3.9477 | 4.1778 | 4.067 | 0.99197 | 0.00064093
| 313.15 | 400000 | 4177.8164 | 4071.6526 | 992.3549 | 0.000653 | 40 | 3.9477 | 4.1778 | 4.0717 | 0.99235 | 0.000653
| 312.15 | 400000 | 4177.8394 | 4076.3196 | 992.7333 | 0.00066545 | 39 | 3.9477 | 4.1778 | 4.0763 | 0.99273 | 0.00066545
| 311.15 | 400000 | 4177.8862 | 4080.9512 | 993.1041 | 0.00067828 | 38 | 3.9477 | 4.1779 | 4.081 | 0.9931 | 0.00067828
| 310.15 | 400000 | 4177.958 | 4085.5452 | 993.4672 | 0.00069153 | 37 | 3.9477 | 4.178 | 4.0855 | 0.99347 | 0.00069153
| 309.15 | 400000 | 4178.0552 | 4090.1008 | 993.8226 | 0.0007052 | 36 | 3.9477 | 4.1781 | 4.0901 | 0.99382 | 0.0007052
| 308.15 | 400000 | 4178.1787 | 4094.6157 | 994.17 | 0.00071932 | 35 | 3.9477 | 4.1782 | 4.0946 | 0.99417 | 0.00071932
| 307.15 | 400000 | 4178.3286 | 4099.0889 | 994.5095 | 0.0007339 | 34 | 3.9477 | 4.1783 | 4.0991 | 0.99451 | 0.0007339
| 306.15 | 400000 | 4178.5059 | 4103.5186 | 994.8409 | 0.00074897 | 33 | 3.9477 | 4.1785 | 4.1035 | 0.99484 | 0.00074897
| 305.15 | 400000 | 4178.7114 | 4107.9028 | 995.1639 | 0.00076454 | 32 | 3.9477 | 4.1787 | 4.1079 | 0.99516 | 0.00076454
| 304.15 | 400000 | 4178.9458 | 4112.2397 | 995.4786 | 0.00078065 | 31 | 3.9477 | 4.1789 | 4.1122 | 0.99548 | 0.00078065
| 303.15 | 400000 | 4179.2104 | 4116.5283 | 995.7849 | 0.00079732 | 30 | 3.9477 | 4.1792 | 4.1165 | 0.99578 | 0.00079732
| 302.15 | 400000 | 4179.5068 | 4120.7666 | 996.0823 | 0.00081457 | 29 | 3.9477 | 4.1795 | 4.1208 | 0.99608 | 0.00081457
| 301.15 | 400000 | 4179.8359 | 4124.9531 | 996.371 | 0.00083243 | 28 | 3.9477 | 4.1798 | 4.125 | 0.99637 | 0.00083243
| 300.15 | 400000 | 4180.1987 | 4129.0854 | 996.6507 | 0.00085094 | 27 | 3.9477 | 4.1802 | 4.1291 | 0.99665 | 0.00085094
| 299.15 | 400000 | 4180.5977 | 4133.1626 | 996.9212 | 0.00087012 | 26 | 3.9477 | 4.1806 | 4.1332 | 0.99692 | 0.00087012
| 298.15 | 400000 | 4181.0342 | 4137.1826 | 997.1825 | 0.00089001 | 25 | 3.9477 | 4.181 | 4.1372 | 0.99718 | 0.00089001
| 297.15 | 400000 | 4181.5107 | 4141.144 | 997.4342 | 0.00091065 | 24 | 3.9477 | 4.1815 | 4.1411 | 0.99743 | 0.00091065
| 296.15 | 400000 | 4182.0293 | 4145.0449 | 997.6763 | 0.00093207 | 23 | 3.9477 | 4.182 | 4.145 | 0.99768 | 0.00093207
| 295.15 | 400000 | 4182.5923 | 4148.8843 | 997.9086 | 0.00095432 | 22 | 3.9477 | 4.1826 | 4.1489 | 0.99791 | 0.00095432
| 294.15 | 400000 | 4183.2031 | 4152.6602 | 998.1307 | 0.00097744 | 21 | 3.9477 | 4.1832 | 4.1527 | 0.99813 | 0.00097744
| 293.15 | 400000 | 4183.8652 | 4156.3706 | 998.3427 | 0.0010015 | 20 | 3.9477 | 4.1839 | 4.1564 | 0.99834 | 0.0010015
| 292.15 | 400000 | 4184.5811 | 4160.0151 | 998.5441 | 0.0010265 | 19 | 3.9477 | 4.1846 | 4.16 | 0.99854 | 0.0010265
| 291.15 | 400000 | 4185.356 | 4163.5913 | 998.7349 | 0.0010525 | 18 | 3.9477 | 4.1854 | 4.1636 | 0.99873 | 0.0010525
| 290.15 | 400000 | 4186.1934 | 4167.0991 | 998.9147 | 0.0010796 | 17 | 3.9477 | 4.1862 | 4.1671 | 0.99891 | 0.0010796
| 289.15 | 400000 | 4187.0986 | 4170.5361 | 999.0833 | 0.0011079 | 16 | 3.9477 | 4.1871 | 4.1705 | 0.99908 | 0.0011079
| 288.15 | 400000 | 4188.0776 | 4173.9023 | 999.2404 | 0.0011373 | 15 | 3.9477 | 4.1881 | 4.1739 | 0.99924 | 0.0011373
| 287.15 | 400000 | 4189.1362 | 4177.1958 | 999.3858 | 0.0011681 | 14 | 3.9477 | 4.1891 | 4.1772 | 0.99939 | 0.0011681
| 286.15 | 400000 | 4190.2812 | 4180.416 | 999.5192 | 0.0012002 | 13 | 3.9477 | 4.1903 | 4.1804 | 0.99952 | 0.0012002
| 285.15 | 400000 | 4191.5205 | 4183.5625 | 999.6403 | 0.0012337 | 12 | 3.9477 | 4.1915 | 4.1836 | 0.99964 | 0.0012337
| 284.15 | 400000 | 4192.8623 | 4186.6348 | 999.7487 | 0.0012688 | 11 | 3.9477 | 4.1929 | 4.1866 | 0.99975 | 0.0012688
| 283.15 | 400000 | 4194.3154 | 4189.6318 | 999.8442 | 0.0013055 | 10 | 3.9477 | 4.1943 | 4.1896 | 0.99984 | 0.0013055
| 282.15 | 400000 | 4195.8911 | 4192.5542 | 999.9263 | 0.001344 | 9 | 3.9477 | 4.1959 | 4.1926 | 0.99993 | 0.001344
| 281.15 | 400000 | 4197.6001 | 4195.4014 | 999.9948 | 0.0013843 | 8 | 3.9477 | 4.1976 | 4.1954 | 0.99999 | 0.0013843
| 280.15 | 400000 | 4199.4561 | 4198.1738 | 1000.0491 | 0.0014266 | 7 | 3.9477 | 4.1995 | 4.1982 | 1 | 0.0014266
| 279.15 | 400000 | 4201.4722 | 4200.8721 | 1000.0889 | 0.001471 | 6 | 3.9477 | 4.2015 | 4.2009 | 1.0001 | 0.001471
| 278.15 | 400000 | 4203.6646 | 4203.4966 | 1000.1137 | 0.0015176 | 5 | 3.9477 | 4.2037 | 4.2035 | 1.0001 | 0.0015176
| 277.15 | 400000 | 4206.0503 | 4206.0488 | 1000.1232 | 0.0015667 | 4 | 3.9477 | 4.2061 | 4.206 | 1.0001 | 0.0015667
| 276.15 | 400000 | 4208.6484 | 4208.5293 | 1000.1166 | 0.0016183 | 3 | 3.9477 | 4.2086 | 4.2085 | 1.0001 | 0.0016183
| 275.15 | 400000 | 4211.48 | 4210.9404 | 1000.0937 | 0.0016728 | 2 | 3.9477 | 4.2115 | 4.2109 | 1.0001 | 0.0016728
| 274.15 | 400000 | 4214.5688 | 4213.2837 | 1000.0538 | 0.0017302 | 0.99999 | 3.9477 | 4.2146 | 4.2133 | 1.0001 | 0.0017302
| 273.15 | 400000 | 4217.9409 | 4215.561 | 999.9962 | 0.0017908 | -6.1035e-06 | 3.9477 | 4.2179 | 4.2156 | 1 | 0.0017908
| 473.15 | 300000 | 2054.7612 | 1544.7472 | 1.3958 | 1.6114e-05 | 200 | 2.9608 | 2.0548 | 1.5447 | 0.0013958 | 1.6114e-05
| 472.15 | 300000 | 2055.7549 | 1545.1791 | 1.3989 | 1.6073e-05 | 199 | 2.9608 | 2.0558 | 1.5452 | 0.0013989 | 1.6073e-05
| 471.15 | 300000 | 2056.7776 | 1545.6302 | 1.4021 | 1.6032e-05 | 198 | 2.9608 | 2.0568 | 1.5456 | 0.0014021 | 1.6032e-05
| 470.15 | 300000 | 2057.8296 | 1546.1011 | 1.4053 | 1.5991e-05 | 197 | 2.9608 | 2.0578 | 1.5461 | 0.0014053 | 1.5991e-05
| 469.15 | 300000 | 2058.9119 | 1546.5919 | 1.4085 | 1.595e-05 | 196 | 2.9608 | 2.0589 | 1.5466 | 0.0014085 | 1.595e-05
| 468.15 | 300000 | 2060.0249 | 1547.1034 | 1.4117 | 1.5909e-05 | 195 | 2.9608 | 2.06 | 1.5471 | 0.0014117 | 1.5909e-05
| 467.15 | 300000 | 2061.1692 | 1547.6359 | 1.415 | 1.5868e-05 | 194 | 2.9608 | 2.0612 | 1.5476 | 0.001415 | 1.5868e-05
| 466.15 | 300000 | 2062.3457 | 1548.1897 | 1.4182 | 1.5827e-05 | 193 | 2.9608 | 2.0623 | 1.5482 | 0.0014182 | 1.5827e-05
| 465.15 | 300000 | 2063.5549 | 1548.7654 | 1.4215 | 1.5786e-05 | 192 | 2.9608 | 2.0636 | 1.5488 | 0.0014215 | 1.5786e-05
| 464.15 | 300000 | 2064.7976 | 1549.3633 | 1.4248 | 1.5746e-05 | 191 | 2.9608 | 2.0648 | 1.5494 | 0.0014248 | 1.5746e-05
| 463.15 | 300000 | 2066.0747 | 1549.9841 | 1.4281 | 1.5705e-05 | 190 | 2.9608 | 2.0661 | 1.55 | 0.0014281 | 1.5705e-05
| 462.15 | 300000 | 2067.3867 | 1550.6283 | 1.4314 | 1.5664e-05 | 189 | 2.9608 | 2.0674 | 1.5506 | 0.0014314 | 1.5664e-05
| 461.15 | 300000 | 2068.7344 | 1551.2961 | 1.4348 | 1.5623e-05 | 188 | 2.9608 | 2.0687 | 1.5513 | 0.0014348 | 1.5623e-05
| 460.15 | 300000 | 2070.1189 | 1551.9884 | 1.4382 | 1.5582e-05 | 187 | 2.9608 | 2.0701 | 1.552 | 0.0014382 | 1.5582e-05
| 459.15 | 300000 | 2071.5405 | 1552.7056 | 1.4415 | 1.5541e-05 | 186 | 2.9608 | 2.0715 | 1.5527 | 0.0014415 | 1.5541e-05
| 458.15 | 300000 | 2073.0005 | 1553.4481 | 1.4449 | 1.55e-05 | 185 | 2.9608 | 2.073 | 1.5534 | 0.0014449 | 1.55e-05
| 457.15 | 300000 | 2074.4998 | 1554.2168 | 1.4484 | 1.5459e-05 | 184 | 2.9608 | 2.0745 | 1.5542 | 0.0014484 | 1.5459e-05
| 456.15 | 300000 | 2076.0391 | 1555.012 | 1.4518 | 1.5419e-05 | 183 | 2.9608 | 2.076 | 1.555 | 0.0014518 | 1.5419e-05
| 455.15 | 300000 | 2077.6191 | 1555.8345 | 1.4553 | 1.5378e-05 | 182 | 2.9608 | 2.0776 | 1.5558 | 0.0014553 | 1.5378e-05
| 454.15 | 300000 | 2079.2415 | 1556.6848 | 1.4587 | 1.5337e-05 | 181 | 2.9608 | 2.0792 | 1.5567 | 0.0014587 | 1.5337e-05
| 453.15 | 300000 | 2080.9067 | 1557.5638 | 1.4622 | 1.5296e-05 | 180 | 2.9608 | 2.0809 | 1.5576 | 0.0014622 | 1.5296e-05
| 452.15 | 300000 | 2082.6162 | 1558.472 | 1.4657 | 1.5256e-05 | 179 | 2.9608 | 2.0826 | 1.5585 | 0.0014657 | 1.5256e-05
| 451.15 | 300000 | 2084.3708 | 1559.4104 | 1.4693 | 1.5215e-05 | 178 | 2.9608 | 2.0844 | 1.5594 | 0.0014693 | 1.5215e-05
| 450.15 | 300000 | 2086.1716 | 1560.3794 | 1.4728 | 1.5174e-05 | 177 | 2.9608 | 2.0862 | 1.5604 | 0.0014728 | 1.5174e-05
| 449.15 | 300000 | 2088.02 | 1561.38 | 1.4764 | 1.5134e-05 | 176 | 2.9608 | 2.088 | 1.5614 | 0.0014764 | 1.5134e-05
| 448.15 | 300000 | 2089.9175 | 1562.4131 | 1.48 | 1.5093e-05 | 175 | 2.9608 | 2.0899 | 1.5624 | 0.00148 | 1.5093e-05
| 447.15 | 300000 | 2091.8647 | 1563.4795 | 1.4836 | 1.5052e-05 | 174 | 2.9608 | 2.0919 | 1.5635 | 0.0014836 | 1.5052e-05
| 446.15 | 300000 | 2093.8638 | 1564.5801 | 1.4872 | 1.5012e-05 | 173 | 2.9608 | 2.0939 | 1.5646 | 0.0014872 | 1.5012e-05
| 445.15 | 300000 | 2095.9158 | 1565.7159 | 1.4909 | 1.4971e-05 | 172 | 2.9608 | 2.0959 | 1.5657 | 0.0014909 | 1.4971e-05
| 444.15 | 300000 | 2098.0225 | 1566.8881 | 1.4946 | 1.493e-05 | 171 | 2.9608 | 2.098 | 1.5669 | 0.0014946 | 1.493e-05
| 443.15 | 300000 | 2100.1853 | 1568.0977 | 1.4983 | 1.489e-05 | 170 | 2.9608 | 2.1002 | 1.5681 | 0.0014983 | 1.489e-05
| 442.15 | 300000 | 2102.406 | 1569.3459 | 1.502 | 1.4849e-05 | 169 | 2.9608 | 2.1024 | 1.5693 | 0.001502 | 1.4849e-05
| 441.15 | 300000 | 2104.6865 | 1570.634 | 1.5057 | 1.4809e-05 | 168 | 2.9608 | 2.1047 | 1.5706 | 0.0015057 | 1.4809e-05
| 440.15 | 300000 | 2107.0291 | 1571.9634 | 1.5095 | 1.4768e-05 | 167 | 2.9608 | 2.107 | 1.572 | 0.0015095 | 1.4768e-05
| 439.15 | 300000 | 2109.4355 | 1573.3354 | 1.5133 | 1.4728e-05 | 166 | 2.9608 | 2.1094 | 1.5733 | 0.0015133 | 1.4728e-05
| 438.15 | 300000 | 2111.9082 | 1574.752 | 1.5171 | 1.4687e-05 | 165 | 2.9608 | 2.1119 | 1.5748 | 0.0015171 | 1.4687e-05
| 437.15 | 300000 | 2114.4497 | 1576.2145 | 1.5209 | 1.4647e-05 | 164 | 2.9608 | 2.1144 | 1.5762 | 0.0015209 | 1.4647e-05
| 436.15 | 300000 | 2117.0625 | 1577.7249 | 1.5248 | 1.4606e-05 | 163 | 2.9608 | 2.1171 | 1.5777 | 0.0015248 | 1.4606e-05
| 435.15 | 300000 | 2119.7498 | 1579.2854 | 1.5287 | 1.4566e-05 | 162 | 2.9608 | 2.1197 | 1.5793 | 0.0015287 | 1.4566e-05
| 434.15 | 300000 | 2122.5146 | 1580.8981 | 1.5326 | 1.4525e-05 | 161 | 2.9608 | 2.1225 | 1.5809 | 0.0015326 | 1.4525e-05
| 433.15 | 300000 | 2125.3601 | 1582.5654 | 1.5365 | 1.4485e-05 | 160 | 2.9608 | 2.1254 | 1.5826 | 0.0015365 | 1.4485e-05
| 432.15 | 300000 | 2128.2905 | 1584.29 | 1.5405 | 1.4445e-05 | 159 | 2.9608 | 2.1283 | 1.5843 | 0.0015405 | 1.4445e-05
| 431.15 | 300000 | 2131.3098 | 1586.0752 | 1.5444 | 1.4404e-05 | 158 | 2.9608 | 2.1313 | 1.5861 | 0.0015444 | 1.4404e-05
| 430.15 | 300000 | 2134.4224 | 1587.924 | 1.5484 | 1.4364e-05 | 157 | 2.9608 | 2.1344 | 1.5879 | 0.0015484 | 1.4364e-05
| 429.15 | 300000 | 2137.6335 | 1589.84 | 1.5525 | 1.4324e-05 | 156 | 2.9608 | 2.1376 | 1.5898 | 0.0015525 | 1.4324e-05
| 428.15 | 300000 | 2140.9485 | 1591.8273 | 1.5565 | 1.4283e-05 | 155 | 2.9608 | 2.1409 | 1.5918 | 0.0015565 | 1.4283e-05
| 427.15 | 300000 | 2144.3738 | 1593.8905 | 1.5606 | 1.4243e-05 | 154 | 2.9608 | 2.1444 | 1.5939 | 0.0015606 | 1.4243e-05
| 426.15 | 300000 | 2147.9163 | 1596.0345 | 1.5647 | 1.4203e-05 | 153 | 2.9608 | 2.1479 | 1.596 | 0.0015647 | 1.4203e-05
| 425.15 | 300000 | 2151.5835 | 1598.2653 | 1.5689 | 1.4163e-05 | 152 | 2.9608 | 2.1516 | 1.5983 | 0.0015689 | 1.4163e-05
| 424.15 | 300000 | 2155.384 | 1600.5889 | 1.573 | 1.4122e-05 | 151 | 2.9608 | 2.1554 | 1.6006 | 0.001573 | 1.4122e-05
| 423.15 | 300000 | 2159.3276 | 1603.0125 | 1.5772 | 1.4082e-05 | 150 | 2.9608 | 2.1593 | 1.603 | 0.0015772 | 1.4082e-05
| 422.15 | 300000 | 2163.4248 | 1605.5439 | 1.5814 | 1.4042e-05 | 149 | 2.9608 | 2.1634 | 1.6055 | 0.0015814 | 1.4042e-05
| 421.15 | 300000 | 2167.6882 | 1608.1925 | 1.5857 | 1.4002e-05 | 148 | 2.9608 | 2.1677 | 1.6082 | 0.0015857 | 1.4002e-05
| 420.15 | 300000 | 2172.1311 | 1610.9684 | 1.59 | 1.3962e-05 | 147 | 2.9608 | 2.1721 | 1.611 | 0.00159 | 1.3962e-05
| 419.15 | 300000 | 2176.769 | 1613.8828 | 1.5943 | 1.3922e-05 | 146 | 2.9608 | 2.1768 | 1.6139 | 0.0015943 | 1.3922e-05
| 418.15 | 300000 | 2181.6194 | 1616.9491 | 1.5986 | 1.3882e-05 | 145 | 2.9608 | 2.1816 | 1.6169 | 0.0015986 | 1.3882e-05
| 417.15 | 300000 | 2186.7021 | 1620.1819 | 1.603 | 1.3841e-05 | 144 | 2.9608 | 2.1867 | 1.6202 | 0.001603 | 1.3841e-05
| 416.15 | 300000 | 2192.0396 | 1623.598 | 1.6074 | 1.3801e-05 | 143 | 2.9608 | 2.192 | 1.6236 | 0.0016074 | 1.3801e-05
| 415.15 | 300000 | 2197.657 | 1627.2164 | 1.6118 | 1.3761e-05 | 142 | 2.9608 | 2.1977 | 1.6272 | 0.0016118 | 1.3761e-05
| 414.15 | 300000 | 2203.5833 | 1631.0588 | 1.6163 | 1.3721e-05 | 141 | 2.9608 | 2.2036 | 1.6311 | 0.0016163 | 1.3721e-05
| 413.15 | 300000 | 2209.8513 | 1635.1498 | 1.6208 | 1.3681e-05 | 140 | 2.9608 | 2.2099 | 1.6351 | 0.0016208 | 1.3681e-05
| 412.15 | 300000 | 2216.4985 | 1639.5173 | 1.6253 | 1.3641e-05 | 139 | 2.9608 | 2.2165 | 1.6395 | 0.0016253 | 1.3641e-05
| 411.15 | 300000 | 2223.5674 | 1644.1935 | 1.6299 | 1.3601e-05 | 138 | 2.9608 | 2.2236 | 1.6442 | 0.0016299 | 1.3601e-05
| 410.15 | 300000 | 2231.1064 | 1649.2145 | 1.6345 | 1.3562e-05 | 137 | 2.9608 | 2.2311 | 1.6492 | 0.0016345 | 1.3562e-05
| 409.15 | 300000 | 2239.1714 | 1654.6219 | 1.6391 | 1.3522e-05 | 136 | 2.9608 | 2.2392 | 1.6546 | 0.0016391 | 1.3522e-05
| 408.15 | 300000 | 2247.825 | 1660.4634 | 1.6438 | 1.3482e-05 | 135 | 2.9608 | 2.2478 | 1.6605 | 0.0016438 | 1.3482e-05
| 407.15 | 300000 | 2257.1399 | 1666.7927 | 1.6485 | 1.3442e-05 | 134 | 2.9608 | 2.2571 | 1.6668 | 0.0016485 | 1.3442e-05
| 406.15 | 300000 | 4270.894 | 3605.4001 | 932.2688 | 0.00020772 | 133 | 2.9608 | 4.2709 | 3.6054 | 0.93227 | 0.00020772
| 405.15 | 300000 | 4268.8223 | 3610.1418 | 933.1326 | 0.00020942 | 132 | 2.9608 | 4.2688 | 3.6101 | 0.93313 | 0.00020942
| 404.15 | 300000 | 4266.7798 | 3614.8948 | 933.9921 | 0.00021115 | 131 | 2.9608 | 4.2668 | 3.6149 | 0.93399 | 0.00021115
| 403.15 | 300000 | 4264.7656 | 3619.6592 | 934.8471 | 0.0002129 | 130 | 2.9608 | 4.2648 | 3.6197 | 0.93485 | 0.0002129
| 402.15 | 300000 | 4262.7788 | 3624.4348 | 935.6978 | 0.00021468 | 129 | 2.9608 | 4.2628 | 3.6244 | 0.9357 | 0.00021468
| 401.15 | 300000 | 4260.8203 | 3629.2214 | 936.5441 | 0.00021649 | 128 | 2.9608 | 4.2608 | 3.6292 | 0.93654 | 0.00021649
| 400.15 | 300000 | 4258.8887 | 3634.019 | 937.386 | 0.00021833 | 127 | 2.9608 | 4.2589 | 3.634 | 0.93739 | 0.00021833
| 399.15 | 300000 | 4256.9844 | 3638.8279 | 938.2234 | 0.0002202 | 126 | 2.9608 | 4.257 | 3.6388 | 0.93822 | 0.0002202
| 398.15 | 300000 | 4255.1069 | 3643.6475 | 939.0566 | 0.0002221 | 125 | 2.9608 | 4.2551 | 3.6436 | 0.93906 | 0.0002221
| 397.15 | 300000 | 4253.2559 | 3648.478 | 939.8853 | 0.00022403 | 124 | 2.9608 | 4.2533 | 3.6485 | 0.93989 | 0.00022403
| 396.15 | 300000 | 4251.4312 | 3653.3193 | 940.7097 | 0.00022599 | 123 | 2.9608 | 4.2514 | 3.6533 | 0.94071 | 0.00022599
| 395.15 | 300000 | 4249.6323 | 3658.1711 | 941.5297 | 0.00022799 | 122 | 2.9608 | 4.2496 | 3.6582 | 0.94153 | 0.00022799
| 394.15 | 300000 | 4247.8594 | 3663.0337 | 942.3452 | 0.00023002 | 121 | 2.9608 | 4.2479 | 3.663 | 0.94235 | 0.00023002
| 393.15 | 300000 | 4246.1113 | 3667.9065 | 943.1564 | 0.00023208 | 120 | 2.9608 | 4.2461 | 3.6679 | 0.94316 | 0.00023208
| 392.15 | 300000 | 4244.3892 | 3672.7898 | 943.9631 | 0.00023417 | 119 | 2.9608 | 4.2444 | 3.6728 | 0.94396 | 0.00023417
| 391.15 | 300000 | 4242.6914 | 3677.6836 | 944.7655 | 0.00023631 | 118 | 2.9608 | 4.2427 | 3.6777 | 0.94477 | 0.00023631
| 390.15 | 300000 | 4241.019 | 3682.5874 | 945.5635 | 0.00023847 | 117 | 2.9608 | 4.241 | 3.6826 | 0.94556 | 0.00023847
| 389.15 | 300000 | 4239.3706 | 3687.5015 | 946.3571 | 0.00024068 | 116 | 2.9608 | 4.2394 | 3.6875 | 0.94636 | 0.00024068
| 388.15 | 300000 | 4237.7471 | 3692.4253 | 947.1462 | 0.00024292 | 115 | 2.9608 | 4.2377 | 3.6924 | 0.94715 | 0.00024292
| 387.15 | 300000 | 4236.1475 | 3697.3594 | 947.9309 | 0.00024521 | 114 | 2.9608 | 4.2361 | 3.6974 | 0.94793 | 0.00024521
| 386.15 | 300000 | 4234.5718 | 3702.303 | 948.7112 | 0.00024753 | 113 | 2.9608 | 4.2346 | 3.7023 | 0.94871 | 0.00024753
| 385.15 | 300000 | 4233.0195 | 3707.2566 | 949.4871 | 0.00024989 | 112 | 2.9608 | 4.233 | 3.7073 | 0.94949 | 0.00024989
| 384.15 | 300000 | 4231.4912 | 3712.2195 | 950.2584 | 0.00025229 | 111 | 2.9608 | 4.2315 | 3.7122 | 0.95026 | 0.00025229
| 383.15 | 300000 | 4229.9863 | 3717.1919 | 951.0254 | 0.00025474 | 110 | 2.9608 | 4.23 | 3.7172 | 0.95103 | 0.00025474
| 382.15 | 300000 | 4228.5044 | 3722.1738 | 951.7878 | 0.00025723 | 109 | 2.9608 | 4.2285 | 3.7222 | 0.95179 | 0.00025723
| 381.15 | 300000 | 4227.0454 | 3727.1648 | 952.5458 | 0.00025977 | 108 | 2.9608 | 4.227 | 3.7272 | 0.95255 | 0.00025977
| 380.15 | 300000 | 4225.6094 | 3732.165 | 953.2994 | 0.00026235 | 107 | 2.9608 | 4.2256 | 3.7322 | 0.9533 | 0.00026235
| 379.15 | 300000 | 4224.1963 | 3737.1743 | 954.0484 | 0.00026498 | 106 | 2.9608 | 4.2242 | 3.7372 | 0.95405 | 0.00026498
| 378.15 | 300000 | 4222.8057 | 3742.1921 | 954.7929 | 0.00026765 | 105 | 2.9608 | 4.2228 | 3.7422 | 0.95479 | 0.00026765
| 377.15 | 300000 | 4221.4375 | 3747.2188 | 955.5329 | 0.00027038 | 104 | 2.9608 | 4.2214 | 3.7472 | 0.95553 | 0.00027038
| 376.15 | 300000 | 4220.0918 | 3752.2539 | 956.2683 | 0.00027315 | 103 | 2.9608 | 4.2201 | 3.7523 | 0.95627 | 0.00027315
| 375.15 | 300000 | 4218.7681 | 3757.2976 | 956.9993 | 0.00027598 | 102 | 2.9608 | 4.2188 | 3.7573 | 0.957 | 0.00027598
| 374.15 | 300000 | 4217.4668 | 3762.3494 | 957.7256 | 0.00027886 | 101 | 2.9608 | 4.2175 | 3.7623 | 0.95773 | 0.00027886
| 373.15 | 300000 | 4216.187 | 3767.4092 | 958.4473 | 0.0002818 | 100 | 2.9608 | 4.2162 | 3.7674 | 0.95845 | 0.0002818
| 372.15 | 300000 | 4214.9292 | 3772.4768 | 959.1645 | 0.00028479 | 99 | 2.9608 | 4.2149 | 3.7725 | 0.95916 | 0.00028479
| 371.15 | 300000 | 4213.6934 | 3777.5522 | 959.8771 | 0.00028784 | 98 | 2.9608 | 4.2137 | 3.7776 | 0.95988 | 0.00028784
| 370.15 | 300000 | 4212.479 | 3782.635 | 960.585 | 0.00029094 | 97 | 2.9608 | 4.2125 | 3.7826 | 0.96059 | 0.00029094
| 369.15 | 300000 | 4211.2861 | 3787.7251 | 961.2883 | 0.00029411 | 96 | 2.9608 | 4.2113 | 3.7877 | 0.96129 | 0.00029411
| 368.15 | 300000 | 4210.1152 | 3792.8223 | 961.9869 | 0.00029734 | 95 | 2.9608 | 4.2101 | 3.7928 | 0.96199 | 0.00029734
| 367.15 | 300000 | 4208.9653 | 3797.9265 | 962.6808 | 0.00030063 | 94 | 2.9608 | 4.209 | 3.7979 | 0.96268 | 0.00030063
| 366.15 | 300000 | 4207.8364 | 3803.0371 | 963.3701 | 0.00030399 | 93 | 2.9608 | 4.2078 | 3.803 | 0.96337 | 0.00030399
| 365.15 | 300000 | 4206.729 | 3808.1543 | 964.0546 | 0.00030741 | 92 | 2.9608 | 4.2067 | 3.8082 | 0.96405 | 0.00030741
| 364.15 | 300000 | 4205.6431 | 3813.2776 | 964.7344 | 0.0003109 | 91 | 2.9608 | 4.2056 | 3.8133 | 0.96473 | 0.0003109
| 363.15 | 300000 | 4204.5781 | 3818.4067 | 965.4094 | 0.00031447 | 90 | 2.9608 | 4.2046 | 3.8184 | 0.96541 | 0.00031447
| 362.15 | 300000 | 4203.5342 | 3823.5417 | 966.0796 | 0.0003181 | 89 | 2.9608 | 4.2035 | 3.8235 | 0.96608 | 0.0003181
| 361.15 | 300000 | 4202.5112 | 3828.6819 | 966.745 | 0.00032181 | 88 | 2.9608 | 4.2025 | 3.8287 | 0.96674 | 0.00032181
| 360.15 | 300000 | 4201.5093 | 3833.8271 | 967.4055 | 0.00032559 | 87 | 2.9608 | 4.2015 | 3.8338 | 0.96741 | 0.00032559
| 359.15 | 300000 | 4200.5283 | 3838.9773 | 968.0612 | 0.00032946 | 86 | 2.9608 | 4.2005 | 3.839 | 0.96806 | 0.00032946
| 358.15 | 300000 | 4199.5679 | 3844.1316 | 968.712 | 0.0003334 | 85 | 2.9608 | 4.1996 | 3.8441 | 0.96871 | 0.0003334
| 357.15 | 300000 | 4198.6289 | 3849.2903 | 969.3579 | 0.00033743 | 84 | 2.9608 | 4.1986 | 3.8493 | 0.96936 | 0.00033743
| 356.15 | 300000 | 4197.7104 | 3854.4526 | 969.9988 | 0.00034154 | 83 | 2.9608 | 4.1977 | 3.8545 | 0.97 | 0.00034154
| 355.15 | 300000 | 4196.8125 | 3859.6184 | 970.6348 | 0.00034574 | 82 | 2.9608 | 4.1968 | 3.8596 | 0.97063 | 0.00034574
| 354.15 | 300000 | 4195.9355 | 3864.7874 | 971.2658 | 0.00035003 | 81 | 2.9608 | 4.1959 | 3.8648 | 0.97127 | 0.00035003
| 353.15 | 300000 | 4195.0796 | 3869.9587 | 971.8917 | 0.00035441 | 80 | 2.9608 | 4.1951 | 3.87 | 0.97189 | 0.00035441
| 352.15 | 300000 | 4194.2441 | 3875.1323 | 972.5126 | 0.00035888 | 79 | 2.9608 | 4.1942 | 3.8751 | 0.97251 | 0.00035888
| 351.15 | 300000 | 4193.4297 | 3880.3079 | 973.1284 | 0.00036346 | 78 | 2.9608 | 4.1934 | 3.8803 | 0.97313 | 0.00036346
| 350.15 | 300000 | 4192.6357 | 3885.4849 | 973.739 | 0.00036813 | 77 | 2.9608 | 4.1926 | 3.8855 | 0.97374 | 0.00036813
| 349.15 | 300000 | 4191.8628 | 3890.6628 | 974.3444 | 0.00037291 | 76 | 2.9608 | 4.1919 | 3.8907 | 0.97434 | 0.00037291
| 348.15 | 300000 | 4191.1104 | 3895.8411 | 974.9447 | 0.0003778 | 75 | 2.9608 | 4.1911 | 3.8958 | 0.97494 | 0.0003778
| 347.15 | 300000 | 4190.3789 | 3901.0193 | 975.5397 | 0.00038279 | 74 | 2.9608 | 4.1904 | 3.901 | 0.97554 | 0.00038279
| 346.15 | 300000 | 4189.668 | 3906.197 | 976.1295 | 0.0003879 | 73 | 2.9608 | 4.1897 | 3.9062 | 0.97613 | 0.0003879
| 345.15 | 300000 | 4188.9775 | 3911.3738 | 976.7139 | 0.00039313 | 72 | 2.9608 | 4.189 | 3.9114 | 0.97671 | 0.00039313
| 344.15 | 300000 | 4188.3086 | 3916.5486 | 977.293 | 0.00039848 | 71 | 2.9608 | 4.1883 | 3.9165 | 0.97729 | 0.00039848
| 343.15 | 300000 | 4187.6597 | 3921.7214 | 977.8667 | 0.00040395 | 70 | 2.9608 | 4.1877 | 3.9217 | 0.97787 | 0.00040395
| 342.15 | 300000 | 4187.0317 | 3926.8914 | 978.435 | 0.00040955 | 69 | 2.9608 | 4.187 | 3.9269 | 0.97843 | 0.00040955
| 341.15 | 300000 | 4186.4248 | 3932.0579 | 978.9977 | 0.00041528 | 68 | 2.9608 | 4.1864 | 3.9321 | 0.979 | 0.00041528
| 340.15 | 300000 | 4185.8389 | 3937.2202 | 979.555 | 0.00042115 | 67 | 2.9608 | 4.1858 | 3.9372 | 0.97955 | 0.00042115
| 339.15 | 300000 | 4185.2734 | 3942.3777 | 980.1067 | 0.00042716 | 66 | 2.9608 | 4.1853 | 3.9424 | 0.98011 | 0.00042716
| 338.15 | 300000 | 4184.729 | 3947.53 | 980.6528 | 0.00043332 | 65 | 2.9608 | 4.1847 | 3.9475 | 0.98065 | 0.00043332
| 337.15 | 300000 | 4184.2056 | 3952.6758 | 981.1932 | 0.00043962 | 64 | 2.9608 | 4.1842 | 3.9527 | 0.98119 | 0.00043962
| 336.15 | 300000 | 4183.7026 | 3957.8149 | 981.7279 | 0.00044608 | 63 | 2.9608 | 4.1837 | 3.9578 | 0.98173 | 0.00044608
| 335.15 | 300000 | 4183.2212 | 3962.9463 | 982.2568 | 0.0004527 | 62 | 2.9608 | 4.1832 | 3.9629 | 0.98226 | 0.0004527
| 334.15 | 300000 | 4182.7603 | 3968.0691 | 982.78 | 0.00045949 | 61 | 2.9608 | 4.1828 | 3.9681 | 0.98278 | 0.00045949
| 333.15 | 300000 | 4182.3208 | 3973.1824 | 983.2972 | 0.00046645 | 60 | 2.9608 | 4.1823 | 3.9732 | 0.9833 | 0.00046645
| 332.15 | 300000 | 4181.9023 | 3978.2856 | 983.8085 | 0.00047358 | 59 | 2.9608 | 4.1819 | 3.9783 | 0.98381 | 0.00047358
| 331.15 | 300000 | 4181.5049 | 3983.3779 | 984.3139 | 0.0004809 | 58 | 2.9608 | 4.1815 | 3.9834 | 0.98431 | 0.0004809
| 330.15 | 300000 | 4181.1289 | 3988.458 | 984.8132 | 0.00048841 | 57 | 2.9608 | 4.1811 | 3.9885 | 0.98481 | 0.00048841
| 329.15 | 300000 | 4180.7739 | 3993.5251 | 985.3064 | 0.00049611 | 56 | 2.9608 | 4.1808 | 3.9935 | 0.98531 | 0.00049611
| 328.15 | 300000 | 4180.4404 | 3998.5784 | 985.7934 | 0.00050402 | 55 | 2.9608 | 4.1804 | 3.9986 | 0.98579 | 0.00050402
| 327.15 | 300000 | 4180.1279 | 4003.6167 | 986.2742 | 0.00051214 | 54 | 2.9608 | 4.1801 | 4.0036 | 0.98627 | 0.00051214
| 326.15 | 300000 | 4179.8369 | 4008.6389 | 986.7488 | 0.00052048 | 53 | 2.9608 | 4.1798 | 4.0086 | 0.98675 | 0.00052048
| 325.15 | 300000 | 4179.5679 | 4013.644 | 987.2169 | 0.00052904 | 52 | 2.9608 | 4.1796 | 4.0136 | 0.98722 | 0.00052904
| 324.15 | 300000 | 4179.3203 | 4018.6311 | 987.6786 | 0.00053784 | 51 | 2.9608 | 4.1793 | 4.0186 | 0.98768 | 0.00053784
| 323.15 | 300000 | 4179.0942 | 4023.5986 | 988.1339 | 0.00054689 | 50 | 2.9608 | 4.1791 | 4.0236 | 0.98813 | 0.00054689
| 322.15 | 300000 | 4178.8901 | 4028.5459 | 988.5825 | 0.00055618 | 49 | 2.9608 | 4.1789 | 4.0285 | 0.98858 | 0.00055618
| 321.15 | 300000 | 4178.708 | 4033.4712 | 989.0245 | 0.00056574 | 48 | 2.9608 | 4.1787 | 4.0335 | 0.98902 | 0.00056574
| 320.15 | 300000 | 4178.5479 | 4038.3738 | 989.4598 | 0.00057557 | 47 | 2.9608 | 4.1785 | 4.0384 | 0.98946 | 0.00057557
| 319.15 | 300000 | 4178.4102 | 4043.252 | 989.8882 | 0.00058569 | 46 | 2.9608 | 4.1784 | 4.0433 | 0.98989 | 0.00058569
| 318.15 | 300000 | 4178.2949 | 4048.1047 | 990.3098 | 0.0005961 | 45 | 2.9608 | 4.1783 | 4.0481 | 0.99031 | 0.0005961
| 317.15 | 300000 | 4178.2021 | 4052.9304 | 990.7244 | 0.00060681 | 44 | 2.9608 | 4.1782 | 4.0529 | 0.99072 | 0.00060681
| 316.15 | 300000 | 4178.1323 | 4057.728 | 991.132 | 0.00061785 | 43 | 2.9608 | 4.1781 | 4.0577 | 0.99113 | 0.00061785
| 315.15 | 300000 | 4178.0854 | 4062.4961 | 991.5323 | 0.00062921 | 42 | 2.9608 | 4.1781 | 4.0625 | 0.99153 | 0.00062921
| 314.15 | 300000 | 4178.0625 | 4067.2327 | 991.9254 | 0.00064092 | 41 | 2.9608 | 4.1781 | 4.0672 | 0.99193 | 0.00064092
| 313.15 | 300000 | 4178.063 | 4071.937 | 992.3112 | 0.00065299 | 40 | 2.9608 | 4.1781 | 4.0719 | 0.99231 | 0.00065299
| 312.15 | 300000 | 4178.0874 | 4076.6072 | 992.6895 | 0.00066544 | 39 | 2.9608 | 4.1781 | 4.0766 | 0.99269 | 0.00066544
| 311.15 | 300000 | 4178.1362 | 4081.2417 | 993.0602 | 0.00067828 | 38 | 2.9608 | 4.1781 | 4.0812 | 0.99306 | 0.00067828
| 310.15 | 300000 | 4178.2104 | 4085.8394 | 993.4233 | 0.00069153 | 37 | 2.9608 | 4.1782 | 4.0858 | 0.99342 | 0.00069153
| 309.15 | 300000 | 4178.3101 | 4090.3979 | 993.7786 | 0.0007052 | 36 | 2.9608 | 4.1783 | 4.0904 | 0.99378 | 0.0007052
| 308.15 | 300000 | 4178.4355 | 4094.9165 | 994.126 | 0.00071932 | 35 | 2.9608 | 4.1784 | 4.0949 | 0.99413 | 0.00071932
| 307.15 | 300000 | 4178.5879 | 4099.3931 | 994.4655 | 0.0007339 | 34 | 2.9608 | 4.1786 | 4.0994 | 0.99447 | 0.0007339
| 306.15 | 300000 | 4178.7681 | 4103.8257 | 994.7967 | 0.00074897 | 33 | 2.9608 | 4.1788 | 4.1038 | 0.9948 | 0.00074897
| 305.15 | 300000 | 4178.9761 | 4108.2134 | 995.1197 | 0.00076455 | 32 | 2.9608 | 4.179 | 4.1082 | 0.99512 | 0.00076455
| 304.15 | 300000 | 4179.2139 | 4112.5542 | 995.4343 | 0.00078066 | 31 | 2.9608 | 4.1792 | 4.1126 | 0.99543 | 0.00078066
| 303.15 | 300000 | 4179.4814 | 4116.8462 | 995.7404 | 0.00079733 | 30 | 2.9608 | 4.1795 | 4.1168 | 0.99574 | 0.00079733
| 302.15 | 300000 | 4179.7808 | 4121.0884 | 996.0378 | 0.00081458 | 29 | 2.9608 | 4.1798 | 4.1211 | 0.99604 | 0.00081458
| 301.15 | 300000 | 4180.1133 | 4125.2783 | 996.3264 | 0.00083245 | 28 | 2.9608 | 4.1801 | 4.1253 | 0.99633 | 0.00083245
| 300.15 | 300000 | 4180.4795 | 4129.4146 | 996.6059 | 0.00085096 | 27 | 2.9608 | 4.1805 | 4.1294 | 0.99661 | 0.00085096
| 299.15 | 300000 | 4180.8823 | 4133.4951 | 996.8763 | 0.00087014 | 26 | 2.9608 | 4.1809 | 4.1335 | 0.99688 | 0.00087014
| 298.15 | 300000 | 4181.3228 | 4137.519 | 997.1375 | 0.00089004 | 25 | 2.9608 | 4.1813 | 4.1375 | 0.99714 | 0.00089004
| 297.15 | 300000 | 4181.8032 | 4141.4844 | 997.3891 | 0.00091068 | 24 | 2.9608 | 4.1818 | 4.1415 | 0.99739 | 0.00091068
| 296.15 | 300000 | 4182.3257 | 4145.3896 | 997.631 | 0.0009321 | 23 | 2.9608 | 4.1823 | 4.1454 | 0.99763 | 0.0009321
| 295.15 | 300000 | 4182.8936 | 4149.2329 | 997.8632 | 0.00095436 | 22 | 2.9608 | 4.1829 | 4.1492 | 0.99786 | 0.00095436
| 294.15 | 300000 | 4183.5093 | 4153.0127 | 998.0852 | 0.00097748 | 21 | 2.9608 | 4.1835 | 4.153 | 0.99809 | 0.00097748
| 293.15 | 300000 | 4184.1758 | 4156.7275 | 998.2969 | 0.0010015 | 20 | 2.9608 | 4.1842 | 4.1567 | 0.9983 | 0.0010015
| 292.15 | 300000 | 4184.897 | 4160.376 | 998.4982 | 0.0010265 | 19 | 2.9608 | 4.1849 | 4.1604 | 0.9985 | 0.0010265
| 291.15 | 300000 | 4185.6772 | 4163.957 | 998.6888 | 0.0010526 | 18 | 2.9608 | 4.1857 | 4.164 | 0.99869 | 0.0010526
| 290.15 | 300000 | 4186.5205 | 4167.4688 | 998.8684 | 0.0010797 | 17 | 2.9608 | 4.1865 | 4.1675 | 0.99887 | 0.0010797
| 289.15 | 300000 | 4187.4321 | 4170.9106 | 999.0368 | 0.0011079 | 16 | 2.9608 | 4.1874 | 4.1709 | 0.99904 | 0.0011079
| 288.15 | 300000 | 4188.418 | 4174.2812 | 999.1938 | 0.0011374 | 15 | 2.9608 | 4.1884 | 4.1743 | 0.99919 | 0.0011374
| 287.15 | 300000 | 4189.4834 | 4177.5801 | 999.339 | 0.0011682 | 14 | 2.9608 | 4.1895 | 4.1776 | 0.99934 | 0.0011682
| 286.15 | 300000 | 4190.6353 | 4180.8052 | 999.4722 | 0.0012003 | 13 | 2.9608 | 4.1906 | 4.1808 | 0.99947 | 0.0012003
| 285.15 | 300000 | 4191.8823 | 4183.957 | 999.593 | 0.0012338 | 12 | 2.9608 | 4.1919 | 4.184 | 0.99959 | 0.0012338
| 284.15 | 300000 | 4193.2319 | 4187.0342 | 999.7012 | 0.0012689 | 11 | 2.9608 | 4.1932 | 4.187 | 0.9997 | 0.0012689
| 283.15 | 300000 | 4194.6938 | 4190.0371 | 999.7964 | 0.0013057 | 10 | 2.9608 | 4.1947 | 4.19 | 0.9998 | 0.0013057
| 282.15 | 300000 | 4196.2783 | 4192.9648 | 999.8783 | 0.0013441 | 9 | 2.9608 | 4.1963 | 4.193 | 0.99988 | 0.0013441
| 281.15 | 300000 | 4197.9971 | 4195.8179 | 999.9465 | 0.0013844 | 8 | 2.9608 | 4.198 | 4.1958 | 0.99995 | 0.0013844
| 280.15 | 300000 | 4199.8628 | 4198.5962 | 1000.0005 | 0.0014267 | 7 | 2.9608 | 4.1999 | 4.1986 | 1 | 0.0014267
| 279.15 | 300000 | 4201.8896 | 4201.3008 | 1000.04 | 0.0014711 | 6 | 2.9608 | 4.2019 | 4.2013 | 1 | 0.0014711
| 278.15 | 300000 | 4204.0938 | 4203.9316 | 1000.0646 | 0.0015178 | 5 | 2.9608 | 4.2041 | 4.2039 | 1.0001 | 0.0015178
| 277.15 | 300000 | 4206.4912 | 4206.4907 | 1000.0737 | 0.0015669 | 4 | 2.9608 | 4.2065 | 4.2065 | 1.0001 | 0.0015669
| 276.15 | 300000 | 4209.1025 | 4208.978 | 1000.0668 | 0.0016185 | 3 | 2.9608 | 4.2091 | 4.209 | 1.0001 | 0.0016185
| 275.15 | 300000 | 4211.9482 | 4211.3965 | 1000.0436 | 0.001673 | 2 | 2.9608 | 4.2119 | 4.2114 | 1 | 0.001673
| 274.15 | 300000 | 4215.0518 | 4213.7471 | 1000.0033 | 0.0017304 | 0.99999 | 2.9608 | 4.2151 | 4.2137 | 1 | 0.0017304
| 273.15 | 300000 | 4218.439 | 4216.0327 | 999.9454 | 0.001791 | -6.1035e-06 | 2.9608 | 4.2184 | 4.216 | 0.99995 | 0.001791
| 473.15 | 200000 | 2013.8756 | 1521.2822 | 0.92548 | 1.6146e-05 | 200 | 1.9738 | 2.0139 | 1.5213 | 0.00092548 | 1.6146e-05
| 472.15 | 200000 | 2014.2909 | 1521.3521 | 0.92753 | 1.6105e-05 | 199 | 1.9738 | 2.0143 | 1.5214 | 0.00092753 | 1.6105e-05
| 471.15 | 200000 | 2014.7244 | 1521.4343 | 0.92959 | 1.6064e-05 | 198 | 1.9738 | 2.0147 | 1.5214 | 0.00092959 | 1.6064e-05
| 470.15 | 200000 | 2015.1761 | 1521.5293 | 0.93165 | 1.6023e-05 | 197 | 1.9738 | 2.0152 | 1.5215 | 0.00093165 | 1.6023e-05
| 469.15 | 200000 | 2015.6467 | 1521.6371 | 0.93373 | 1.5983e-05 | 196 | 1.9738 | 2.0156 | 1.5216 | 0.00093373 | 1.5983e-05
| 468.15 | 200000 | 2016.1366 | 1521.7582 | 0.93582 | 1.5942e-05 | 195 | 1.9738 | 2.0161 | 1.5218 | 0.00093582 | 1.5942e-05
| 467.15 | 200000 | 2016.646 | 1521.8927 | 0.93791 | 1.5901e-05 | 194 | 1.9738 | 2.0166 | 1.5219 | 0.00093791 | 1.5901e-05
| 466.15 | 200000 | 2017.1753 | 1522.0409 | 0.94002 | 1.5861e-05 | 193 | 1.9738 | 2.0172 | 1.522 | 0.00094002 | 1.5861e-05
| 465.15 | 200000 | 2017.7251 | 1522.203 | 0.94214 | 1.582e-05 | 192 | 1.9738 | 2.0177 | 1.5222 | 0.00094214 | 1.582e-05
| 464.15 | 200000 | 2018.2955 | 1522.3795 | 0.94427 | 1.578e-05 | 191 | 1.9738 | 2.0183 | 1.5224 | 0.00094427 | 1.578e-05
| 463.15 | 200000 | 2018.8873 | 1522.5706 | 0.9464 | 1.5739e-05 | 190 | 1.9738 | 2.0189 | 1.5226 | 0.0009464 | 1.5739e-05
| 462.15 | 200000 | 2019.5007 | 1522.7765 | 0.94855 | 1.5698e-05 | 189 | 1.9738 | 2.0195 | 1.5228 | 0.00094855 | 1.5698e-05
| 461.15 | 200000 | 2020.1364 | 1522.9976 | 0.95071 | 1.5658e-05 | 188 | 1.9738 | 2.0201 | 1.523 | 0.00095071 | 1.5658e-05
| 460.15 | 200000 | 2020.7946 | 1523.2341 | 0.95288 | 1.5617e-05 | 187 | 1.9738 | 2.0208 | 1.5232 | 0.00095288 | 1.5617e-05
| 459.15 | 200000 | 2021.4757 | 1523.4865 | 0.95506 | 1.5577e-05 | 186 | 1.9738 | 2.0215 | 1.5235 | 0.00095506 | 1.5577e-05
| 458.15 | 200000 | 2022.1804 | 1523.755 | 0.95726 | 1.5536e-05 | 185 | 1.9738 | 2.0222 | 1.5238 | 0.00095726 | 1.5536e-05
| 457.15 | 200000 | 2022.9092 | 1524.0399 | 0.95946 | 1.5496e-05 | 184 | 1.9738 | 2.0229 | 1.524 | 0.00095946 | 1.5496e-05
| 456.15 | 200000 | 2023.6626 | 1524.3417 | 0.96167 | 1.5455e-05 | 183 | 1.9738 | 2.0237 | 1.5243 | 0.00096167 | 1.5455e-05
| 455.15 | 200000 | 2024.4409 | 1524.6606 | 0.9639 | 1.5415e-05 | 182 | 1.9738 | 2.0244 | 1.5247 | 0.0009639 | 1.5415e-05
| 454.15 | 200000 | 2025.2449 | 1524.9971 | 0.96614 | 1.5375e-05 | 181 | 1.9738 | 2.0252 | 1.525 | 0.00096614 | 1.5375e-05
| 453.15 | 200000 | 2026.0751 | 1525.3514 | 0.96839 | 1.5334e-05 | 180 | 1.9738 | 2.0261 | 1.5254 | 0.00096839 | 1.5334e-05
| 452.15 | 200000 | 2026.9319 | 1525.724 | 0.97065 | 1.5294e-05 | 179 | 1.9738 | 2.0269 | 1.5257 | 0.00097065 | 1.5294e-05
| 451.15 | 200000 | 2027.816 | 1526.1152 | 0.97292 | 1.5253e-05 | 178 | 1.9738 | 2.0278 | 1.5261 | 0.00097292 | 1.5253e-05
| 450.15 | 200000 | 2028.7281 | 1526.5256 | 0.9752 | 1.5213e-05 | 177 | 1.9738 | 2.0287 | 1.5265 | 0.0009752 | 1.5213e-05
| 449.15 | 200000 | 2029.6687 | 1526.9553 | 0.9775 | 1.5173e-05 | 176 | 1.9738 | 2.0297 | 1.527 | 0.0009775 | 1.5173e-05
| 448.15 | 200000 | 2030.6384 | 1527.405 | 0.97981 | 1.5133e-05 | 175 | 1.9738 | 2.0306 | 1.5274 | 0.00097981 | 1.5133e-05
| 447.15 | 200000 | 2031.6378 | 1527.8751 | 0.98213 | 1.5092e-05 | 174 | 1.9738 | 2.0316 | 1.5279 | 0.00098213 | 1.5092e-05
| 446.15 | 200000 | 2032.6677 | 1528.3658 | 0.98446 | 1.5052e-05 | 173 | 1.9738 | 2.0327 | 1.5284 | 0.00098446 | 1.5052e-05
| 445.15 | 200000 | 2033.7288 | 1528.8779 | 0.9868 | 1.5012e-05 | 172 | 1.9738 | 2.0337 | 1.5289 | 0.0009868 | 1.5012e-05
| 444.15 | 200000 | 2034.8217 | 1529.4116 | 0.98916 | 1.4972e-05 | 171 | 1.9738 | 2.0348 | 1.5294 | 0.00098916 | 1.4972e-05
| 443.15 | 200000 | 2035.9471 | 1529.9675 | 0.99153 | 1.4931e-05 | 170 | 1.9738 | 2.0359 | 1.53 | 0.00099153 | 1.4931e-05
| 442.15 | 200000 | 2037.1058 | 1530.5463 | 0.99391 | 1.4891e-05 | 169 | 1.9738 | 2.0371 | 1.5305 | 0.00099391 | 1.4891e-05
| 441.15 | 200000 | 2038.2987 | 1531.1481 | 0.99631 | 1.4851e-05 | 168 | 1.9738 | 2.0383 | 1.5311 | 0.00099631 | 1.4851e-05
| 440.15 | 200000 | 2039.5265 | 1531.7738 | 0.99871 | 1.4811e-05 | 167 | 1.9738 | 2.0395 | 1.5318 | 0.00099871 | 1.4811e-05
| 439.15 | 200000 | 2040.79 | 1532.4238 | 1.0011 | 1.4771e-05 | 166 | 1.9738 | 2.0408 | 1.5324 | 0.0010011 | 1.4771e-05
| 438.15 | 200000 | 2042.0902 | 1533.0988 | 1.0036 | 1.4731e-05 | 165 | 1.9738 | 2.0421 | 1.5331 | 0.0010036 | 1.4731e-05
| 437.15 | 200000 | 2043.4279 | 1533.7993 | 1.006 | 1.4691e-05 | 164 | 1.9738 | 2.0434 | 1.5338 | 0.001006 | 1.4691e-05
| 436.15 | 200000 | 2044.8038 | 1534.5259 | 1.0085 | 1.4651e-05 | 163 | 1.9738 | 2.0448 | 1.5345 | 0.0010085 | 1.4651e-05
| 435.15 | 200000 | 2046.2194 | 1535.2794 | 1.011 | 1.4611e-05 | 162 | 1.9738 | 2.0462 | 1.5353 | 0.001011 | 1.4611e-05
| 434.15 | 200000 | 2047.6753 | 1536.0604 | 1.0134 | 1.4571e-05 | 161 | 1.9738 | 2.0477 | 1.5361 | 0.0010134 | 1.4571e-05
| 433.15 | 200000 | 2049.1726 | 1536.8698 | 1.0159 | 1.4531e-05 | 160 | 1.9738 | 2.0492 | 1.5369 | 0.0010159 | 1.4531e-05
| 432.15 | 200000 | 2050.7126 | 1537.708 | 1.0185 | 1.4491e-05 | 159 | 1.9738 | 2.0507 | 1.5377 | 0.0010185 | 1.4491e-05
| 431.15 | 200000 | 2052.2964 | 1538.5762 | 1.021 | 1.4451e-05 | 158 | 1.9738 | 2.0523 | 1.5386 | 0.001021 | 1.4451e-05
| 430.15 | 200000 | 2053.925 | 1539.4749 | 1.0235 | 1.4411e-05 | 157 | 1.9738 | 2.0539 | 1.5395 | 0.0010235 | 1.4411e-05
| 429.15 | 200000 | 2055.6001 | 1540.4052 | 1.0261 | 1.4371e-05 | 156 | 1.9738 | 2.0556 | 1.5404 | 0.0010261 | 1.4371e-05
| 428.15 | 200000 | 2057.3228 | 1541.3679 | 1.0287 | 1.4332e-05 | 155 | 1.9738 | 2.0573 | 1.5414 | 0.0010287 | 1.4332e-05
| 427.15 | 200000 | 2059.0945 | 1542.3641 | 1.0313 | 1.4292e-05 | 154 | 1.9738 | 2.0591 | 1.5424 | 0.0010313 | 1.4292e-05
| 426.15 | 200000 | 2060.9167 | 1543.395 | 1.0339 | 1.4252e-05 | 153 | 1.9738 | 2.0609 | 1.5434 | 0.0010339 | 1.4252e-05
| 425.15 | 200000 | 2062.7913 | 1544.4615 | 1.0365 | 1.4212e-05 | 152 | 1.9738 | 2.0628 | 1.5445 | 0.0010365 | 1.4212e-05
| 424.15 | 200000 | 2064.72 | 1545.5649 | 1.0391 | 1.4172e-05 | 151 | 1.9738 | 2.0647 | 1.5456 | 0.0010391 | 1.4172e-05
| 423.15 | 200000 | 2066.7043 | 1546.7067 | 1.0418 | 1.4133e-05 | 150 | 1.9738 | 2.0667 | 1.5467 | 0.0010418 | 1.4133e-05
| 422.15 | 200000 | 2068.7466 | 1547.8881 | 1.0444 | 1.4093e-05 | 149 | 1.9738 | 2.0687 | 1.5479 | 0.0010444 | 1.4093e-05
| 421.15 | 200000 | 2070.8491 | 1549.1107 | 1.0471 | 1.4053e-05 | 148 | 1.9738 | 2.0708 | 1.5491 | 0.0010471 | 1.4053e-05
| 420.15 | 200000 | 2073.0137 | 1550.3762 | 1.0498 | 1.4014e-05 | 147 | 1.9738 | 2.073 | 1.5504 | 0.0010498 | 1.4014e-05
| 419.15 | 200000 | 2075.2434 | 1551.6864 | 1.0525 | 1.3974e-05 | 146 | 1.9738 | 2.0752 | 1.5517 | 0.0010525 | 1.3974e-05
| 418.15 | 200000 | 2077.5405 | 1553.0435 | 1.0553 | 1.3935e-05 | 145 | 1.9738 | 2.0775 | 1.553 | 0.0010553 | 1.3935e-05
| 417.15 | 200000 | 2079.9087 | 1554.4493 | 1.058 | 1.3895e-05 | 144 | 1.9738 | 2.0799 | 1.5544 | 0.001058 | 1.3895e-05
| 416.15 | 200000 | 2082.3506 | 1555.9065 | 1.0608 | 1.3856e-05 | 143 | 1.9738 | 2.0824 | 1.5559 | 0.0010608 | 1.3856e-05
| 415.15 | 200000 | 2084.8701 | 1557.4177 | 1.0636 | 1.3816e-05 | 142 | 1.9738 | 2.0849 | 1.5574 | 0.0010636 | 1.3816e-05
| 414.15 | 200000 | 2087.4712 | 1558.986 | 1.0664 | 1.3777e-05 | 141 | 1.9738 | 2.0875 | 1.559 | 0.0010664 | 1.3777e-05
| 413.15 | 200000 | 2090.1584 | 1560.6143 | 1.0692 | 1.3737e-05 | 140 | 1.9738 | 2.0902 | 1.5606 | 0.0010692 | 1.3737e-05
| 412.15 | 200000 | 2092.9365 | 1562.3065 | 1.072 | 1.3698e-05 | 139 | 1.9738 | 2.0929 | 1.5623 | 0.001072 | 1.3698e-05
| 411.15 | 200000 | 2095.811 | 1564.0667 | 1.0749 | 1.3659e-05 | 138 | 1.9738 | 2.0958 | 1.5641 | 0.0010749 | 1.3659e-05
| 410.15 | 200000 | 2098.7881 | 1565.8992 | 1.0778 | 1.3619e-05 | 137 | 1.9738 | 2.0988 | 1.5659 | 0.0010778 | 1.3619e-05
| 409.15 | 200000 | 2101.874 | 1567.8092 | 1.0807 | 1.358e-05 | 136 | 1.9738 | 2.1019 | 1.5678 | 0.0010807 | 1.358e-05
| 408.15 | 200000 | 2105.0769 | 1569.8025 | 1.0836 | 1.3541e-05 | 135 | 1.9738 | 2.1051 | 1.5698 | 0.0010836 | 1.3541e-05
| 407.15 | 200000 | 2108.405 | 1571.8854 | 1.0865 | 1.3501e-05 | 134 | 1.9738 | 2.1084 | 1.5719 | 0.0010865 | 1.3501e-05
| 406.15 | 200000 | 2111.8677 | 1574.0652 | 1.0894 | 1.3462e-05 | 133 | 1.9738 | 2.1119 | 1.5741 | 0.0010894 | 1.3462e-05
| 405.15 | 200000 | 2115.4763 | 1576.35 | 1.0924 | 1.3423e-05 | 132 | 1.9738 | 2.1155 | 1.5763 | 0.0010924 | 1.3423e-05
| 404.15 | 200000 | 2119.2424 | 1578.749 | 1.0954 | 1.3384e-05 | 131 | 1.9738 | 2.1192 | 1.5787 | 0.0010954 | 1.3384e-05
| 403.15 | 200000 | 2123.1802 | 1581.2728 | 1.0984 | 1.3345e-05 | 130 | 1.9738 | 2.1232 | 1.5813 | 0.0010984 | 1.3345e-05
| 402.15 | 200000 | 2127.3049 | 1583.9332 | 1.1014 | 1.3306e-05 | 129 | 1.9738 | 2.1273 | 1.5839 | 0.0011014 | 1.3306e-05
| 401.15 | 200000 | 2131.6343 | 1586.7438 | 1.1045 | 1.3267e-05 | 128 | 1.9738 | 2.1316 | 1.5867 | 0.0011045 | 1.3267e-05
| 400.15 | 200000 | 2136.1885 | 1589.7197 | 1.1076 | 1.3228e-05 | 127 | 1.9738 | 2.1362 | 1.5897 | 0.0011076 | 1.3228e-05
| 399.15 | 200000 | 2140.9902 | 1592.8787 | 1.1106 | 1.3189e-05 | 126 | 1.9738 | 2.141 | 1.5929 | 0.0011106 | 1.3189e-05
| 398.15 | 200000 | 2146.0654 | 1596.2402 | 1.1138 | 1.315e-05 | 125 | 1.9738 | 2.1461 | 1.5962 | 0.0011138 | 1.315e-05
| 397.15 | 200000 | 2151.4441 | 1599.8274 | 1.1169 | 1.3111e-05 | 124 | 1.9738 | 2.1514 | 1.5998 | 0.0011169 | 1.3111e-05
| 396.15 | 200000 | 2157.1594 | 1603.666 | 1.1201 | 1.3072e-05 | 123 | 1.9738 | 2.1572 | 1.6037 | 0.0011201 | 1.3072e-05
| 395.15 | 200000 | 2163.2505 | 1607.7855 | 1.1232 | 1.3033e-05 | 122 | 1.9738 | 2.1633 | 1.6078 | 0.0011232 | 1.3033e-05
| 394.15 | 200000 | 2169.761 | 1612.2198 | 1.1265 | 1.2994e-05 | 121 | 1.9738 | 2.1698 | 1.6122 | 0.0011265 | 1.2994e-05
| 393.15 | 200000 | 4246.3672 | 3668.0259 | 943.1063 | 0.00023205 | 120 | 1.9738 | 4.2464 | 3.668 | 0.94311 | 0.00023205
| 392.15 | 200000 | 4244.6431 | 3672.9104 | 943.9133 | 0.00023415 | 119 | 1.9738 | 4.2446 | 3.6729 | 0.94391 | 0.00023415
| 391.15 | 200000 | 4242.9443 | 3677.8054 | 944.7159 | 0.00023628 | 118 | 1.9738 | 4.2429 | 3.6778 | 0.94472 | 0.00023628
| 390.15 | 200000 | 4241.27 | 3682.7104 | 945.514 | 0.00023845 | 117 | 1.9738 | 4.2413 | 3.6827 | 0.94551 | 0.00023845
| 389.15 | 200000 | 4239.6206 | 3687.6255 | 946.3077 | 0.00024065 | 116 | 1.9738 | 4.2396 | 3.6876 | 0.94631 | 0.00024065
| 388.15 | 200000 | 4237.9951 | 3692.5508 | 947.097 | 0.0002429 | 115 | 1.9738 | 4.238 | 3.6926 | 0.9471 | 0.0002429
| 387.15 | 200000 | 4236.394 | 3697.4861 | 947.882 | 0.00024518 | 114 | 1.9738 | 4.2364 | 3.6975 | 0.94788 | 0.00024518
| 386.15 | 200000 | 4234.8169 | 3702.4312 | 948.6624 | 0.0002475 | 113 | 1.9738 | 4.2348 | 3.7024 | 0.94866 | 0.0002475
| 385.15 | 200000 | 4233.2637 | 3707.3857 | 949.4384 | 0.00024986 | 112 | 1.9738 | 4.2333 | 3.7074 | 0.94944 | 0.00024986
| 384.15 | 200000 | 4231.7339 | 3712.3501 | 950.21 | 0.00025227 | 111 | 1.9738 | 4.2317 | 3.7124 | 0.95021 | 0.00025227
| 383.15 | 200000 | 4230.2275 | 3717.324 | 950.9771 | 0.00025471 | 110 | 1.9738 | 4.2302 | 3.7173 | 0.95098 | 0.00025471
| 382.15 | 200000 | 4228.7446 | 3722.3071 | 951.7397 | 0.00025721 | 109 | 1.9738 | 4.2287 | 3.7223 | 0.95174 | 0.00025721
| 381.15 | 200000 | 4227.2847 | 3727.2996 | 952.4979 | 0.00025974 | 108 | 1.9738 | 4.2273 | 3.7273 | 0.9525 | 0.00025974
| 380.15 | 200000 | 4225.8472 | 3732.3013 | 953.2515 | 0.00026232 | 107 | 1.9738 | 4.2258 | 3.7323 | 0.95325 | 0.00026232
| 379.15 | 200000 | 4224.4331 | 3737.3118 | 954.0007 | 0.00026495 | 106 | 1.9738 | 4.2244 | 3.7373 | 0.954 | 0.00026495
| 378.15 | 200000 | 4223.0415 | 3742.3313 | 954.7454 | 0.00026763 | 105 | 1.9738 | 4.223 | 3.7423 | 0.95475 | 0.00026763
| 377.15 | 200000 | 4221.6724 | 3747.3594 | 955.4855 | 0.00027035 | 104 | 1.9738 | 4.2217 | 3.7474 | 0.95549 | 0.00027035
| 376.15 | 200000 | 4220.3252 | 3752.396 | 956.2211 | 0.00027313 | 103 | 1.9738 | 4.2203 | 3.7524 | 0.95622 | 0.00027313
| 375.15 | 200000 | 4219.0005 | 3757.4409 | 956.9521 | 0.00027596 | 102 | 1.9738 | 4.219 | 3.7574 | 0.95695 | 0.00027596
| 374.15 | 200000 | 4217.6982 | 3762.4944 | 957.6786 | 0.00027884 | 101 | 1.9738 | 4.2177 | 3.7625 | 0.95768 | 0.00027884
| 373.15 | 200000 | 4216.4175 | 3767.5557 | 958.4005 | 0.00028177 | 100 | 1.9738 | 4.2164 | 3.7676 | 0.9584 | 0.00028177
| 372.15 | 200000 | 4215.1592 | 3772.625 | 959.1178 | 0.00028476 | 99 | 1.9738 | 4.2152 | 3.7726 | 0.95912 | 0.00028476
| 371.15 | 200000 | 4213.9224 | 3777.7019 | 959.8305 | 0.00028781 | 98 | 1.9738 | 4.2139 | 3.7777 | 0.95983 | 0.00028781
| 370.15 | 200000 | 4212.707 | 3782.7864 | 960.5385 | 0.00029092 | 97 | 1.9738 | 4.2127 | 3.7828 | 0.96054 | 0.00029092
| 369.15 | 200000 | 4211.5137 | 3787.8782 | 961.2419 | 0.00029408 | 96 | 1.9738 | 4.2115 | 3.7879 | 0.96124 | 0.00029408
| 368.15 | 200000 | 4210.3413 | 3792.9771 | 961.9407 | 0.00029731 | 95 | 1.9738 | 4.2103 | 3.793 | 0.96194 | 0.00029731
| 367.15 | 200000 | 4209.1909 | 3798.0828 | 962.6348 | 0.0003006 | 94 | 1.9738 | 4.2092 | 3.7981 | 0.96263 | 0.0003006
| 366.15 | 200000 | 4208.0615 | 3803.1953 | 963.3241 | 0.00030396 | 93 | 1.9738 | 4.2081 | 3.8032 | 0.96332 | 0.00030396
| 365.15 | 200000 | 4206.9536 | 3808.3142 | 964.0087 | 0.00030738 | 92 | 1.9738 | 4.207 | 3.8083 | 0.96401 | 0.00030738
| 364.15 | 200000 | 4205.8667 | 3813.4392 | 964.6886 | 0.00031088 | 91 | 1.9738 | 4.2059 | 3.8134 | 0.96469 | 0.00031088
| 363.15 | 200000 | 4204.8013 | 3818.5701 | 965.3637 | 0.00031444 | 90 | 1.9738 | 4.2048 | 3.8186 | 0.96536 | 0.00031444
| 362.15 | 200000 | 4203.7568 | 3823.7068 | 966.0341 | 0.00031807 | 89 | 1.9738 | 4.2038 | 3.8237 | 0.96603 | 0.00031807
| 361.15 | 200000 | 4202.7334 | 3828.8489 | 966.6995 | 0.00032178 | 88 | 1.9738 | 4.2027 | 3.8288 | 0.9667 | 0.00032178
| 360.15 | 200000 | 4201.731 | 3833.9958 | 967.3602 | 0.00032557 | 87 | 1.9738 | 4.2017 | 3.834 | 0.96736 | 0.00032557
| 359.15 | 200000 | 4200.7495 | 3839.1479 | 968.016 | 0.00032943 | 86 | 1.9738 | 4.2007 | 3.8391 | 0.96802 | 0.00032943
| 358.15 | 200000 | 4199.7886 | 3844.3042 | 968.6669 | 0.00033337 | 85 | 1.9738 | 4.1998 | 3.8443 | 0.96867 | 0.00033337
| 357.15 | 200000 | 4198.8491 | 3849.4648 | 969.3129 | 0.0003374 | 84 | 1.9738 | 4.1988 | 3.8495 | 0.96931 | 0.0003374
| 356.15 | 200000 | 4197.9302 | 3854.6292 | 969.9539 | 0.00034151 | 83 | 1.9738 | 4.1979 | 3.8546 | 0.96995 | 0.00034151
| 355.15 | 200000 | 4197.0322 | 3859.7969 | 970.59 | 0.00034571 | 82 | 1.9738 | 4.197 | 3.8598 | 0.97059 | 0.00034571
| 354.15 | 200000 | 4196.1553 | 3864.9675 | 971.221 | 0.00035 | 81 | 1.9738 | 4.1962 | 3.865 | 0.97122 | 0.00035
| 353.15 | 200000 | 4195.2988 | 3870.1411 | 971.847 | 0.00035438 | 80 | 1.9738 | 4.1953 | 3.8701 | 0.97185 | 0.00035438
| 352.15 | 200000 | 4194.4634 | 3875.3169 | 972.468 | 0.00035886 | 79 | 1.9738 | 4.1945 | 3.8753 | 0.97247 | 0.00035886
| 351.15 | 200000 | 4193.6489 | 3880.4944 | 973.0838 | 0.00036343 | 78 | 1.9738 | 4.1936 | 3.8805 | 0.97308 | 0.00036343
| 350.15 | 200000 | 4192.855 | 3885.6733 | 973.6945 | 0.00036811 | 77 | 1.9738 | 4.1929 | 3.8857 | 0.97369 | 0.00036811
| 349.15 | 200000 | 4192.0815 | 3890.8535 | 974.3 | 0.00037289 | 76 | 1.9738 | 4.1921 | 3.8909 | 0.9743 | 0.00037289
| 348.15 | 200000 | 4191.3291 | 3896.0339 | 974.9004 | 0.00037777 | 75 | 1.9738 | 4.1913 | 3.896 | 0.9749 | 0.00037777
| 347.15 | 200000 | 4190.5977 | 3901.2144 | 975.4955 | 0.00038277 | 74 | 1.9738 | 4.1906 | 3.9012 | 0.9755 | 0.00038277
| 346.15 | 200000 | 4189.8867 | 3906.3943 | 976.0853 | 0.00038788 | 73 | 1.9738 | 4.1899 | 3.9064 | 0.97609 | 0.00038788
| 345.15 | 200000 | 4189.1968 | 3911.573 | 976.6698 | 0.00039311 | 72 | 1.9738 | 4.1892 | 3.9116 | 0.97667 | 0.00039311
| 344.15 | 200000 | 4188.5273 | 3916.7502 | 977.249 | 0.00039845 | 71 | 1.9738 | 4.1885 | 3.9168 | 0.97725 | 0.00039845
| 343.15 | 200000 | 4187.8789 | 3921.9253 | 977.8227 | 0.00040393 | 70 | 1.9738 | 4.1879 | 3.9219 | 0.97782 | 0.00040393
| 342.15 | 200000 | 4187.251 | 3927.0974 | 978.3911 | 0.00040953 | 69 | 1.9738 | 4.1873 | 3.9271 | 0.97839 | 0.00040953
| 341.15 | 200000 | 4186.6445 | 3932.2664 | 978.9539 | 0.00041526 | 68 | 1.9738 | 4.1866 | 3.9323 | 0.97895 | 0.00041526
| 340.15 | 200000 | 4186.0586 | 3937.4309 | 979.5112 | 0.00042113 | 67 | 1.9738 | 4.1861 | 3.9374 | 0.97951 | 0.00042113
| 339.15 | 200000 | 4185.4932 | 3942.5908 | 980.0629 | 0.00042714 | 66 | 1.9738 | 4.1855 | 3.9426 | 0.98006 | 0.00042714
| 338.15 | 200000 | 4184.9492 | 3947.7454 | 980.609 | 0.00043329 | 65 | 1.9738 | 4.1849 | 3.9477 | 0.98061 | 0.00043329
| 337.15 | 200000 | 4184.4263 | 3952.8938 | 981.1495 | 0.0004396 | 64 | 1.9738 | 4.1844 | 3.9529 | 0.98115 | 0.0004396
| 336.15 | 200000 | 4183.9238 | 3958.0354 | 981.6842 | 0.00044606 | 63 | 1.9738 | 4.1839 | 3.958 | 0.98168 | 0.00044606
| 335.15 | 200000 | 4183.4429 | 3963.1692 | 982.2132 | 0.00045268 | 62 | 1.9738 | 4.1834 | 3.9632 | 0.98221 | 0.00045268
| 334.15 | 200000 | 4182.9824 | 3968.2944 | 982.7363 | 0.00045947 | 61 | 1.9738 | 4.183 | 3.9683 | 0.98274 | 0.00045947
| 333.15 | 200000 | 4182.5435 | 3973.4104 | 983.2536 | 0.00046642 | 60 | 1.9738 | 4.1825 | 3.9734 | 0.98325 | 0.00046642
| 332.15 | 200000 | 4182.1255 | 3978.5161 | 983.765 | 0.00047356 | 59 | 1.9738 | 4.1821 | 3.9785 | 0.98376 | 0.00047356
| 331.15 | 200000 | 4181.729 | 3983.6108 | 984.2703 | 0.00048088 | 58 | 1.9738 | 4.1817 | 3.9836 | 0.98427 | 0.00048088
| 330.15 | 200000 | 4181.3535 | 3988.6936 | 984.7697 | 0.00048839 | 57 | 1.9738 | 4.1814 | 3.9887 | 0.98477 | 0.00048839
| 329.15 | 200000 | 4180.9995 | 3993.7634 | 985.2629 | 0.00049609 | 56 | 1.9738 | 4.181 | 3.9938 | 0.98526 | 0.00049609
| 328.15 | 200000 | 4180.6665 | 3998.8193 | 985.7499 | 0.000504 | 55 | 1.9738 | 4.1807 | 3.9988 | 0.98575 | 0.000504
| 327.15 | 200000 | 4180.355 | 4003.8601 | 986.2308 | 0.00051212 | 54 | 1.9738 | 4.1804 | 4.0039 | 0.98623 | 0.00051212
| 326.15 | 200000 | 4180.0654 | 4008.8853 | 986.7053 | 0.00052046 | 53 | 1.9738 | 4.1801 | 4.0089 | 0.98671 | 0.00052046
| 325.15 | 200000 | 4179.7969 | 4013.8931 | 987.1735 | 0.00052903 | 52 | 1.9738 | 4.1798 | 4.0139 | 0.98717 | 0.00052903
| 324.15 | 200000 | 4179.5503 | 4018.8828 | 987.6352 | 0.00053783 | 51 | 1.9738 | 4.1796 | 4.0189 | 0.98764 | 0.00053783
| 323.15 | 200000 | 4179.3257 | 4023.8533 | 988.0904 | 0.00054687 | 50 | 1.9738 | 4.1793 | 4.0239 | 0.98809 | 0.00054687
| 322.15 | 200000 | 4179.1226 | 4028.8032 | 988.5391 | 0.00055617 | 49 | 1.9738 | 4.1791 | 4.0288 | 0.98854 | 0.00055617
| 321.15 | 200000 | 4178.9419 | 4033.7317 | 988.981 | 0.00056573 | 48 | 1.9738 | 4.1789 | 4.0337 | 0.98898 | 0.00056573
| 320.15 | 200000 | 4178.7832 | 4038.637 | 989.4163 | 0.00057556 | 47 | 1.9738 | 4.1788 | 4.0386 | 0.98942 | 0.00057556
| 319.15 | 200000 | 4178.6465 | 4043.5181 | 989.8447 | 0.00058567 | 46 | 1.9738 | 4.1786 | 4.0435 | 0.98984 | 0.00058567
| 318.15 | 200000 | 4178.5327 | 4048.3738 | 990.2663 | 0.00059608 | 45 | 1.9738 | 4.1785 | 4.0484 | 0.99027 | 0.00059608
| 317.15 | 200000 | 4178.4414 | 4053.2026 | 990.6808 | 0.0006068 | 44 | 1.9738 | 4.1784 | 4.0532 | 0.99068 | 0.0006068
| 316.15 | 200000 | 4178.3735 | 4058.0032 | 991.0883 | 0.00061783 | 43 | 1.9738 | 4.1784 | 4.058 | 0.99109 | 0.00061783
| 315.15 | 200000 | 4178.3286 | 4062.7742 | 991.4886 | 0.0006292 | 42 | 1.9738 | 4.1783 | 4.0628 | 0.99149 | 0.0006292
| 314.15 | 200000 | 4178.3071 | 4067.5142 | 991.8817 | 0.00064091 | 41 | 1.9738 | 4.1783 | 4.0675 | 0.99188 | 0.00064091
| 313.15 | 200000 | 4178.3091 | 4072.2214 | 992.2675 | 0.00065299 | 40 | 1.9738 | 4.1783 | 4.0722 | 0.99227 | 0.00065299
| 312.15 | 200000 | 4178.3359 | 4076.8948 | 992.6457 | 0.00066543 | 39 | 1.9738 | 4.1783 | 4.0769 | 0.99265 | 0.00066543
| 311.15 | 200000 | 4178.3867 | 4081.5327 | 993.0164 | 0.00067827 | 38 | 1.9738 | 4.1784 | 4.0815 | 0.99302 | 0.00067827
| 310.15 | 200000 | 4178.4629 | 4086.1333 | 993.3794 | 0.00069152 | 37 | 1.9738 | 4.1785 | 4.0861 | 0.99338 | 0.00069152
| 309.15 | 200000 | 4178.5649 | 4090.6953 | 993.7346 | 0.0007052 | 36 | 1.9738 | 4.1786 | 4.0907 | 0.99373 | 0.0007052
| 308.15 | 200000 | 4178.6929 | 4095.2173 | 994.082 | 0.00071932 | 35 | 1.9738 | 4.1787 | 4.0952 | 0.99408 | 0.00071932
| 307.15 | 200000 | 4178.8477 | 4099.6968 | 994.4213 | 0.0007339 | 34 | 1.9738 | 4.1788 | 4.0997 | 0.99442 | 0.0007339
| 306.15 | 200000 | 4179.0303 | 4104.1333 | 994.7525 | 0.00074897 | 33 | 1.9738 | 4.179 | 4.1041 | 0.99475 | 0.00074897
| 305.15 | 200000 | 4179.2412 | 4108.5244 | 995.0754 | 0.00076455 | 32 | 1.9738 | 4.1792 | 4.1085 | 0.99508 | 0.00076455
| 304.15 | 200000 | 4179.4819 | 4112.8687 | 995.39 | 0.00078066 | 31 | 1.9738 | 4.1795 | 4.1129 | 0.99539 | 0.00078066
| 303.15 | 200000 | 4179.7524 | 4117.1646 | 995.6959 | 0.00079734 | 30 | 1.9738 | 4.1798 | 4.1172 | 0.9957 | 0.00079734
| 302.15 | 200000 | 4180.0552 | 4121.4097 | 995.9932 | 0.00081459 | 29 | 1.9738 | 4.1801 | 4.1214 | 0.99599 | 0.00081459
| 301.15 | 200000 | 4180.3906 | 4125.6035 | 996.2817 | 0.00083246 | 28 | 1.9738 | 4.1804 | 4.1256 | 0.99628 | 0.00083246
| 300.15 | 200000 | 4180.7607 | 4129.7432 | 996.5612 | 0.00085097 | 27 | 1.9738 | 4.1808 | 4.1297 | 0.99656 | 0.00085097
| 299.15 | 200000 | 4181.167 | 4133.8281 | 996.8315 | 0.00087016 | 26 | 1.9738 | 4.1812 | 4.1338 | 0.99683 | 0.00087016
| 298.15 | 200000 | 4181.6113 | 4137.856 | 997.0925 | 0.00089006 | 25 | 1.9738 | 4.1816 | 4.1379 | 0.99709 | 0.00089006
| 297.15 | 200000 | 4182.0957 | 4141.8252 | 997.3439 | 0.0009107 | 24 | 1.9738 | 4.1821 | 4.1418 | 0.99734 | 0.0009107
| 296.15 | 200000 | 4182.623 | 4145.7339 | 997.5858 | 0.00093213 | 23 | 1.9738 | 4.1826 | 4.1457 | 0.99759 | 0.00093213
| 295.15 | 200000 | 4183.1948 | 4149.5815 | 997.8177 | 0.00095439 | 22 | 1.9738 | 4.1832 | 4.1496 | 0.99782 | 0.00095439
| 294.15 | 200000 | 4183.8154 | 4153.3652 | 998.0396 | 0.00097752 | 21 | 1.9738 | 4.1838 | 4.1534 | 0.99804 | 0.00097752
| 293.15 | 200000 | 4184.4868 | 4157.0845 | 998.2512 | 0.0010016 | 20 | 1.9738 | 4.1845 | 4.1571 | 0.99825 | 0.0010016
| 292.15 | 200000 | 4185.2134 | 4160.7373 | 998.4523 | 0.0010266 | 19 | 1.9738 | 4.1852 | 4.1607 | 0.99845 | 0.0010266
| 291.15 | 200000 | 4185.999 | 4164.3228 | 998.6428 | 0.0010526 | 18 | 1.9738 | 4.186 | 4.1643 | 0.99864 | 0.0010526
| 290.15 | 200000 | 4186.8481 | 4167.8394 | 998.8221 | 0.0010797 | 17 | 1.9738 | 4.1868 | 4.1678 | 0.99882 | 0.0010797
| 289.15 | 200000 | 4187.7661 | 4171.2856 | 998.9904 | 0.001108 | 16 | 1.9738 | 4.1878 | 4.1713 | 0.99899 | 0.001108
| 288.15 | 200000 | 4188.7578 | 4174.6611 | 999.1472 | 0.0011375 | 15 | 1.9738 | 4.1888 | 4.1747 | 0.99915 | 0.0011375
| 287.15 | 200000 | 4189.8301 | 4177.9644 | 999.2921 | 0.0011682 | 14 | 1.9738 | 4.1898 | 4.178 | 0.99929 | 0.0011682
| 286.15 | 200000 | 4190.9897 | 4181.1948 | 999.4251 | 0.0012004 | 13 | 1.9738 | 4.191 | 4.1812 | 0.99943 | 0.0012004
| 285.15 | 200000 | 4192.2441 | 4184.3516 | 999.5457 | 0.0012339 | 12 | 1.9738 | 4.1922 | 4.1844 | 0.99955 | 0.0012339
| 284.15 | 200000 | 4193.6016 | 4187.4341 | 999.6537 | 0.001269 | 11 | 1.9738 | 4.1936 | 4.1874 | 0.99965 | 0.001269
| 283.15 | 200000 | 4195.0723 | 4190.4419 | 999.7487 | 0.0013058 | 10 | 1.9738 | 4.1951 | 4.1904 | 0.99975 | 0.0013058
| 282.15 | 200000 | 4196.666 | 4193.3755 | 999.8303 | 0.0013442 | 9 | 1.9738 | 4.1967 | 4.1934 | 0.99983 | 0.0013442
| 281.15 | 200000 | 4198.394 | 4196.2344 | 999.8982 | 0.0013846 | 8 | 1.9738 | 4.1984 | 4.1962 | 0.9999 | 0.0013846
| 280.15 | 200000 | 4200.27 | 4199.019 | 999.952 | 0.0014269 | 7 | 1.9738 | 4.2003 | 4.199 | 0.99995 | 0.0014269
| 279.15 | 200000 | 4202.3081 | 4201.7295 | 999.9912 | 0.0014713 | 6 | 1.9738 | 4.2023 | 4.2017 | 0.99999 | 0.0014713
| 278.15 | 200000 | 4204.5229 | 4204.3672 | 1000.0154 | 0.001518 | 5 | 1.9738 | 4.2045 | 4.2044 | 1 | 0.001518
| 277.15 | 200000 | 4206.9331 | 4206.9326 | 1000.0242 | 0.0015671 | 4 | 1.9738 | 4.2069 | 4.2069 | 1 | 0.0015671
| 276.15 | 200000 | 4209.5571 | 4209.4272 | 1000.0171 | 0.0016187 | 3 | 1.9738 | 4.2096 | 4.2094 | 1 | 0.0016187
| 275.15 | 200000 | 4212.4165 | 4211.853 | 999.9935 | 0.0016732 | 2 | 1.9738 | 4.2124 | 4.2119 | 0.99999 | 0.0016732
| 274.15 | 200000 | 4215.5347 | 4214.2109 | 999.9528 | 0.0017306 | 0.99999 | 1.9738 | 4.2155 | 4.2142 | 0.99995 | 0.0017306
| 273.15 | 200000 | 4218.938 | 4216.5044 | 999.8945 | 0.0017913 | -6.1035e-06 | 1.9738 | 4.2189 | 4.2165 | 0.99989 | 0.0017913
| 473.15 | 100000 | 1975.688 | 1499.2363 | 0.4603 | 1.6177e-05 | 200 | 0.98692 | 1.9757 | 1.4992 | 0.0004603 | 1.6177e-05
| 472.15 | 100000 | 1975.5853 | 1498.975 | 0.4613 | 1.6136e-05 | 199 | 0.98692 | 1.9756 | 1.499 | 0.0004613 | 1.6136e-05
| 471.15 | 100000 | 1975.4916 | 1498.7197 | 0.4623 | 1.6096e-05 | 198 | 0.98692 | 1.9755 | 1.4987 | 0.0004623 | 1.6096e-05
| 470.15 | 100000 | 1975.4066 | 1498.4709 | 0.4633 | 1.6056e-05 | 197 | 0.98692 | 1.9754 | 1.4985 | 0.0004633 | 1.6056e-05
| 469.15 | 100000 | 1975.3307 | 1498.2285 | 0.46431 | 1.6015e-05 | 196 | 0.98692 | 1.9753 | 1.4982 | 0.00046431 | 1.6015e-05
| 468.15 | 100000 | 1975.264 | 1497.9929 | 0.46532 | 1.5975e-05 | 195 | 0.98692 | 1.9753 | 1.498 | 0.00046532 | 1.5975e-05
| 467.15 | 100000 | 1975.2069 | 1497.7639 | 0.46634 | 1.5935e-05 | 194 | 0.98692 | 1.9752 | 1.4978 | 0.00046634 | 1.5935e-05
| 466.15 | 100000 | 1975.1593 | 1497.5419 | 0.46737 | 1.5894e-05 | 193 | 0.98692 | 1.9752 | 1.4975 | 0.00046737 | 1.5894e-05
| 465.15 | 100000 | 1975.1216 | 1497.3269 | 0.46839 | 1.5854e-05 | 192 | 0.98692 | 1.9751 | 1.4973 | 0.00046839 | 1.5854e-05
| 464.15 | 100000 | 1975.0938 | 1497.119 | 0.46943 | 1.5814e-05 | 191 | 0.98692 | 1.9751 | 1.4971 | 0.00046943 | 1.5814e-05
| 463.15 | 100000 | 1975.0762 | 1496.9185 | 0.47046 | 1.5773e-05 | 190 | 0.98692 | 1.9751 | 1.4969 | 0.00047046 | 1.5773e-05
| 462.15 | 100000 | 1975.069 | 1496.7253 | 0.47151 | 1.5733e-05 | 189 | 0.98692 | 1.9751 | 1.4967 | 0.00047151 | 1.5733e-05
| 461.15 | 100000 | 1975.0724 | 1496.5398 | 0.47255 | 1.5693e-05 | 188 | 0.98692 | 1.9751 | 1.4965 | 0.00047255 | 1.5693e-05
| 460.15 | 100000 | 1975.0865 | 1496.3619 | 0.47361 | 1.5653e-05 | 187 | 0.98692 | 1.9751 | 1.4964 | 0.00047361 | 1.5653e-05
| 459.15 | 100000 | 1975.1118 | 1496.192 | 0.47466 | 1.5612e-05 | 186 | 0.98692 | 1.9751 | 1.4962 | 0.00047466 | 1.5612e-05
| 458.15 | 100000 | 1975.1483 | 1496.0302 | 0.47572 | 1.5572e-05 | 185 | 0.98692 | 1.9751 | 1.496 | 0.00047572 | 1.5572e-05
| 457.15 | 100000 | 1975.1962 | 1495.8763 | 0.47679 | 1.5532e-05 | 184 | 0.98692 | 1.9752 | 1.4959 | 0.00047679 | 1.5532e-05
| 456.15 | 100000 | 1975.2559 | 1495.7311 | 0.47786 | 1.5492e-05 | 183 | 0.98692 | 1.9753 | 1.4957 | 0.00047786 | 1.5492e-05
| 455.15 | 100000 | 1975.3274 | 1495.5942 | 0.47894 | 1.5452e-05 | 182 | 0.98692 | 1.9753 | 1.4956 | 0.00047894 | 1.5452e-05
| 454.15 | 100000 | 1975.4111 | 1495.4661 | 0.48002 | 1.5412e-05 | 181 | 0.98692 | 1.9754 | 1.4955 | 0.00048002 | 1.5412e-05
| 453.15 | 100000 | 1975.5072 | 1495.3468 | 0.48111 | 1.5372e-05 | 180 | 0.98692 | 1.9755 | 1.4953 | 0.00048111 | 1.5372e-05
| 452.15 | 100000 | 1975.6161 | 1495.2366 | 0.4822 | 1.5332e-05 | 179 | 0.98692 | 1.9756 | 1.4952 | 0.0004822 | 1.5332e-05
| 451.15 | 100000 | 1975.7378 | 1495.1355 | 0.4833 | 1.5292e-05 | 178 | 0.98692 | 1.9757 | 1.4951 | 0.0004833 | 1.5292e-05
| 450.15 | 100000 | 1975.8727 | 1495.0439 | 0.4844 | 1.5252e-05 | 177 | 0.98692 | 1.9759 | 1.495 | 0.0004844 | 1.5252e-05
| 449.15 | 100000 | 1976.021 | 1494.9619 | 0.48551 | 1.5212e-05 | 176 | 0.98692 | 1.976 | 1.495 | 0.00048551 | 1.5212e-05
| 448.15 | 100000 | 1976.1831 | 1494.8896 | 0.48662 | 1.5172e-05 | 175 | 0.98692 | 1.9762 | 1.4949 | 0.00048662 | 1.5172e-05
| 447.15 | 100000 | 1976.3593 | 1494.8274 | 0.48774 | 1.5132e-05 | 174 | 0.98692 | 1.9764 | 1.4948 | 0.00048774 | 1.5132e-05
| 446.15 | 100000 | 1976.5497 | 1494.7754 | 0.48887 | 1.5092e-05 | 173 | 0.98692 | 1.9765 | 1.4948 | 0.00048887 | 1.5092e-05
| 445.15 | 100000 | 1976.7546 | 1494.7338 | 0.49 | 1.5052e-05 | 172 | 0.98692 | 1.9768 | 1.4947 | 0.00049 | 1.5052e-05
| 444.15 | 100000 | 1976.9745 | 1494.7026 | 0.49113 | 1.5013e-05 | 171 | 0.98692 | 1.977 | 1.4947 | 0.00049113 | 1.5013e-05
| 443.15 | 100000 | 1977.2097 | 1494.6825 | 0.49227 | 1.4973e-05 | 170 | 0.98692 | 1.9772 | 1.4947 | 0.00049227 | 1.4973e-05
| 442.15 | 100000 | 1977.4603 | 1494.6733 | 0.49342 | 1.4933e-05 | 169 | 0.98692 | 1.9775 | 1.4947 | 0.00049342 | 1.4933e-05
| 441.15 | 100000 | 1977.7268 | 1494.6754 | 0.49457 | 1.4893e-05 | 168 | 0.98692 | 1.9777 | 1.4947 | 0.00049457 | 1.4893e-05
| 440.15 | 100000 | 1978.0095 | 1494.689 | 0.49573 | 1.4854e-05 | 167 | 0.98692 | 1.978 | 1.4947 | 0.00049573 | 1.4854e-05
| 439.15 | 100000 | 1978.3087 | 1494.7144 | 0.49689 | 1.4814e-05 | 166 | 0.98692 | 1.9783 | 1.4947 | 0.00049689 | 1.4814e-05
| 438.15 | 100000 | 1978.6248 | 1494.7518 | 0.49806 | 1.4774e-05 | 165 | 0.98692 | 1.9786 | 1.4948 | 0.00049806 | 1.4774e-05
| 437.15 | 100000 | 1978.9581 | 1494.8014 | 0.49924 | 1.4735e-05 | 164 | 0.98692 | 1.979 | 1.4948 | 0.00049924 | 1.4735e-05
| 436.15 | 100000 | 1979.3091 | 1494.8635 | 0.50042 | 1.4695e-05 | 163 | 0.98692 | 1.9793 | 1.4949 | 0.00050042 | 1.4695e-05
| 435.15 | 100000 | 1979.678 | 1494.9384 | 0.5016 | 1.4656e-05 | 162 | 0.98692 | 1.9797 | 1.4949 | 0.0005016 | 1.4656e-05
| 434.15 | 100000 | 1980.0653 | 1495.0264 | 0.5028 | 1.4616e-05 | 161 | 0.98692 | 1.9801 | 1.495 | 0.0005028 | 1.4616e-05
| 433.15 | 100000 | 1980.4713 | 1495.1276 | 0.504 | 1.4576e-05 | 160 | 0.98692 | 1.9805 | 1.4951 | 0.000504 | 1.4576e-05
| 432.15 | 100000 | 1980.8965 | 1495.2424 | 0.5052 | 1.4537e-05 | 159 | 0.98692 | 1.9809 | 1.4952 | 0.0005052 | 1.4537e-05
| 431.15 | 100000 | 1981.3413 | 1495.3711 | 0.50641 | 1.4498e-05 | 158 | 0.98692 | 1.9813 | 1.4954 | 0.00050641 | 1.4498e-05
| 430.15 | 100000 | 1981.8062 | 1495.514 | 0.50763 | 1.4458e-05 | 157 | 0.98692 | 1.9818 | 1.4955 | 0.00050763 | 1.4458e-05
| 429.15 | 100000 | 1982.2914 | 1495.6715 | 0.50886 | 1.4419e-05 | 156 | 0.98692 | 1.9823 | 1.4957 | 0.00050886 | 1.4419e-05
| 428.15 | 100000 | 1982.7976 | 1495.8436 | 0.51009 | 1.4379e-05 | 155 | 0.98692 | 1.9828 | 1.4958 | 0.00051009 | 1.4379e-05
| 427.15 | 100000 | 1983.3252 | 1496.031 | 0.51132 | 1.434e-05 | 154 | 0.98692 | 1.9833 | 1.496 | 0.00051132 | 1.434e-05
| 426.15 | 100000 | 1983.8745 | 1496.2339 | 0.51257 | 1.4301e-05 | 153 | 0.98692 | 1.9839 | 1.4962 | 0.00051257 | 1.4301e-05
| 425.15 | 100000 | 1984.4463 | 1496.4525 | 0.51382 | 1.4261e-05 | 152 | 0.98692 | 1.9844 | 1.4965 | 0.00051382 | 1.4261e-05
| 424.15 | 100000 | 1985.0409 | 1496.6874 | 0.51507 | 1.4222e-05 | 151 | 0.98692 | 1.985 | 1.4967 | 0.00051507 | 1.4222e-05
| 423.15 | 100000 | 1985.6589 | 1496.9386 | 0.51634 | 1.4183e-05 | 150 | 0.98692 | 1.9857 | 1.4969 | 0.00051634 | 1.4183e-05
| 422.15 | 100000 | 1986.3008 | 1497.2069 | 0.5176 | 1.4144e-05 | 149 | 0.98692 | 1.9863 | 1.4972 | 0.0005176 | 1.4144e-05
| 421.15 | 100000 | 1986.9672 | 1497.4924 | 0.51888 | 1.4105e-05 | 148 | 0.98692 | 1.987 | 1.4975 | 0.00051888 | 1.4105e-05
| 420.15 | 100000 | 1987.6584 | 1497.7957 | 0.52016 | 1.4066e-05 | 147 | 0.98692 | 1.9877 | 1.4978 | 0.00052016 | 1.4066e-05
| 419.15 | 100000 | 1988.3755 | 1498.1171 | 0.52145 | 1.4026e-05 | 146 | 0.98692 | 1.9884 | 1.4981 | 0.00052145 | 1.4026e-05
| 418.15 | 100000 | 1989.1188 | 1498.4569 | 0.52275 | 1.3987e-05 | 145 | 0.98692 | 1.9891 | 1.4985 | 0.00052275 | 1.3987e-05
| 417.15 | 100000 | 1989.8888 | 1498.8158 | 0.52406 | 1.3948e-05 | 144 | 0.98692 | 1.9899 | 1.4988 | 0.00052406 | 1.3948e-05
| 416.15 | 100000 | 1990.6864 | 1499.1941 | 0.52537 | 1.3909e-05 | 143 | 0.98692 | 1.9907 | 1.4992 | 0.00052537 | 1.3909e-05
| 415.15 | 100000 | 1991.5122 | 1499.5923 | 0.52669 | 1.387e-05 | 142 | 0.98692 | 1.9915 | 1.4996 | 0.00052669 | 1.387e-05
| 414.15 | 100000 | 1992.3669 | 1500.0109 | 0.52801 | 1.3832e-05 | 141 | 0.98692 | 1.9924 | 1.5 | 0.00052801 | 1.3832e-05
| 413.15 | 100000 | 1993.2513 | 1500.4506 | 0.52934 | 1.3793e-05 | 140 | 0.98692 | 1.9933 | 1.5005 | 0.00052934 | 1.3793e-05
| 412.15 | 100000 | 1994.1661 | 1500.9116 | 0.53068 | 1.3754e-05 | 139 | 0.98692 | 1.9942 | 1.5009 | 0.00053068 | 1.3754e-05
| 411.15 | 100000 | 1995.1122 | 1501.3947 | 0.53203 | 1.3715e-05 | 138 | 0.98692 | 1.9951 | 1.5014 | 0.00053203 | 1.3715e-05
| 410.15 | 100000 | 1996.0902 | 1501.9005 | 0.53339 | 1.3676e-05 | 137 | 0.98692 | 1.9961 | 1.5019 | 0.00053339 | 1.3676e-05
| 409.15 | 100000 | 1997.1012 | 1502.4296 | 0.53475 | 1.3638e-05 | 136 | 0.98692 | 1.9971 | 1.5024 | 0.00053475 | 1.3638e-05
| 408.15 | 100000 | 1998.146 | 1502.9825 | 0.53612 | 1.3599e-05 | 135 | 0.98692 | 1.9981 | 1.503 | 0.00053612 | 1.3599e-05
| 407.15 | 100000 | 1999.2256 | 1503.5602 | 0.5375 | 1.356e-05 | 134 | 0.98692 | 1.9992 | 1.5036 | 0.0005375 | 1.356e-05
| 406.15 | 100000 | 2000.3411 | 1504.1632 | 0.53888 | 1.3522e-05 | 133 | 0.98692 | 2.0003 | 1.5042 | 0.00053888 | 1.3522e-05
| 405.15 | 100000 | 2001.4935 | 1504.7925 | 0.54028 | 1.3483e-05 | 132 | 0.98692 | 2.0015 | 1.5048 | 0.00054028 | 1.3483e-05
| 404.15 | 100000 | 2002.684 | 1505.4486 | 0.54168 | 1.3444e-05 | 131 | 0.98692 | 2.0027 | 1.5054 | 0.00054168 | 1.3444e-05
| 403.15 | 100000 | 2003.9137 | 1506.1328 | 0.54309 | 1.3406e-05 | 130 | 0.98692 | 2.0039 | 1.5061 | 0.00054309 | 1.3406e-05
| 402.15 | 100000 | 2005.1841 | 1506.8457 | 0.54451 | 1.3367e-05 | 129 | 0.98692 | 2.0052 | 1.5068 | 0.00054451 | 1.3367e-05
| 401.15 | 100000 | 2006.4965 | 1507.5886 | 0.54593 | 1.3329e-05 | 128 | 0.98692 | 2.0065 | 1.5076 | 0.00054593 | 1.3329e-05
| 400.15 | 100000 | 2007.8524 | 1508.3625 | 0.54737 | 1.3291e-05 | 127 | 0.98692 | 2.0079 | 1.5084 | 0.00054737 | 1.3291e-05
| 399.15 | 100000 | 2009.2533 | 1509.1687 | 0.54881 | 1.3252e-05 | 126 | 0.98692 | 2.0093 | 1.5092 | 0.00054881 | 1.3252e-05
| 398.15 | 100000 | 2010.7012 | 1510.0084 | 0.55026 | 1.3214e-05 | 125 | 0.98692 | 2.0107 | 1.51 | 0.00055026 | 1.3214e-05
| 397.15 | 100000 | 2012.1979 | 1510.8832 | 0.55172 | 1.3176e-05 | 124 | 0.98692 | 2.0122 | 1.5109 | 0.00055172 | 1.3176e-05
| 396.15 | 100000 | 2013.7452 | 1511.7944 | 0.55319 | 1.3137e-05 | 123 | 0.98692 | 2.0137 | 1.5118 | 0.00055319 | 1.3137e-05
| 395.15 | 100000 | 2015.3457 | 1512.744 | 0.55467 | 1.3099e-05 | 122 | 0.98692 | 2.0153 | 1.5127 | 0.00055467 | 1.3099e-05
| 394.15 | 100000 | 2017.0018 | 1513.7338 | 0.55616 | 1.3061e-05 | 121 | 0.98692 | 2.017 | 1.5137 | 0.00055616 | 1.3061e-05
| 393.15 | 100000 | 2018.7161 | 1514.7659 | 0.55765 | 1.3023e-05 | 120 | 0.98692 | 2.0187 | 1.5148 | 0.00055765 | 1.3023e-05
| 392.15 | 100000 | 2020.4916 | 1515.8425 | 0.55916 | 1.2985e-05 | 119 | 0.98692 | 2.0205 | 1.5158 | 0.00055916 | 1.2985e-05
| 391.15 | 100000 | 2022.3317 | 1516.9664 | 0.56067 | 1.2947e-05 | 118 | 0.98692 | 2.0223 | 1.517 | 0.00056067 | 1.2947e-05
| 390.15 | 100000 | 2024.24 | 1518.1405 | 0.56219 | 1.2909e-05 | 117 | 0.98692 | 2.0242 | 1.5181 | 0.00056219 | 1.2909e-05
| 389.15 | 100000 | 2026.2206 | 1519.3678 | 0.56372 | 1.2871e-05 | 116 | 0.98692 | 2.0262 | 1.5194 | 0.00056372 | 1.2871e-05
| 388.15 | 100000 | 2028.2781 | 1520.6521 | 0.56527 | 1.2833e-05 | 115 | 0.98692 | 2.0283 | 1.5207 | 0.00056527 | 1.2833e-05
| 387.15 | 100000 | 2030.4175 | 1521.9973 | 0.56682 | 1.2795e-05 | 114 | 0.98692 | 2.0304 | 1.522 | 0.00056682 | 1.2795e-05
| 386.15 | 100000 | 2032.6447 | 1523.4083 | 0.56838 | 1.2758e-05 | 113 | 0.98692 | 2.0326 | 1.5234 | 0.00056838 | 1.2758e-05
| 385.15 | 100000 | 2034.9658 | 1524.8899 | 0.56995 | 1.272e-05 | 112 | 0.98692 | 2.035 | 1.5249 | 0.00056995 | 1.272e-05
| 384.15 | 100000 | 2037.3884 | 1526.4482 | 0.57153 | 1.2682e-05 | 111 | 0.98692 | 2.0374 | 1.5264 | 0.00057153 | 1.2682e-05
| 383.15 | 100000 | 2039.9207 | 1528.0897 | 0.57313 | 1.2644e-05 | 110 | 0.98692 | 2.0399 | 1.5281 | 0.00057313 | 1.2644e-05
| 382.15 | 100000 | 2042.5717 | 1529.8219 | 0.57473 | 1.2607e-05 | 109 | 0.98692 | 2.0426 | 1.5298 | 0.00057473 | 1.2607e-05
| 381.15 | 100000 | 2045.3522 | 1531.6536 | 0.57634 | 1.2569e-05 | 108 | 0.98692 | 2.0454 | 1.5317 | 0.00057634 | 1.2569e-05
| 380.15 | 100000 | 2048.2739 | 1533.5941 | 0.57796 | 1.2532e-05 | 107 | 0.98692 | 2.0483 | 1.5336 | 0.00057796 | 1.2532e-05
| 379.15 | 100000 | 2051.3506 | 1535.6549 | 0.5796 | 1.2494e-05 | 106 | 0.98692 | 2.0514 | 1.5357 | 0.0005796 | 1.2494e-05
| 378.15 | 100000 | 2054.5979 | 1537.8485 | 0.58124 | 1.2457e-05 | 105 | 0.98692 | 2.0546 | 1.5378 | 0.00058124 | 1.2457e-05
| 377.15 | 100000 | 2058.0332 | 1540.1896 | 0.5829 | 1.2419e-05 | 104 | 0.98692 | 2.058 | 1.5402 | 0.0005829 | 1.2419e-05
| 376.15 | 100000 | 2061.6772 | 1542.6945 | 0.58457 | 1.2382e-05 | 103 | 0.98692 | 2.0617 | 1.5427 | 0.00058457 | 1.2382e-05
| 375.15 | 100000 | 2065.5527 | 1545.3822 | 0.58624 | 1.2345e-05 | 102 | 0.98692 | 2.0656 | 1.5454 | 0.00058624 | 1.2345e-05
| 374.15 | 100000 | 2069.6863 | 1548.2748 | 0.58793 | 1.2308e-05 | 101 | 0.98692 | 2.0697 | 1.5483 | 0.00058793 | 1.2308e-05
| 373.15 | 100000 | 2074.1084 | 1551.3972 | 0.58964 | 1.227e-05 | 100 | 0.98692 | 2.0741 | 1.5514 | 0.00058964 | 1.227e-05
| 372.15 | 100000 | 4215.3887 | 3772.7732 | 959.071 | 0.00028474 | 99 | 0.98692 | 4.2154 | 3.7728 | 0.95907 | 0.00028474
| 371.15 | 100000 | 4214.1514 | 3777.8516 | 959.7839 | 0.00028778 | 98 | 0.98692 | 4.2142 | 3.7779 | 0.95978 | 0.00028778
| 370.15 | 100000 | 4212.9351 | 3782.9377 | 960.4921 | 0.00029089 | 97 | 0.98692 | 4.2129 | 3.7829 | 0.96049 | 0.00029089
| 369.15 | 100000 | 4211.7407 | 3788.0312 | 961.1956 | 0.00029406 | 96 | 0.98692 | 4.2117 | 3.788 | 0.9612 | 0.00029406
| 368.15 | 100000 | 4210.5679 | 3793.1318 | 961.8945 | 0.00029729 | 95 | 0.98692 | 4.2106 | 3.7931 | 0.96189 | 0.00029729
| 367.15 | 100000 | 4209.4165 | 3798.2393 | 962.5886 | 0.00030058 | 94 | 0.98692 | 4.2094 | 3.7982 | 0.96259 | 0.00030058
| 366.15 | 100000 | 4208.2866 | 3803.3533 | 963.2781 | 0.00030393 | 93 | 0.98692 | 4.2083 | 3.8034 | 0.96328 | 0.00030393
| 365.15 | 100000 | 4207.1782 | 3808.4739 | 963.9628 | 0.00030736 | 92 | 0.98692 | 4.2072 | 3.8085 | 0.96396 | 0.00030736
| 364.15 | 100000 | 4206.0908 | 3813.6008 | 964.6428 | 0.00031085 | 91 | 0.98692 | 4.2061 | 3.8136 | 0.96464 | 0.00031085
| 363.15 | 100000 | 4205.0244 | 3818.7336 | 965.3181 | 0.00031441 | 90 | 0.98692 | 4.205 | 3.8187 | 0.96532 | 0.00031441
| 362.15 | 100000 | 4203.9795 | 3823.8721 | 965.9885 | 0.00031805 | 89 | 0.98692 | 4.204 | 3.8239 | 0.96599 | 0.00031805
| 361.15 | 100000 | 4202.9556 | 3829.0159 | 966.6541 | 0.00032176 | 88 | 0.98692 | 4.203 | 3.829 | 0.96665 | 0.00032176
| 360.15 | 100000 | 4201.9526 | 3834.1648 | 967.3148 | 0.00032554 | 87 | 0.98692 | 4.202 | 3.8342 | 0.96731 | 0.00032554
| 359.15 | 100000 | 4200.9707 | 3839.3186 | 967.9708 | 0.0003294 | 86 | 0.98692 | 4.201 | 3.8393 | 0.96797 | 0.0003294
| 358.15 | 100000 | 4200.0098 | 3844.4768 | 968.6217 | 0.00033335 | 85 | 0.98692 | 4.2 | 3.8445 | 0.96862 | 0.00033335
| 357.15 | 100000 | 4199.0698 | 3849.6392 | 969.2678 | 0.00033737 | 84 | 0.98692 | 4.1991 | 3.8496 | 0.96927 | 0.00033737
| 356.15 | 100000 | 4198.1509 | 3854.8054 | 969.9089 | 0.00034149 | 83 | 0.98692 | 4.1982 | 3.8548 | 0.96991 | 0.00034149
| 355.15 | 100000 | 4197.2524 | 3859.9751 | 970.545 | 0.00034568 | 82 | 0.98692 | 4.1973 | 3.86 | 0.97055 | 0.00034568
| 354.15 | 100000 | 4196.375 | 3865.1479 | 971.1762 | 0.00034997 | 81 | 0.98692 | 4.1964 | 3.8651 | 0.97118 | 0.00034997
| 353.15 | 100000 | 4195.5186 | 3870.3235 | 971.8023 | 0.00035435 | 80 | 0.98692 | 4.1955 | 3.8703 | 0.9718 | 0.00035435
| 352.15 | 100000 | 4194.6826 | 3875.5012 | 972.4233 | 0.00035883 | 79 | 0.98692 | 4.1947 | 3.8755 | 0.97242 | 0.00035883
| 351.15 | 100000 | 4193.8677 | 3880.6809 | 973.0392 | 0.00036341 | 78 | 0.98692 | 4.1939 | 3.8807 | 0.97304 | 0.00036341
| 350.15 | 100000 | 4193.0737 | 3885.8621 | 973.65 | 0.00036808 | 77 | 0.98692 | 4.1931 | 3.8859 | 0.97365 | 0.00036808
| 349.15 | 100000 | 4192.3003 | 3891.0442 | 974.2557 | 0.00037286 | 76 | 0.98692 | 4.1923 | 3.891 | 0.97426 | 0.00037286
| 348.15 | 100000 | 4191.5479 | 3896.2268 | 974.8561 | 0.00037775 | 75 | 0.98692 | 4.1915 | 3.8962 | 0.97486 | 0.00037775
| 347.15 | 100000 | 4190.8164 | 3901.4094 | 975.4512 | 0.00038274 | 74 | 0.98692 | 4.1908 | 3.9014 | 0.97545 | 0.00038274
| 346.15 | 100000 | 4190.1055 | 3906.5913 | 976.0411 | 0.00038785 | 73 | 0.98692 | 4.1901 | 3.9066 | 0.97604 | 0.00038785
| 345.15 | 100000 | 4189.4155 | 3911.7725 | 976.6257 | 0.00039308 | 72 | 0.98692 | 4.1894 | 3.9118 | 0.97663 | 0.00039308
| 344.15 | 100000 | 4188.7461 | 3916.9519 | 977.2049 | 0.00039843 | 71 | 0.98692 | 4.1887 | 3.917 | 0.9772 | 0.00039843
| 343.15 | 100000 | 4188.0981 | 3922.1292 | 977.7787 | 0.0004039 | 70 | 0.98692 | 4.1881 | 3.9221 | 0.97778 | 0.0004039
| 342.15 | 100000 | 4187.4707 | 3927.3037 | 978.3471 | 0.0004095 | 69 | 0.98692 | 4.1875 | 3.9273 | 0.97835 | 0.0004095
| 341.15 | 100000 | 4186.8638 | 3932.4749 | 978.91 | 0.00041523 | 68 | 0.98692 | 4.1869 | 3.9325 | 0.97891 | 0.00041523
| 340.15 | 100000 | 4186.2783 | 3937.6418 | 979.4673 | 0.0004211 | 67 | 0.98692 | 4.1863 | 3.9376 | 0.97947 | 0.0004211
| 339.15 | 100000 | 4185.7134 | 3942.8042 | 980.0191 | 0.00042711 | 66 | 0.98692 | 4.1857 | 3.9428 | 0.98002 | 0.00042711
| 338.15 | 100000 | 4185.1699 | 3947.9612 | 980.5652 | 0.00043327 | 65 | 0.98692 | 4.1852 | 3.948 | 0.98057 | 0.00043327
| 337.15 | 100000 | 4184.647 | 3953.1118 | 981.1058 | 0.00043957 | 64 | 0.98692 | 4.1846 | 3.9531 | 0.98111 | 0.00043957
| 336.15 | 100000 | 4184.145 | 3958.2559 | 981.6406 | 0.00044604 | 63 | 0.98692 | 4.1841 | 3.9583 | 0.98164 | 0.00044604
| 335.15 | 100000 | 4183.6646 | 3963.3921 | 982.1696 | 0.00045266 | 62 | 0.98692 | 4.1837 | 3.9634 | 0.98217 | 0.00045266
| 334.15 | 100000 | 4183.2051 | 3968.5198 | 982.6927 | 0.00045944 | 61 | 0.98692 | 4.1832 | 3.9685 | 0.98269 | 0.00045944
| 333.15 | 100000 | 4182.7666 | 3973.6382 | 983.21 | 0.0004664 | 60 | 0.98692 | 4.1828 | 3.9736 | 0.98321 | 0.0004664
| 332.15 | 100000 | 4182.3491 | 3978.7466 | 983.7214 | 0.00047354 | 59 | 0.98692 | 4.1823 | 3.9787 | 0.98372 | 0.00047354
| 331.15 | 100000 | 4181.9531 | 3983.844 | 984.2268 | 0.00048086 | 58 | 0.98692 | 4.182 | 3.9838 | 0.98423 | 0.00048086
| 330.15 | 100000 | 4181.5786 | 3988.9292 | 984.7261 | 0.00048837 | 57 | 0.98692 | 4.1816 | 3.9889 | 0.98473 | 0.00048837
| 329.15 | 100000 | 4181.2251 | 3994.0017 | 985.2194 | 0.00049607 | 56 | 0.98692 | 4.1812 | 3.994 | 0.98522 | 0.00049607
| 328.15 | 100000 | 4180.8931 | 3999.0603 | 985.7064 | 0.00050398 | 55 | 0.98692 | 4.1809 | 3.9991 | 0.98571 | 0.00050398
| 327.15 | 100000 | 4180.5825 | 4004.104 | 986.1873 | 0.0005121 | 54 | 0.98692 | 4.1806 | 4.0041 | 0.98619 | 0.0005121
| 326.15 | 100000 | 4180.2935 | 4009.1316 | 986.6618 | 0.00052044 | 53 | 0.98692 | 4.1803 | 4.0091 | 0.98666 | 0.00052044
| 325.15 | 100000 | 4180.0264 | 4014.1423 | 987.1299 | 0.00052901 | 52 | 0.98692 | 4.18 | 4.0141 | 0.98713 | 0.00052901
| 324.15 | 100000 | 4179.7808 | 4019.1348 | 987.5917 | 0.00053781 | 51 | 0.98692 | 4.1798 | 4.0191 | 0.98759 | 0.00053781
| 323.15 | 100000 | 4179.5571 | 4024.1082 | 988.0469 | 0.00054685 | 50 | 0.98692 | 4.1796 | 4.0241 | 0.98805 | 0.00054685
| 322.15 | 100000 | 4179.3555 | 4029.061 | 988.4955 | 0.00055615 | 49 | 0.98692 | 4.1794 | 4.0291 | 0.9885 | 0.00055615
| 321.15 | 100000 | 4179.1758 | 4033.9922 | 988.9375 | 0.00056571 | 48 | 0.98692 | 4.1792 | 4.034 | 0.98894 | 0.00056571
| 320.15 | 100000 | 4179.0181 | 4038.9004 | 989.3727 | 0.00057554 | 47 | 0.98692 | 4.179 | 4.0389 | 0.98937 | 0.00057554
| 319.15 | 100000 | 4178.8833 | 4043.7844 | 989.8012 | 0.00058566 | 46 | 0.98692 | 4.1789 | 4.0438 | 0.9898 | 0.00058566
| 318.15 | 100000 | 4178.771 | 4048.6431 | 990.2227 | 0.00059607 | 45 | 0.98692 | 4.1788 | 4.0486 | 0.99022 | 0.00059607
| 317.15 | 100000 | 4178.6812 | 4053.4751 | 990.6372 | 0.00060679 | 44 | 0.98692 | 4.1787 | 4.0535 | 0.99064 | 0.00060679
| 316.15 | 100000 | 4178.6147 | 4058.2786 | 991.0447 | 0.00061782 | 43 | 0.98692 | 4.1786 | 4.0583 | 0.99104 | 0.00061782
| 315.15 | 100000 | 4178.5713 | 4063.0527 | 991.445 | 0.00062919 | 42 | 0.98692 | 4.1786 | 4.0631 | 0.99145 | 0.00062919
| 314.15 | 100000 | 4178.5518 | 4067.7957 | 991.838 | 0.0006409 | 41 | 0.98692 | 4.1786 | 4.0678 | 0.99184 | 0.0006409
| 313.15 | 100000 | 4178.5557 | 4072.5061 | 992.2237 | 0.00065298 | 40 | 0.98692 | 4.1786 | 4.0725 | 0.99222 | 0.00065298
| 312.15 | 100000 | 4178.5845 | 4077.1826 | 992.6019 | 0.00066543 | 39 | 0.98692 | 4.1786 | 4.0772 | 0.9926 | 0.00066543
| 311.15 | 100000 | 4178.6377 | 4081.8237 | 992.9725 | 0.00067827 | 38 | 0.98692 | 4.1786 | 4.0818 | 0.99297 | 0.00067827
| 310.15 | 100000 | 4178.7158 | 4086.4277 | 993.3355 | 0.00069152 | 37 | 0.98692 | 4.1787 | 4.0864 | 0.99334 | 0.00069152
| 309.15 | 100000 | 4178.8198 | 4090.9929 | 993.6907 | 0.00070519 | 36 | 0.98692 | 4.1788 | 4.091 | 0.99369 | 0.00070519
| 308.15 | 100000 | 4178.9502 | 4095.5181 | 994.038 | 0.00071932 | 35 | 0.98692 | 4.179 | 4.0955 | 0.99404 | 0.00071932
| 307.15 | 100000 | 4179.1079 | 4100.0015 | 994.3772 | 0.0007339 | 34 | 0.98692 | 4.1791 | 4.1 | 0.99438 | 0.0007339
| 306.15 | 100000 | 4179.293 | 4104.4409 | 994.7083 | 0.00074897 | 33 | 0.98692 | 4.1793 | 4.1044 | 0.99471 | 0.00074897
| 305.15 | 100000 | 4179.5068 | 4108.8354 | 995.0311 | 0.00076456 | 32 | 0.98692 | 4.1795 | 4.1088 | 0.99503 | 0.00076456
| 304.15 | 100000 | 4179.75 | 4113.1836 | 995.3456 | 0.00078067 | 31 | 0.98692 | 4.1798 | 4.1132 | 0.99535 | 0.00078067
| 303.15 | 100000 | 4180.0239 | 4117.4824 | 995.6515 | 0.00079735 | 30 | 0.98692 | 4.18 | 4.1175 | 0.99565 | 0.00079735
| 302.15 | 100000 | 4180.3296 | 4121.7319 | 995.9487 | 0.0008146 | 29 | 0.98692 | 4.1803 | 4.1217 | 0.99595 | 0.0008146
| 301.15 | 100000 | 4180.6685 | 4125.9287 | 996.237 | 0.00083248 | 28 | 0.98692 | 4.1807 | 4.1259 | 0.99624 | 0.00083248
| 300.15 | 100000 | 4181.042 | 4130.0728 | 996.5164 | 0.00085099 | 27 | 0.98692 | 4.181 | 4.1301 | 0.99652 | 0.00085099
| 299.15 | 100000 | 4181.4517 | 4134.1611 | 996.7866 | 0.00087018 | 26 | 0.98692 | 4.1815 | 4.1342 | 0.99679 | 0.00087018
| 298.15 | 100000 | 4181.8999 | 4138.1929 | 997.0474 | 0.00089008 | 25 | 0.98692 | 4.1819 | 4.1382 | 0.99705 | 0.00089008
| 297.15 | 100000 | 4182.3887 | 4142.166 | 997.2988 | 0.00091073 | 24 | 0.98692 | 4.1824 | 4.1422 | 0.9973 | 0.00091073
| 296.15 | 100000 | 4182.9199 | 4146.0786 | 997.5405 | 0.00093216 | 23 | 0.98692 | 4.1829 | 4.1461 | 0.99754 | 0.00093216
| 295.15 | 100000 | 4183.4966 | 4149.9302 | 997.7723 | 0.00095442 | 22 | 0.98692 | 4.1835 | 4.1499 | 0.99777 | 0.00095442
| 294.15 | 100000 | 4184.1216 | 4153.7183 | 997.994 | 0.00097756 | 21 | 0.98692 | 4.1841 | 4.1537 | 0.99799 | 0.00097756
| 293.15 | 100000 | 4184.7983 | 4157.4414 | 998.2055 | 0.0010016 | 20 | 0.98692 | 4.1848 | 4.1574 | 0.99821 | 0.0010016
| 292.15 | 100000 | 4185.5303 | 4161.0986 | 998.4064 | 0.0010266 | 19 | 0.98692 | 4.1855 | 4.1611 | 0.99841 | 0.0010266
| 291.15 | 100000 | 4186.3213 | 4164.6885 | 998.5967 | 0.0010527 | 18 | 0.98692 | 4.1863 | 4.1647 | 0.9986 | 0.0010527
| 290.15 | 100000 | 4187.1763 | 4168.2095 | 998.7759 | 0.0010798 | 17 | 0.98692 | 4.1872 | 4.1682 | 0.99878 | 0.0010798
| 289.15 | 100000 | 4188.1001 | 4171.6606 | 998.944 | 0.0011081 | 16 | 0.98692 | 4.1881 | 4.1717 | 0.99894 | 0.0011081
| 288.15 | 100000 | 4189.0986 | 4175.041 | 999.1005 | 0.0011376 | 15 | 0.98692 | 4.1891 | 4.175 | 0.9991 | 0.0011376
| 287.15 | 100000 | 4190.1777 | 4178.3491 | 999.2453 | 0.0011683 | 14 | 0.98692 | 4.1902 | 4.1783 | 0.99925 | 0.0011683
| 286.15 | 100000 | 4191.3442 | 4181.5845 | 999.3781 | 0.0012004 | 13 | 0.98692 | 4.1913 | 4.1816 | 0.99938 | 0.0012004
| 285.15 | 100000 | 4192.606 | 4184.7461 | 999.4985 | 0.001234 | 12 | 0.98692 | 4.1926 | 4.1847 | 0.9995 | 0.001234
| 284.15 | 100000 | 4193.9722 | 4187.834 | 999.6062 | 0.0012691 | 11 | 0.98692 | 4.194 | 4.1878 | 0.99961 | 0.0012691
| 283.15 | 100000 | 4195.4512 | 4190.8477 | 999.7009 | 0.0013059 | 10 | 0.98692 | 4.1955 | 4.1908 | 0.9997 | 0.0013059
| 282.15 | 100000 | 4197.0537 | 4193.7866 | 999.7823 | 0.0013444 | 9 | 0.98692 | 4.1971 | 4.1938 | 0.99978 | 0.0013444
| 281.15 | 100000 | 4198.7915 | 4196.6514 | 999.8499 | 0.0013847 | 8 | 0.98692 | 4.1988 | 4.1967 | 0.99985 | 0.0013847
| 280.15 | 100000 | 4200.6777 | 4199.4419 | 999.9034 | 0.001427 | 7 | 0.98692 | 4.2007 | 4.1994 | 0.9999 | 0.001427
| 279.15 | 100000 | 4202.7261 | 4202.1587 | 999.9423 | 0.0014714 | 6 | 0.98692 | 4.2027 | 4.2022 | 0.99994 | 0.0014714
| 278.15 | 100000 | 4204.9531 | 4204.8027 | 999.9662 | 0.0015181 | 5 | 0.98692 | 4.205 | 4.2048 | 0.99997 | 0.0015181
| 277.15 | 100000 | 4207.375 | 4207.375 | 999.9747 | 0.0015672 | 4 | 0.98692 | 4.2074 | 4.2074 | 0.99997 | 0.0015672
| 276.15 | 100000 | 4210.0122 | 4209.8765 | 999.9673 | 0.0016189 | 3 | 0.98692 | 4.21 | 4.2099 | 0.99997 | 0.0016189
| 275.15 | 100000 | 4212.8853 | 4212.3096 | 999.9433 | 0.0016734 | 2 | 0.98692 | 4.2129 | 4.2123 | 0.99994 | 0.0016734
| 274.15 | 100000 | 4216.0181 | 4214.6753 | 999.9023 | 0.0017309 | 0.99999 | 0.98692 | 4.216 | 4.2147 | 0.9999 | 0.0017309
| 273.15 | 100000 | 4219.437 | 4216.9766 | 999.8436 | 0.0017915 | -6.1035e-06 | 0.98692 | 4.2194 | 4.217 | 0.99984 | 0.0017915